## Data-Cooling Tower
|  | width | 19 | Hight | 12 | inch | area | 228 | inch2 | 2 sides | 456 | Expect area | 60 | % | 273.6 | sq inch
[15 empty] | 0.17652 | sq m
Date-Time | Index | Interval Filter | Date | Time | ST | GS | Check | Weight | Unit | Pump-Status | Voltage (V) | Current (A) | Power (W) | Energy (Wh) | Operation Time | Intake Air Temperature (°C) | Intake Air Velocity | Intake Air Relative Humidity (%) | Outtake Air Temperature (°C) | Outtake Air Velocity | Outtake Air Relative Humidity (%) | Column1 | Intake Air Velocity2 | Intake Air Vec. Unit | Column2 | Outtake Air Velocit | Outtake Air Vel. Unit | Operation time (decimal) | Incremental Energy (kWh) | Cumulative Energy (kWh) | Column4 | Water | Accumulate Water | Acuumulate Water | kW.h/L | Absolut Humidity (intake) | Absolute Humidity (outtake) | Intake Water (L) | Total Water Intake Air (L) | Harvesting Efficiency
2025-05-19 10:17 | 1 | Keep | 2025-05-19 | 10:17 | ST | GS | + | 0 | g | 0 | 112.8 | 10.984 | 1067.2 | 50351 | 0:00 | 28.7 | 2.96 m/s | 33.7 | 29.3 | 3.61 m/s | 30 |  | 2.96 | m/s |  | 3.61 | m/s | 0.00027778 | 0.0088933 | 0.0088933 |  | 0 | 0 | 0 | 0 | 9.5298 | 8.7662 | 0.041493 | 0.041493 | 0
2025-05-19 10:17 | 2 | Remove | 2025-05-19 | 10:17 | US | GS | - | 2 | g | 0 | 112.8 | 11.017 | 1070.9 | 50360 | 0:01 | 28.7 | 2.67 m/s | 33.4 | 29.4 | 3.9 m/s | 29 |  | 2.67 | m/s |  | 3.9 | m/s | 0.0086111 | 0.0089242 | 0.017818 |  | 2 | 2 | 0.002 | 8.9088 | 9.445 | 8.5203 | 0.037095 | 0.078588 | 2.5449
2025-05-19 10:18 | 3 | Remove | 2025-05-19 | 10:18 | US | GS | - | 1.5 | g | 0 | 112.8 | 11.003 | 1069.4 | 50369 | 0:01 | 28.6 | 2.26 m/s | 33.2 | 29.4 | 4.24 m/s | 28.5 |  | 2.26 | m/s |  | 4.24 | m/s | 0.016944 | 0.0089117 | 0.026729 |  | -0.5 | 1.5 | 0.0015 | 17.8194 | 9.3371 | 8.3734 | 0.03104 | 0.10963 | 1.3683
2025-05-19 10:18 | 4 | Remove | 2025-05-19 | 10:18 | ST | GS | + | 0 | g | 0 | 112.8 | 11.023 | 1072.4 | 50378 | 0:02 | 28.6 | 2.42 m/s | 34 | 29.5 | 4.03 m/s | 28.7 |  | 2.42 | m/s |  | 4.03 | m/s | 0.025278 | 0.0089367 | 0.035666 |  | -1.5 | 0 | 0 | 0 | 9.5621 | 8.4782 | 0.034039 | 0.14367 | 0
2025-05-19 10:19 | 5 | Remove | 2025-05-19 | 10:19 | ST | GS | - | 0.5 | g | 0 | 112.8 | 10.995 | 1069.7 | 50387 | 0:02 | 28.6 | 2.71 m/s | 32 | 29.6 | 3.9 m/s | 27 |  | 2.71 | m/s |  | 3.9 | m/s | 0.033611 | 0.0089142 | 0.04458 |  | 0.5 | 0.5 | 0.0005 | 89.16 | 8.9996 | 8.0195 | 0.035875 | 0.17954 | 0.27849
2025-05-19 10:19 | 6 | Remove | 2025-05-19 | 10:19 | ST | GS | + | 2 | g | 0 | 112.7 | 11.061 | 1077.6 | 50396 | 0:03 | 28.6 | 2.23 m/s | 33.9 | 29.6 | 3.9 m/s | 27 |  | 2.23 | m/s |  | 3.9 | m/s | 0.041944 | 0.00898 | 0.05356 |  | 1.5 | 2 | 0.002 | 26.78 | 9.534 | 8.0195 | 0.031274 | 0.21082 | 0.94869
2025-05-19 10:20 | 7 | Remove | 2025-05-19 | 10:20 | US | GS | + | 0 | g | 0 | 112.8 | 11.019 | 1072.9 | 50405 | 0:03 | 28.6 | 2.33 m/s | 32.2 | 29.6 | 4.26 m/s | 28.3 |  | 2.33 | m/s |  | 4.26 | m/s | 0.050278 | 0.0089408 | 0.062501 |  | -2 | 0 | 0 | 0 | 9.0559 | 8.4056 | 0.031038 | 0.24185 | 0
2025-05-19 10:20 | 8 | Remove | 2025-05-19 | 10:20 | ST | GS | + | 0 | g | 0 | 112.7 | 11.061 | 1078.1 | 50414 | 0:04 | 28.6 | 2.42 m/s | 33.1 | 29.7 | 3.75 m/s | 26.6 |  | 2.42 | m/s |  | 3.75 | m/s | 0.058611 | 0.0089842 | 0.071485 |  | 0 | 0 | 0 | 0 | 9.309 | 7.9438 | 0.033138 | 0.27499 | 0
2025-05-19 10:21 | 9 | Remove | 2025-05-19 | 10:21 | US | GS | + | 0.5 | g | 0 | 112.7 | 11.055 | 1077.3 | 50423 | 0:04 | 28.6 | 2.42 m/s | 33.1 | 29.7 | 4.06 m/s | 27.2 |  | 2.42 | m/s |  | 4.06 | m/s | 0.066944 | 0.0089775 | 0.080463 |  | 0.5 | 0.5 | 0.0005 | 160.925 | 9.309 | 8.123 | 0.033138 | 0.30813 | 0.16227
2025-05-19 10:21 | 10 | Remove | 2025-05-19 | 10:21 | US | GS | - | 3.5 | g | 0 | 112.6 | 11.157 | 1089.9 | 50432 | 0:05 | 28.6 | 2.22 m/s | 31.6 | 29.7 | 4.15 m/s | 26 |  | 2.22 | m/s |  | 4.15 | m/s | 0.075278 | 0.0090825 | 0.089545 |  | 3 | 3.5 | 0.0035 | 25.5843 | 8.8871 | 7.7646 | 0.029021 | 0.33715 | 1.0381
2025-05-19 10:22 | 11 | Remove | 2025-05-19 | 10:22 | ST | GS | + | 0 | g | 0 | 112.7 | 11.107 | 1084.3 | 50441 | 0:05 | 28.6 | 2.51 m/s | 38 | 29.8 | 3.96 m/s | 29.9 |  | 2.51 | m/s |  | 3.96 | m/s | 0.083611 | 0.0090358 | 0.098581 |  | -3.5 | 0 | 0 | 0 | 10.6871 | 8.9779 | 0.039458 | 0.37661 | 0
2025-05-19 10:22 | 12 | Remove | 2025-05-19 | 10:22 | US | GS | + | 0.5 | g | 0 | 112.7 | 11.145 | 1088.5 | 50450 | 0:06 | 28.6 | 2.48 m/s | 33 | 29.9 | 3.94 m/s | 26.5 |  | 2.48 | m/s |  | 3.94 | m/s | 0.091944 | 0.0090708 | 0.10765 |  | 0.5 | 0.5 | 0.0005 | 215.3033 | 9.2809 | 8.0003 | 0.033857 | 0.41047 | 0.12181
2025-05-19 10:23 | 13 | Remove | 2025-05-19 | 10:23 | ST | GS | + | 1.5 | g | 0 | 112.6 | 11.102 | 1083.9 | 50459 | 0:06 | 28.6 | 2.34 m/s | 34.5 | 29.9 | 3.88 m/s | 26.9 |  | 2.34 | m/s |  | 3.88 | m/s | 0.10028 | 0.0090325 | 0.11668 |  | 1 | 1.5 | 0.0015 | 77.7894 | 9.7027 | 8.1211 | 0.033397 | 0.44386 | 0.33794
2025-05-19 10:23 | 14 | Remove | 2025-05-19 | 10:23 | US | GS | + | 2 | g | 0 | 112.5 | 11.223 | 1098.5 | 50468 | 0:07 | 28.6 | 2.48 m/s | 32.5 | 30 | 3.98 m/s | 25.8 |  | 2.48 | m/s |  | 3.98 | m/s | 0.10861 | 0.0091542 | 0.12584 |  | 0.5 | 2 | 0.002 | 62.9192 | 9.1403 | 7.8314 | 0.033344 | 0.47721 | 0.41911
2025-05-19 10:24 | 15 | Remove | 2025-05-19 | 10:24 | US | GS | + | 0 | g | 0 | 112.5 | 11.184 | 1093.9 | 50478 | 0:07 | 28.6 | 2.34 m/s | 39.3 | 30 | 3.92 m/s | 30 |  | 2.34 | m/s |  | 3.92 | m/s | 0.11694 | 0.0091158 | 0.13495 |  | -2 | 0 | 0 | 0 | 11.0527 | 9.1062 | 0.038044 | 0.51525 | 0
2025-05-19 10:24 | 16 | Remove | 2025-05-19 | 10:24 | US | GS | - | 5.5 | g | 0 | 112.6 | 11.111 | 1084.9 | 50487 | 0:08 | 28.6 | 2.27 m/s | 38 | 30.1 | 4.16 m/s | 28.8 |  | 2.27 | m/s |  | 4.16 | m/s | 0.12528 | 0.0090408 | 0.14399 |  | 5.5 | 5.5 | 0.0055 | 26.1809 | 10.6871 | 8.7895 | 0.035685 | 0.55094 | 0.9983
2025-05-19 10:25 | 17 | Remove | 2025-05-19 | 10:25 | US | GS | - | 5 | g | 0 | 112.6 | 11.111 | 1085.1 | 50496 | 0:08 | 28.6 | 2.64 m/s | 31.1 | 30.1 | 3.86 m/s | 24.7 |  | 2.64 | m/s |  | 3.86 | m/s | 0.13389 | 0.0090425 | 0.15304 |  | -0.5 | 5 | 0.005 | 30.6075 | 8.7465 | 7.5382 | 0.033966 | 0.5849 | 0.85485
2025-05-19 10:25 | 18 | Remove | 2025-05-19 | 10:25 | ST | GS | - | 3 | g | 0 | 112.5 | 11.158 | 1090.8 | 50505 | 0:09 | 28.6 | 2.64 m/s | 31.1 | 30 | 3.81 m/s | 24.2 |  | 2.64 | m/s |  | 3.81 | m/s | 0.14222 | 0.00909 | 0.16213 |  | -2 | 3 | 0.003 | 54.0425 | 8.7465 | 7.3457 | 0.033966 | 0.61887 | 0.48476
2025-05-19 10:26 | 19 | Remove | 2025-05-19 | 10:26 | ST | GS | + | 0 | g | 0 | 112.5 | 11.204 | 1096.5 | 50514 | 0:09 | 28.6 | 2.3 m/s | 33.6 | 30 | 4.0 m/s | 25.8 |  | 2.3 | m/s |  | 4 | m/s | 0.15056 | 0.0091375 | 0.17126 |  | -3 | 0 | 0 | 0 | 9.4496 | 7.8314 | 0.03197 | 0.65084 | 0
2025-05-19 10:26 | 20 | Remove | 2025-05-19 | 10:26 | US | GS | + | 1.5 | g | 0 | 112.6 | 11.145 | 1089.4 | 50523 | 0:10 | 28.6 | 2.51 m/s | 35.4 | 30.1 | 3.9 m/s | 27.3 |  | 2.51 | m/s |  | 3.9 | m/s | 0.15889 | 0.0090783 | 0.18034 |  | 1.5 | 1.5 | 0.0015 | 120.2289 | 9.9559 | 8.3317 | 0.036758 | 0.6876 | 0.21815
2025-05-19 10:27 | 21 | Remove | 2025-05-19 | 10:27 | ST | GS | + | 3 | g | 0 | 112.3 | 11.216 | 1098.1 | 50532 | 0:10 | 28.6 | 2.2 m/s | 32.1 | 30.1 | 4.01 m/s | 24.7 |  | 2.2 | m/s |  | 4.01 | m/s | 0.16722 | 0.0091508 | 0.18949 |  | 1.5 | 3 | 0.003 | 63.1647 | 9.0278 | 7.5382 | 0.029215 | 0.71681 | 0.41852
2025-05-19 10:27 | 22 | Remove | 2025-05-19 | 10:27 | US | GS | + | 1.5 | g | 0 | 112.5 | 11.219 | 1098.7 | 50542 | 0:11 | 28.6 | 2.19 m/s | 33.4 | 30.2 | 4.12 m/s | 25.8 |  | 2.19 | m/s |  | 4.12 | m/s | 0.17556 | 0.0091558 | 0.19865 |  | -1.5 | 1.5 | 0.0015 | 132.4333 | 9.3934 | 7.9167 | 0.03026 | 0.74707 | 0.20078
2025-05-19 10:28 | 23 | Remove | 2025-05-19 | 10:28 | ST | GS | + | 1.5 | g | 0 | 112.4 | 11.207 | 1097.4 | 50551 | 0:11 | 28.7 | 2.37 m/s | 33 | 30.3 | 3.8 m/s | 24.8 |  | 2.37 | m/s |  | 3.8 | m/s | 0.18389 | 0.009145 | 0.20779 |  | 0 | 1.5 | 0.0015 | 138.53 | 9.3319 | 7.6511 | 0.032533 | 0.7796 | 0.19241
2025-05-19 10:28 | 24 | Remove | 2025-05-19 | 10:28 | ST | GS | + | 1.5 | g | 0 | 112.4 | 11.238 | 1100.4 | 50560 | 0:12 | 28.7 | 2.42 m/s | 32.4 | 30.3 | 3.88 m/s | 24.4 |  | 2.42 | m/s |  | 3.88 | m/s | 0.19222 | 0.00917 | 0.21696 |  | 0 | 1.5 | 0.0015 | 144.6433 | 9.1622 | 7.5277 | 0.032615 | 0.81222 | 0.18468
2025-05-19 10:29 | 25 | Remove | 2025-05-19 | 10:29 | ST | GS | + | 1.5 | g | 0 | 112.3 | 11.254 | 1103.4 | 50569 | 0:12 | 28.7 | 2.38 m/s | 31.9 | 30.3 | 3.84 m/s | 24 |  | 2.38 | m/s |  | 3.84 | m/s | 0.20056 | 0.009195 | 0.22616 |  | 0 | 1.5 | 0.0015 | 150.7733 | 9.0208 | 7.4043 | 0.031581 | 0.8438 | 0.17777
2025-05-19 10:29 | 26 | Remove | 2025-05-19 | 10:29 | ST | GS | + | 1 | g | 0 | 112.4 | 11.211 | 1098.4 | 50578 | 0:13 | 28.7 | 2.37 m/s | 34.1 | 30.4 | 3.76 m/s | 25.7 |  | 2.37 | m/s |  | 3.76 | m/s | 0.20889 | 0.0091533 | 0.23531 |  | -0.5 | 1 | 0.001 | 235.3133 | 9.6429 | 7.9718 | 0.033617 | 0.87742 | 0.11397
2025-05-19 10:30 | 27 | Remove | 2025-05-19 | 10:30 | ST | GS | - | 2 | g | 0 | 112.4 | 11.25 | 1102.9 | 50588 | 0:13 | 28.7 | 2.67 m/s | 31.8 | 30.4 | 3.89 m/s | 23.6 |  | 2.67 | m/s |  | 3.89 | m/s | 0.21722 | 0.0091908 | 0.2445 |  | 1 | 2 | 0.002 | 122.2521 | 8.9925 | 7.3204 | 0.035318 | 0.91273 | 0.21912
2025-05-19 10:30 | 28 | Remove | 2025-05-19 | 10:30 | ST | GS | - | 3.5 | g | 0 | 112.3 | 11.233 | 1100.6 | 50597 | 0:14 | 28.7 | 3.02 m/s | 34.7 | 30.4 | 3.79 m/s | 25.3 |  | 3.02 | m/s |  | 3.79 | m/s | 0.22556 | 0.0091717 | 0.25368 |  | 1.5 | 3.5 | 0.0035 | 72.4788 | 9.8126 | 7.8477 | 0.043591 | 0.95632 | 0.36598
2025-05-19 10:31 | 29 | Remove | 2025-05-19 | 10:31 | ST | GS | + | 0 | g | 0 | 112.3 | 11.244 | 1102.2 | 50606 | 0:14 | 28.7 | 2.5 m/s | 33.3 | 30.4 | 3.81 m/s | 24.5 |  | 2.5 | m/s |  | 3.81 | m/s | 0.23389 | 0.009185 | 0.26286 |  | -3.5 | 0 | 0 | 0 | 9.4167 | 7.5996 | 0.034629 | 0.99095 | 0
2025-05-19 10:31 | 30 | Remove | 2025-05-19 | 10:31 | ST | GS | - | 2.5 | g | 0 | 112.4 | 11.209 | 1097.5 | 50615 | 0:15 | 28.7 | 2.71 m/s | 34.7 | 30.4 | 3.73 m/s | 25.4 |  | 2.71 | m/s |  | 3.73 | m/s | 0.24222 | 0.0091458 | 0.27201 |  | 2.5 | 2.5 | 0.0025 | 108.8027 | 9.8126 | 7.8787 | 0.039116 | 1.0301 | 0.2427
2025-05-19 10:32 | 31 | Keep | 2025-05-19 | 10:32 | ST | GS | + | 0 | g | 0 | 112.4 | 11.247 | 1102.5 | 50624 | 0:15 | 28.7 | 2.48 m/s | 32.2 | 30.4 | 3.84 m/s | 23.4 |  | 2.48 | m/s |  | 3.84 | m/s | 0.25056 | 0.0091875 | 0.28119 |  | -2.5 | 0 | 0 | 0 | 9.1056 | 7.2584 | 0.033217 | 1.0633 | 0
2025-05-19 10:32 | 32 | Remove | 2025-05-19 | 10:32 | ST | GS | + | 0 | g | 0 | 112.4 | 11.273 | 1105.2 | 50633 | 0:16 | 28.7 | 2.5 m/s | 32.1 | 30.4 | 3.84 m/s | 23.5 |  | 2.5 | m/s |  | 3.84 | m/s | 0.25889 | 0.00921 | 0.2904 |  | 0 | 0 | 0 | 0 | 9.0774 | 7.2894 | 0.033381 | 1.0967 | 0
2025-05-19 10:33 | 33 | Remove | 2025-05-19 | 10:33 | ST | GS | - | 1 | g | 0 | 112.4 | 11.254 | 1104.1 | 50643 | 0:16 | 28.7 | 2.57 m/s | 34.6 | 30.4 | 3.8 m/s | 25.1 |  | 2.57 | m/s |  | 3.8 | m/s | 0.26722 | 0.0092008 | 0.29961 |  | 1 | 1 | 0.001 | 299.605 | 9.7843 | 7.7857 | 0.036988 | 1.1337 | 0.08821
2025-05-19 10:33 | 34 | Remove | 2025-05-19 | 10:33 | ST | GS | + | 0 | g | 0 | 112.4 | 11.246 | 1102.6 | 50652 | 0:17 | 28.7 | 2.84 m/s | 31.6 | 30.4 | 3.89 m/s | 23 |  | 2.84 | m/s |  | 3.89 | m/s | 0.27583 | 0.0091883 | 0.30879 |  | -1 | 0 | 0 | 0 | 8.936 | 7.1343 | 0.03733 | 1.171 | 0
2025-05-19 10:34 | 35 | Remove | 2025-05-19 | 10:34 | ST | GS | - | 2 | g | 0 | 112.3 | 11.251 | 1102.9 | 50661 | 0:17 | 28.7 | 2.45 m/s | 32.3 | 30.4 | 3.88 m/s | 23.7 |  | 2.45 | m/s |  | 3.88 | m/s | 0.28417 | 0.0091908 | 0.31798 |  | 2 | 2 | 0.002 | 158.9921 | 9.1339 | 7.3514 | 0.032917 | 1.2039 | 0.16613
2025-05-19 10:34 | 36 | Remove | 2025-05-19 | 10:34 | US | GS | - | 5.5 | g | 0 | 112.4 | 11.253 | 1103.8 | 50670 | 0:18 | 28.7 | 2.93 m/s | 31.8 | 30.4 | 3.77 m/s | 23.3 |  | 2.93 | m/s |  | 3.77 | m/s | 0.2925 | 0.0091983 | 0.32718 |  | 3.5 | 5.5 | 0.0055 | 59.4877 | 8.9925 | 7.2273 | 0.038757 | 1.2427 | 0.4426
2025-05-19 10:35 | 37 | Remove | 2025-05-19 | 10:35 | US | GS | - | 3.5 | g | 0 | 113 | 11.23 | 1101.4 | 50680 | 0:18 | 28.7 | 2.58 m/s | 31.8 | 30.4 | 3.89 m/s | 23.3 |  | 2.58 | m/s |  | 3.89 | m/s | 0.30083 | 0.0091783 | 0.33636 |  | -2 | 3.5 | 0.0035 | 96.1031 | 8.9925 | 7.2273 | 0.034127 | 1.2768 | 0.27413
2025-05-19 10:35 | 38 | Remove | 2025-05-19 | 10:35 | US | GS | - | 0.5 | g | 0 | 112.7 | 11.326 | 1112.7 | 50689 | 0:19 | 28.7 | 2.8 m/s | 33 | 30.3 | 3.76 m/s | 24.2 |  | 2.8 | m/s |  | 3.76 | m/s | 0.30917 | 0.0092725 | 0.34563 |  | -3 | 0.5 | 0.0005 | 691.2667 | 9.3319 | 7.466 | 0.038435 | 1.3152 | 0.038016
2025-05-19 10:36 | 39 | Remove | 2025-05-19 | 10:36 | ST | GS | + | 0 | g | 0 | 113 | 11.21 | 1098.9 | 50698 | 0:19 | 28.7 | 2.37 m/s | 40 | 30.3 | 4.0 m/s | 28.4 |  | 2.37 | m/s |  | 4 | m/s | 0.3175 | 0.0091575 | 0.35479 |  | -0.5 | 0 | 0 | 0 | 11.3113 | 8.7618 | 0.039433 | 1.3547 | 0
2025-05-19 10:36 | 40 | Remove | 2025-05-19 | 10:36 | ST | GS | - | 1.5 | g | 0 | 112.8 | 11.291 | 1108.7 | 50707 | 0:20 | 28.6 | 2.58 m/s | 33.2 | 30.4 | 3.92 m/s | 24.3 |  | 2.58 | m/s |  | 3.92 | m/s | 0.32583 | 0.0092392 | 0.36403 |  | 1.5 | 1.5 | 0.0015 | 242.6867 | 9.3371 | 7.5375 | 0.035435 | 1.3901 | 0.10791
2025-05-19 10:37 | 41 | Remove | 2025-05-19 | 10:37 | ST | GS | + | 0 | g | 0 | 112.8 | 11.299 | 1111.2 | 50717 | 0:20 | 28.7 | 2.2 m/s | 34.6 | 30.4 | 3.88 m/s | 25.3 |  | 2.2 | m/s |  | 3.88 | m/s | 0.33417 | 0.00926 | 0.37329 |  | -1.5 | 0 | 0 | 0 | 9.7843 | 7.8477 | 0.031663 | 1.4218 | 0
2025-05-19 10:37 | 42 | Remove | 2025-05-19 | 10:37 | US | GS | - | 6.5 | g | 0 | 112.7 | 11.338 | 1115.7 | 50726 | 0:21 | 28.7 | 2.25 m/s | 32.8 | 30.4 | 3.96 m/s | 23.8 |  | 2.25 | m/s |  | 3.96 | m/s | 0.3425 | 0.0092975 | 0.38259 |  | 6.5 | 6.5 | 0.0065 | 58.8596 | 9.2753 | 7.3824 | 0.030698 | 1.4525 | 0.44752
2025-05-19 10:38 | 43 | Remove | 2025-05-19 | 10:38 | ST | GS | - | 5.5 | g | 0 | 112.9 | 11.276 | 1108.3 | 50735 | 0:21 | 28.7 | 2.51 m/s | 33.2 | 30.5 | 3.97 m/s | 24.4 |  | 2.51 | m/s |  | 3.97 | m/s | 0.35083 | 0.0092358 | 0.39182 |  | -1 | 5.5 | 0.0055 | 71.2406 | 9.3884 | 7.6096 | 0.034663 | 1.4871 | 0.36984
2025-05-19 10:38 | 44 | Remove | 2025-05-19 | 10:38 | US | GS | + | 3.5 | g | 0 | 112.7 | 11.305 | 1111.1 | 50744 | 0:22 | 28.7 | 2.15 m/s | 33.5 | 30.5 | 3.97 m/s | 24.4 |  | 2.15 | m/s |  | 3.97 | m/s | 0.35917 | 0.0092592 | 0.40108 |  | -2 | 3.5 | 0.0035 | 114.595 | 9.4733 | 7.6096 | 0.02996 | 1.5171 | 0.23071
2025-05-19 10:39 | 45 | Remove | 2025-05-19 | 10:39 | ST | GS | - | 1 | g | 0 | 112.8 | 11.277 | 1108.2 | 50754 | 0:22 | 28.7 | 2.53 m/s | 33.4 | 30.5 | 3.79 m/s | 24.3 |  | 2.53 | m/s |  | 3.79 | m/s | 0.3675 | 0.009235 | 0.41032 |  | -2.5 | 1 | 0.001 | 410.3175 | 9.445 | 7.5784 | 0.03515 | 1.5522 | 0.064424
2025-05-19 10:39 | 46 | Remove | 2025-05-19 | 10:39 | US | GS | + | 0 | g | 0 | 112.8 | 11.282 | 1108.7 | 50763 | 0:23 | 28.7 | 2.62 m/s | 31.3 | 30.5 | 3.77 m/s | 22.5 |  | 2.62 | m/s |  | 3.77 | m/s | 0.37583 | 0.0092392 | 0.41956 |  | -1 | 0 | 0 | 0 | 8.8511 | 7.017 | 0.034112 | 1.5863 | 0
2025-05-19 10:40 | 47 | Remove | 2025-05-19 | 10:40 | ST | GS | + | 0 | g | 0 | 112.8 | 11.267 | 1106.8 | 50772 | 0:23 | 28.7 | 2.51 m/s | 31.3 | 30.5 | 3.77 m/s | 22.5 |  | 2.51 | m/s |  | 3.77 | m/s | 0.38417 | 0.0092233 | 0.42878 |  | 0 | 0 | 0 | 0 | 8.8511 | 7.017 | 0.032679 | 1.619 | 0
2025-05-19 10:40 | 48 | Remove | 2025-05-19 | 10:40 | ST | GS | + | 0.5 | g | 0 | 112.6 | 11.342 | 1115.6 | 50782 | 0:24 | 28.7 | 2.15 m/s | 32.4 | 30.5 | 4.04 m/s | 23.5 |  | 2.15 | m/s |  | 4.04 | m/s | 0.3925 | 0.0092967 | 0.43808 |  | 0.5 | 0.5 | 0.0005 | 876.1533 | 9.1622 | 7.3289 | 0.028976 | 1.648 | 0.03034
2025-05-19 10:41 | 49 | Remove | 2025-05-19 | 10:41 | ST | GS | + | 0 | g | 0 | 112.7 | 11.362 | 1118.3 | 50791 | 0:24 | 28.7 | 2.09 m/s | 33.5 | 30.5 | 4.04 m/s | 24.2 |  | 2.09 | m/s |  | 4.04 | m/s | 0.40083 | 0.0093192 | 0.4474 |  | -0.5 | 0 | 0 | 0 | 9.4733 | 7.5472 | 0.029124 | 1.6771 | 0
2025-05-19 10:41 | 50 | Remove | 2025-05-19 | 10:41 | US | GS | - | 5 | g | 0 | 112.6 | 11.343 | 1115.9 | 50800 | 0:25 | 28.7 | 2.15 m/s | 33 | 30.6 | 4.24 m/s | 23.8 |  | 2.15 | m/s |  | 4.24 | m/s | 0.40917 | 0.0092992 | 0.4567 |  | 5 | 5 | 0.005 | 91.339 | 9.3319 | 7.4626 | 0.029513 | 1.7066 | 0.29297
2025-05-19 10:42 | 51 | Remove | 2025-05-19 | 10:42 | ST | GS | + | 1 | g | 0 | 112.7 | 11.323 | 1114.2 | 50809 | 0:25 | 28.7 | 2.48 m/s | 32.4 | 30.6 | 4.07 m/s | 23.2 |  | 2.48 | m/s |  | 4.07 | m/s | 0.41778 | 0.009285 | 0.46598 |  | -4 | 1 | 0.001 | 465.98 | 9.1622 | 7.2745 | 0.033424 | 1.7401 | 0.057469
2025-05-19 10:42 | 52 | Remove | 2025-05-19 | 10:42 | US | GS | - | 2.5 | g | 0 | 112.6 | 11.383 | 1121.6 | 50819 | 0:26 | 28.7 | 2.2 m/s | 32.3 | 30.7 | 4.1 m/s | 23 |  | 2.2 | m/s |  | 4.1 | m/s | 0.42611 | 0.0093467 | 0.47533 |  | 1.5 | 2.5 | 0.0025 | 190.1307 | 9.1339 | 7.2508 | 0.029558 | 1.7696 | 0.14127
2025-05-19 10:43 | 53 | Remove | 2025-05-19 | 10:43 | ST | GS | + | 0.5 | g | 0 | 112.6 | 11.433 | 1127.4 | 50828 | 0:26 | 28.7 | 2.15 m/s | 32.7 | 30.7 | 4.12 m/s | 22.9 |  | 2.15 | m/s |  | 4.12 | m/s | 0.43444 | 0.009395 | 0.48472 |  | -2 | 0.5 | 0.0005 | 969.4433 | 9.247 | 7.2193 | 0.029244 | 1.7989 | 0.027795
2025-05-19 10:43 | 54 | Remove | 2025-05-19 | 10:43 | ST | GS | + | 0 | g | 0 | 112.6 | 11.418 | 1124.9 | 50838 | 0:27 | 28.8 | 2.04 m/s | 32.4 | 30.7 | 4.4 m/s | 22.8 |  | 2.04 | m/s |  | 4.4 | m/s | 0.44278 | 0.0093742 | 0.4941 |  | -0.5 | 0 | 0 | 0 | 9.2125 | 7.1878 | 0.027645 | 1.8265 | 0
2025-05-19 10:44 | 55 | Remove | 2025-05-19 | 10:44 | ST | GS | - | 2.5 | g | 0 | 112.7 | 11.391 | 1122.9 | 50847 | 0:27 | 28.8 | 2.23 m/s | 32.5 | 30.8 | 4.0 m/s | 23 |  | 2.23 | m/s |  | 4 | m/s | 0.45111 | 0.0093575 | 0.50345 |  | 2.5 | 2.5 | 0.0025 | 201.3813 | 9.2409 | 7.29 | 0.030313 | 1.8568 | 0.13464
2025-05-19 10:44 | 56 | Remove | 2025-05-19 | 10:44 | ST | GS | - | 1 | g | 0 | 112.7 | 11.369 | 1120.6 | 50856 | 0:28 | 28.8 | 2.55 m/s | 32 | 30.8 | 3.81 m/s | 22.5 |  | 2.55 | m/s |  | 3.81 | m/s | 0.45944 | 0.0093383 | 0.51279 |  | -1.5 | 1 | 0.001 | 512.7917 | 9.0987 | 7.1315 | 0.034129 | 1.8909 | 0.052884
2025-05-19 10:45 | 57 | Remove | 2025-05-19 | 10:45 | ST | GS | - | 1.5 | g | 0 | 112.7 | 11.355 | 1117.6 | 50866 | 0:28 | 28.8 | 2.25 m/s | 32 | 30.8 | 3.86 m/s | 22.7 |  | 2.25 | m/s |  | 3.86 | m/s | 0.46778 | 0.0093133 | 0.52211 |  | 0.5 | 1.5 | 0.0015 | 348.07 | 9.0987 | 7.1949 | 0.030114 | 1.9211 | 0.078082
2025-05-19 10:45 | 58 | Remove | 2025-05-19 | 10:45 | ST | GS | - | 1 | g | 0 | 112.7 | 11.342 | 1115.6 | 50875 | 0:29 | 28.8 | 2.33 m/s | 31.1 | 30.7 | 3.89 m/s | 22.3 |  | 2.33 | m/s |  | 3.89 | m/s | 0.47611 | 0.0092967 | 0.5314 |  | -0.5 | 1 | 0.001 | 531.4017 | 8.8428 | 7.0301 | 0.030308 | 1.9514 | 0.051246
2025-05-19 10:46 | 59 | Remove | 2025-05-19 | 10:46 | ST | GS | - | 3.5 | g | 0 | 112.6 | 11.347 | 1117.4 | 50884 | 0:29 | 28.8 | 2.5 m/s | 31.6 | 30.7 | 3.93 m/s | 22.5 |  | 2.5 | m/s |  | 3.93 | m/s | 0.48444 | 0.0093117 | 0.54071 |  | 2.5 | 3.5 | 0.0035 | 154.4895 | 8.985 | 7.0932 | 0.033042 | 1.9844 | 0.17638
2025-05-19 10:46 | 60 | Remove | 2025-05-19 | 10:46 | US | GS | + | 3 | g | 0 | 112.6 | 11.358 | 1118.5 | 50894 | 0:30 | 28.8 | 2.51 m/s | 30.8 | 30.7 | 3.76 m/s | 22.1 |  | 2.51 | m/s |  | 3.76 | m/s | 0.49278 | 0.0093208 | 0.55003 |  | -0.5 | 3 | 0.003 | 183.3447 | 8.7575 | 6.9671 | 0.032334 | 2.0167 | 0.14875
2025-05-19 10:47 | 61 | Keep | 2025-05-19 | 10:47 | US | GS | + | 2.5 | g | 0 | 112.6 | 11.386 | 1121.9 | 50903 | 0:30 | 28.8 | 2.26 m/s | 31.8 | 30.7 | 3.97 m/s | 22.8 |  | 2.26 | m/s |  | 3.97 | m/s | 0.50111 | 0.0093492 | 0.55938 |  | -0.5 | 2.5 | 0.0025 | 223.7533 | 9.0419 | 7.1878 | 0.030059 | 2.0468 | 0.12214
2025-05-19 10:47 | 62 | Remove | 2025-05-19 | 10:47 | US | GS | + | 1 | g | 0 | 112.6 | 11.378 | 1120.4 | 50913 | 0:31 | 28.8 | 2.19 m/s | 33.2 | 30.7 | 3.96 m/s | 23.5 |  | 2.19 | m/s |  | 3.96 | m/s | 0.50944 | 0.0093367 | 0.56872 |  | -1.5 | 1 | 0.001 | 568.72 | 9.44 | 7.4084 | 0.03041 | 2.0772 | 0.048142
2025-05-19 10:48 | 63 | Remove | 2025-05-19 | 10:48 | US | GS | + | 0 | g | 0 | 112.5 | 11.43 | 1126.1 | 50922 | 0:31 | 28.8 | 2.34 m/s | 32.9 | 30.7 | 4.03 m/s | 23.2 |  | 2.34 | m/s |  | 4.03 | m/s | 0.51778 | 0.0093842 | 0.5781 |  | -1 | 0 | 0 | 0 | 9.3546 | 7.3139 | 0.032199 | 2.1094 | 0
2025-05-19 10:48 | 64 | Remove | 2025-05-19 | 10:48 | ST | GS | + | 2.5 | g | 0 | 112.5 | 11.425 | 1126.7 | 50931 | 0:32 | 28.8 | 2.35 m/s | 32 | 30.8 | 4.01 m/s | 22.6 |  | 2.35 | m/s |  | 4.01 | m/s | 0.52611 | 0.0093892 | 0.58749 |  | 2.5 | 2.5 | 0.0025 | 234.9973 | 9.0987 | 7.1632 | 0.031452 | 2.1409 | 0.11678
2025-05-19 10:49 | 65 | Remove | 2025-05-19 | 10:49 | ST | GS | + | 1 | g | 0 | 112.4 | 11.468 | 1131.3 | 50941 | 0:32 | 28.8 | 2.13 m/s | 32.7 | 30.8 | 4.07 m/s | 23.2 |  | 2.13 | m/s |  | 4.07 | m/s | 0.53444 | 0.0094275 | 0.59692 |  | -1.5 | 1 | 0.001 | 596.9208 | 9.2978 | 7.3534 | 0.029131 | 2.17 | 0.046083
2025-05-19 10:49 | 66 | Remove | 2025-05-19 | 10:49 | ST | GS | + | 1.5 | g | 0 | 112.5 | 11.451 | 1129.7 | 50950 | 0:33 | 28.9 | 2.18 m/s | 32.5 | 30.8 | 3.9 m/s | 23.2 |  | 2.18 | m/s |  | 3.9 | m/s | 0.54278 | 0.0094142 | 0.60633 |  | 0.5 | 1.5 | 0.0015 | 404.2233 | 9.2916 | 7.3534 | 0.029795 | 2.1998 | 0.068188
2025-05-19 10:50 | 67 | Remove | 2025-05-19 | 10:50 | US | GS | - | 14 | g | 0 | 112.5 | 11.419 | 1125.1 | 50960 | 0:33 | 28.9 | 2.33 m/s | 35.3 | 30.9 | 4.3 m/s | 24.8 |  | 2.33 | m/s |  | 4.3 | m/s | 0.55111 | 0.0093758 | 0.61571 |  | 12.5 | 14 | 0.014 | 43.9793 | 10.0921 | 7.903 | 0.034589 | 2.2344 | 0.62657
2025-05-19 10:50 | 68 | Remove | 2025-05-19 | 10:50 | US | GS | - | 11 | g | 0 | 112.5 | 11.371 | 1119.8 | 50969 | 0:34 | 28.9 | 2.7 m/s | 34.3 | 30.9 | 4.07 m/s | 23.8 |  | 2.7 | m/s |  | 4.07 | m/s | 0.55972 | 0.0093317 | 0.62504 |  | -3 | 11 | 0.011 | 56.822 | 9.8062 | 7.5843 | 0.038946 | 2.2733 | 0.48387
2025-05-19 10:51 | 69 | Remove | 2025-05-19 | 10:51 | ST | GS | - | 2 | g | 0 | 112.5 | 11.369 | 1119.3 | 50978 | 0:34 | 28.8 | 2.4 m/s | 32 | 30.9 | 4.29 m/s | 22.3 |  | 2.4 | m/s |  | 4.29 | m/s | 0.56806 | 0.0093275 | 0.63437 |  | -9 | 2 | 0.002 | 317.185 | 9.0987 | 7.1063 | 0.032121 | 2.3054 | 0.086751
2025-05-19 10:51 | 70 | Remove | 2025-05-19 | 10:51 | ST | GS | - | 8.5 | g | 0 | 112.6 | 11.381 | 1120.8 | 50988 | 0:35 | 28.8 | 2.27 m/s | 31.3 | 30.8 | 4.0 m/s | 22 |  | 2.27 | m/s |  | 4 | m/s | 0.57639 | 0.00934 | 0.64371 |  | 6.5 | 8.5 | 0.0085 | 75.7306 | 8.8997 | 6.973 | 0.029717 | 2.3352 | 0.364
2025-05-19 10:52 | 71 | Remove | 2025-05-19 | 10:52 | ST | GS | - | 2.5 | g | 0 | 112.5 | 11.35 | 1117.4 | 50997 | 0:35 | 28.8 | 2.96 m/s | 30.7 | 30.8 | 3.75 m/s | 21.6 |  | 2.96 | m/s |  | 3.75 | m/s | 0.58472 | 0.0093117 | 0.65302 |  | -6 | 2.5 | 0.0025 | 261.2087 | 8.7291 | 6.8463 | 0.038007 | 2.3732 | 0.10534
2025-05-19 10:52 | 72 | Remove | 2025-05-19 | 10:52 | ST | GS | - | 4 | g | 0 | 112.5 | 11.363 | 1118.6 | 51006 | 0:36 | 28.8 | 2.45 m/s | 32.7 | 30.8 | 3.92 m/s | 22.8 |  | 2.45 | m/s |  | 3.92 | m/s | 0.59306 | 0.0093217 | 0.66234 |  | 1.5 | 4 | 0.004 | 165.5858 | 9.2978 | 7.2266 | 0.033508 | 2.4067 | 0.1662
2025-05-19 10:53 | 73 | Remove | 2025-05-19 | 10:53 | ST | GS | - | 1.5 | g | 0 | 112.5 | 11.381 | 1120.8 | 51016 | 0:36 | 28.8 | 2.67 m/s | 32.5 | 30.7 | 3.69 m/s | 23.1 |  | 2.67 | m/s |  | 3.69 | m/s | 0.60139 | 0.00934 | 0.67168 |  | -2.5 | 1.5 | 0.0015 | 447.7889 | 9.2409 | 7.2823 | 0.036293 | 2.443 | 0.061401
2025-05-19 10:53 | 74 | Remove | 2025-05-19 | 10:53 | ST | GS | - | 4 | g | 0 | 112.5 | 11.348 | 1116.7 | 51025 | 0:37 | 28.8 | 2.3 m/s | 31.5 | 30.7 | 4.1 m/s | 22.5 |  | 2.3 | m/s |  | 4.1 | m/s | 0.60972 | 0.0093058 | 0.68099 |  | 2.5 | 4 | 0.004 | 170.2473 | 8.9566 | 7.0932 | 0.030302 | 2.4733 | 0.16173
2025-05-19 10:54 | 75 | Remove | 2025-05-19 | 10:54 | US | GS | - | 6.5 | g | 0 | 112.6 | 11.34 | 1115.6 | 51034 | 0:37 | 28.8 | 2.75 m/s | 31.3 | 30.7 | 3.98 m/s | 22.1 |  | 2.75 | m/s |  | 3.98 | m/s | 0.61806 | 0.0092967 | 0.69029 |  | 2.5 | 6.5 | 0.0065 | 106.1978 | 8.8997 | 6.9671 | 0.036001 | 2.5093 | 0.25904
2025-05-19 10:54 | 76 | Remove | 2025-05-19 | 10:54 | ST | GS | - | 4 | g | 0 | 112.6 | 11.343 | 1116.5 | 51044 | 0:38 | 28.8 | 2.47 m/s | 32.5 | 30.7 | 3.85 m/s | 23.2 |  | 2.47 | m/s |  | 3.85 | m/s | 0.62639 | 0.0093042 | 0.69959 |  | -2.5 | 4 | 0.004 | 174.8975 | 9.2409 | 7.3139 | 0.033575 | 2.5428 | 0.1573
2025-05-19 10:55 | 77 | Remove | 2025-05-19 | 10:55 | US | GS | - | 6 | g | 0 | 112.6 | 11.386 | 1121.6 | 51053 | 0:38 | 28.8 | 2.25 m/s | 31.7 | 30.7 | 4.16 m/s | 22.6 |  | 2.25 | m/s |  | 4.16 | m/s | 0.63472 | 0.0093467 | 0.70894 |  | 2 | 6 | 0.006 | 118.1561 | 9.0134 | 7.1247 | 0.029832 | 2.5727 | 0.23322
2025-05-19 10:55 | 78 | Remove | 2025-05-19 | 10:55 | ST | GS | + | 0 | g | 0 | 112.5 | 11.369 | 1119.7 | 51062 | 0:39 | 28.8 | 2.27 m/s | 31.9 | 30.7 | 4.07 m/s | 22.7 |  | 2.27 | m/s |  | 4.07 | m/s | 0.64306 | 0.0093308 | 0.71827 |  | -6 | 0 | 0 | 0 | 9.0703 | 7.1562 | 0.030287 | 2.603 | 0
2025-05-19 10:56 | 79 | Remove | 2025-05-19 | 10:56 | US | GS | + | 0 | g | 0 | 112.5 | 11.452 | 1130.4 | 51072 | 0:39 | 28.8 | 2.33 m/s | 32.3 | 30.7 | 4.27 m/s | 22.8 |  | 2.33 | m/s |  | 4.27 | m/s | 0.65139 | 0.00942 | 0.72769 |  | 0 | 0 | 0 | 0 | 9.184 | 7.1878 | 0.031477 | 2.6344 | 0
2025-05-19 10:56 | 80 | Remove | 2025-05-19 | 10:56 | ST | GS | - | 6.5 | g | 0 | 112.5 | 11.381 | 1121 | 51081 | 0:40 | 28.8 | 2.48 m/s | 33.6 | 30.8 | 4.32 m/s | 23.8 |  | 2.48 | m/s |  | 4.32 | m/s | 0.65972 | 0.0093417 | 0.73703 |  | 6.5 | 6.5 | 0.0065 | 113.3891 | 9.5537 | 7.5436 | 0.034852 | 2.6693 | 0.24351
2025-05-19 10:57 | 81 | Remove | 2025-05-19 | 10:57 | ST | GS | - | 3 | g | 0 | 112.5 | 11.373 | 1120.1 | 51091 | 0:40 | 28.8 | 2.75 m/s | 33.9 | 30.8 | 4.12 m/s | 24.1 |  | 2.75 | m/s |  | 4.12 | m/s | 0.66806 | 0.0093342 | 0.74636 |  | -3.5 | 3 | 0.003 | 248.7878 | 9.639 | 7.6387 | 0.038991 | 2.7083 | 0.11077
2025-05-19 10:57 | 82 | Remove | 2025-05-19 | 10:57 | ST | GS | - | 1.5 | g | 0 | 112.5 | 11.411 | 1124.5 | 51100 | 0:41 | 28.8 | 2.11 m/s | 33 | 30.8 | 3.81 m/s | 22.8 |  | 2.11 | m/s |  | 3.81 | m/s | 0.67639 | 0.0093708 | 0.75573 |  | -1.5 | 1.5 | 0.0015 | 503.8228 | 9.3831 | 7.2266 | 0.029123 | 2.7374 | 0.054796
2025-05-19 10:58 | 83 | Remove | 2025-05-19 | 10:58 | US | GS | - | 4 | g | 0 | 112.4 | 11.393 | 1122.7 | 51109 | 0:41 | 28.8 | 2.4 m/s | 34 | 30.7 | 3.86 m/s | 23.8 |  | 2.4 | m/s |  | 3.86 | m/s | 0.68472 | 0.0093558 | 0.76509 |  | 2.5 | 4 | 0.004 | 191.2725 | 9.6674 | 7.503 | 0.034129 | 2.7715 | 0.14432
2025-05-19 10:58 | 84 | Remove | 2025-05-19 | 10:58 | US | GS | - | 2 | g | 0 | 112.5 | 11.371 | 1120.2 | 51119 | 0:42 | 28.8 | 3.07 m/s | 32.1 | 30.7 | 3.8 m/s | 22.6 |  | 3.07 | m/s |  | 3.8 | m/s | 0.69333 | 0.009335 | 0.77442 |  | -2 | 2 | 0.002 | 387.2125 | 9.1272 | 7.1247 | 0.041217 | 2.8128 | 0.071105
2025-05-19 10:59 | 85 | Remove | 2025-05-19 | 10:59 | ST | GS | - | 0.5 | g | 0 | 112.6 | 11.383 | 1121.8 | 51128 | 0:42 | 28.8 | 2.6 m/s | 32.4 | 30.7 | 3.93 m/s | 22.8 |  | 2.6 | m/s |  | 3.93 | m/s | 0.70167 | 0.0093483 | 0.78377 |  | -1.5 | 0.5 | 0.0005 | 1567.5467 | 9.2125 | 7.1878 | 0.035233 | 2.848 | 0.017556
2025-05-19 10:59 | 86 | Remove | 2025-05-19 | 10:59 | US | GS | - | 1 | g | 0 | 112.5 | 11.359 | 1118.4 | 51137 | 0:43 | 28.8 | 2.57 m/s | 32 | 30.7 | 3.79 m/s | 22.8 |  | 2.57 | m/s |  | 3.79 | m/s | 0.71 | 0.00932 | 0.79309 |  | 0.5 | 1 | 0.001 | 793.0933 | 9.0987 | 7.1878 | 0.034397 | 2.8824 | 0.034694
2025-05-19 11:00 | 87 | Remove | 2025-05-19 | 11:00 | US | GS | + | 1.5 | g | 0 | 112.4 | 11.372 | 1120.2 | 51147 | 0:43 | 28.8 | 2.47 m/s | 33.9 | 30.8 | 4.29 m/s | 23.6 |  | 2.47 | m/s |  | 4.29 | m/s | 0.71833 | 0.009335 | 0.80243 |  | 0.5 | 1.5 | 0.0015 | 534.9522 | 9.639 | 7.4802 | 0.035021 | 2.9174 | 0.051416
2025-05-19 11:00 | 88 | Remove | 2025-05-19 | 11:00 | ST | GS | + | 4.5 | g | 0 | 112.5 | 11.367 | 1118.4 | 51156 | 0:44 | 28.8 | 2.51 m/s | 31.4 | 30.7 | 3.9 m/s | 22.1 |  | 2.51 | m/s |  | 3.9 | m/s | 0.72667 | 0.00932 | 0.81175 |  | 3 | 4.5 | 0.0045 | 180.3885 | 8.9281 | 6.9671 | 0.032964 | 2.9504 | 0.15252
2025-05-19 11:01 | 89 | Remove | 2025-05-19 | 11:01 | ST | GS | + | 0.5 | g | 0 | 112.4 | 11.384 | 1119.6 | 51166 | 0:44 | 28.8 | 2.61 m/s | 30.8 | 30.7 | 3.94 m/s | 21.9 |  | 2.61 | m/s |  | 3.94 | m/s | 0.735 | 0.00933 | 0.82108 |  | -4 | 0.5 | 0.0005 | 1642.1567 | 8.7575 | 6.904 | 0.033622 | 2.984 | 0.016756
2025-05-19 11:01 | 90 | Remove | 2025-05-19 | 11:01 | ST | GS | + | 0.5 | g | 0 | 112.4 | 11.411 | 1124.3 | 51175 | 0:45 | 28.8 | 2.26 m/s | 32.5 | 30.7 | 3.88 m/s | 23.4 |  | 2.26 | m/s |  | 3.88 | m/s | 0.74333 | 0.0093692 | 0.83045 |  | 0 | 0.5 | 0.0005 | 1660.895 | 9.2409 | 7.3769 | 0.03072 | 3.0147 | 0.016585
2025-05-19 11:02 | 91 | Keep | 2025-05-19 | 11:02 | US | GS | - | 1.5 | g | 0 | 112.5 | 11.401 | 1122.6 | 51184 | 0:45 | 28.8 | 2.34 m/s | 33.3 | 30.7 | 4.0 m/s | 24.3 |  | 2.34 | m/s |  | 4 | m/s | 0.75167 | 0.009355 | 0.8398 |  | 1 | 1.5 | 0.0015 | 559.8683 | 9.4684 | 7.6606 | 0.032591 | 3.0473 | 0.049224
2025-05-19 11:02 | 92 | Remove | 2025-05-19 | 11:02 | ST | GS | - | 4 | g | 0 | 112.5 | 11.386 | 1121.7 | 51194 | 0:46 | 28.8 | 2.62 m/s | 33.7 | 30.7 | 3.9 m/s | 23.5 |  | 2.62 | m/s |  | 3.9 | m/s | 0.76 | 0.0093475 | 0.84915 |  | 2.5 | 4 | 0.004 | 212.2875 | 9.5821 | 7.4084 | 0.036929 | 3.0842 | 0.12969
2025-05-19 11:03 | 93 | Remove | 2025-05-19 | 11:03 | ST | GS | - | 3.5 | g | 0 | 112.4 | 11.442 | 1128.9 | 51203 | 0:46 | 28.8 | 2.16 m/s | 33.3 | 30.7 | 4.12 m/s | 23.8 |  | 2.16 | m/s |  | 4.12 | m/s | 0.76833 | 0.0094075 | 0.85856 |  | -0.5 | 3.5 | 0.0035 | 245.3021 | 9.4684 | 7.503 | 0.030084 | 3.1143 | 0.11238
2025-05-19 11:03 | 94 | Remove | 2025-05-19 | 11:03 | ST | GS | - | 3.5 | g | 0 | 112.4 | 11.356 | 1117.5 | 51213 | 0:47 | 28.8 | 2.67 m/s | 36.2 | 30.7 | 3.9 m/s | 25.2 |  | 2.67 | m/s |  | 3.9 | m/s | 0.77667 | 0.0093125 | 0.86787 |  | 0 | 3.5 | 0.0035 | 247.9629 | 10.293 | 7.9444 | 0.040425 | 3.1547 | 0.11094
2025-05-19 11:04 | 95 | Remove | 2025-05-19 | 11:04 | US | GS | - | 7 | g | 0 | 112.4 | 11.402 | 1125 | 51222 | 0:47 | 28.8 | 2.38 m/s | 31.2 | 30.7 | 3.79 m/s | 22.1 |  | 2.38 | m/s |  | 3.79 | m/s | 0.785 | 0.009375 | 0.87724 |  | 3.5 | 7 | 0.007 | 125.3207 | 8.8713 | 6.9671 | 0.031057 | 3.1858 | 0.21973
2025-05-19 11:04 | 96 | Remove | 2025-05-19 | 11:04 | ST | GS | - | 1.5 | g | 0 | 112.4 | 11.368 | 1119.9 | 51231 | 0:48 | 28.8 | 2.6 m/s | 32.3 | 30.7 | 3.81 m/s | 22.5 |  | 2.6 | m/s |  | 3.81 | m/s | 0.79333 | 0.0093325 | 0.88658 |  | -5.5 | 1.5 | 0.0015 | 591.0517 | 9.184 | 7.0932 | 0.035124 | 3.2209 | 0.046571
2025-05-19 11:05 | 97 | Remove | 2025-05-19 | 11:05 | ST | GS | - | 6 | g | 0 | 112.4 | 11.379 | 1121.4 | 51241 | 0:48 | 28.8 | 2.34 m/s | 33.2 | 30.7 | 3.99 m/s | 25.2 |  | 2.34 | m/s |  | 3.99 | m/s | 0.80167 | 0.009345 | 0.89592 |  | 4.5 | 6 | 0.006 | 149.3204 | 9.44 | 7.9444 | 0.032493 | 3.2534 | 0.18442
2025-05-19 11:05 | 98 | Remove | 2025-05-19 | 11:05 | US | GS | - | 4.5 | g | 0 | 112.4 | 11.388 | 1123.2 | 51250 | 0:49 | 28.8 | 2.68 m/s | 32.4 | 30.7 | 3.84 m/s | 22.7 |  | 2.68 | m/s |  | 3.84 | m/s | 0.81 | 0.00936 | 0.90528 |  | -1.5 | 4.5 | 0.0045 | 201.1739 | 9.2125 | 7.1562 | 0.036317 | 3.2897 | 0.13679
2025-05-19 11:06 | 99 | Remove | 2025-05-19 | 11:06 | US | GS | + | 4 | g | 0 | 112.3 | 11.358 | 1118.3 | 51259 | 0:49 | 28.8 | 2.74 m/s | 35 | 30.7 | 3.79 m/s | 24.6 |  | 2.74 | m/s |  | 3.79 | m/s | 0.81833 | 0.0093192 | 0.9146 |  | -0.5 | 4 | 0.004 | 228.6504 | 9.9518 | 7.7552 | 0.04011 | 3.3298 | 0.12013
2025-05-19 11:06 | 100 | Remove | 2025-05-19 | 11:06 | US | GS | - | 3 | g | 0 | 112.2 | 11.363 | 1119 | 51269 | 0:50 | 28.8 | 2.72 m/s | 34.1 | 30.7 | 3.86 m/s | 23.9 |  | 2.72 | m/s |  | 3.86 | m/s | 0.82667 | 0.009325 | 0.92393 |  | -1 | 3 | 0.003 | 307.9756 | 9.6959 | 7.5345 | 0.038793 | 3.3686 | 0.089057
2025-05-19 11:07 | 101 | Remove | 2025-05-19 | 11:07 | US | GS | - | 7 | g | 0 | 112.4 | 11.363 | 1119.8 | 51278 | 0:50 | 28.8 | 2.6 m/s | 32.4 | 30.7 | 4.03 m/s | 23.4 |  | 2.6 | m/s |  | 4.03 | m/s | 0.83528 | 0.0093317 | 0.93326 |  | 4 | 7 | 0.007 | 133.3226 | 9.2125 | 7.3769 | 0.035233 | 3.4039 | 0.20565
2025-05-19 11:07 | 102 | Remove | 2025-05-19 | 11:07 | ST | GS | - | 5.5 | g | 0 | 112.4 | 11.394 | 1123.1 | 51288 | 0:51 | 28.8 | 2.47 m/s | 31.4 | 30.7 | 4.35 m/s | 22.1 |  | 2.47 | m/s |  | 4.35 | m/s | 0.84361 | 0.0093592 | 0.94262 |  | -1.5 | 5.5 | 0.0055 | 171.385 | 8.9281 | 6.9671 | 0.032438 | 3.4363 | 0.16006
2025-05-19 11:08 | 103 | Remove | 2025-05-19 | 11:08 | US | GS | - | 4.5 | g | 0 | 112.5 | 11.36 | 1118.9 | 51297 | 0:51 | 28.8 | 2.6 m/s | 33.5 | 30.7 | 3.73 m/s | 23.9 |  | 2.6 | m/s |  | 3.73 | m/s | 0.85194 | 0.0093242 | 0.95194 |  | -1 | 4.5 | 0.0045 | 211.5426 | 9.5253 | 7.5345 | 0.036429 | 3.4727 | 0.12958
2025-05-19 11:08 | 104 | Remove | 2025-05-19 | 11:08 | ST | GS | - | 3.5 | g | 0 | 112.3 | 11.379 | 1120.3 | 51306 | 0:52 | 28.8 | 2.81 m/s | 30.3 | 30.6 | 3.88 m/s | 21.8 |  | 2.81 | m/s |  | 3.88 | m/s | 0.86028 | 0.0093358 | 0.96128 |  | -1 | 3.5 | 0.0035 | 274.6507 | 8.6154 | 6.8355 | 0.035611 | 3.5083 | 0.099762
2025-05-19 11:09 | 105 | Remove | 2025-05-19 | 11:09 | ST | GS | - | 5 | g | 0 | 112.3 | 11.396 | 1122.8 | 51316 | 0:52 | 28.8 | 2.51 m/s | 33 | 30.6 | 3.8 m/s | 23.4 |  | 2.51 | m/s |  | 3.8 | m/s | 0.86861 | 0.0093567 | 0.97063 |  | 1.5 | 5 | 0.005 | 194.1268 | 9.3831 | 7.3372 | 0.034643 | 3.543 | 0.14112
2025-05-19 11:09 | 106 | Remove | 2025-05-19 | 11:09 | ST | GS | - | 6 | g | 0 | 112.2 | 11.395 | 1122.2 | 51325 | 0:53 | 28.8 | 2.67 m/s | 33.5 | 30.6 | 3.93 m/s | 24.8 |  | 2.67 | m/s |  | 3.93 | m/s | 0.87694 | 0.0093517 | 0.97999 |  | 1 | 6 | 0.006 | 163.331 | 9.5253 | 7.7762 | 0.03741 | 3.5804 | 0.16758
2025-05-19 11:10 | 107 | Remove | 2025-05-19 | 11:10 | US | GS | - | 1.5 | g | 0 | 112.3 | 11.448 | 1129.6 | 51334 | 0:53 | 28.8 | 2.2 m/s | 32.9 | 30.6 | 4.0 m/s | 23.3 |  | 2.2 | m/s |  | 4 | m/s | 0.88528 | 0.0094133 | 0.9894 |  | -4.5 | 1.5 | 0.0015 | 659.5994 | 9.3546 | 7.3059 | 0.030273 | 3.6107 | 0.041543
2025-05-19 11:10 | 108 | Remove | 2025-05-19 | 11:10 | ST | GS | - | 2 | g | 0 | 112.3 | 11.447 | 1129.9 | 51344 | 0:54 | 28.8 | 2.41 m/s | 33.5 | 30.7 | 3.88 m/s | 24.2 |  | 2.41 | m/s |  | 3.88 | m/s | 0.89361 | 0.0094158 | 0.99881 |  | 0.5 | 2 | 0.002 | 499.4075 | 9.5253 | 7.6291 | 0.033767 | 3.6444 | 0.054878
2025-05-19 11:11 | 109 | Remove | 2025-05-19 | 11:11 | US | GS | - | 8.5 | g | 0 | 112.4 | 11.382 | 1121.2 | 51353 | 0:54 | 28.8 | 2.3 m/s | 36.4 | 30.7 | 4.06 m/s | 25.4 |  | 2.3 | m/s |  | 4.06 | m/s | 0.90194 | 0.0093433 | 1.0082 |  | 6.5 | 8.5 | 0.0085 | 118.6069 | 10.3498 | 8.0074 | 0.035016 | 3.6795 | 0.23101
2025-05-19 11:11 | 110 | Remove | 2025-05-19 | 11:11 | ST | GS | - | 5.5 | g | 0 | 112.3 | 11.43 | 1127.2 | 51363 | 0:55 | 28.8 | 2.74 m/s | 32.3 | 30.8 | 3.68 m/s | 23.6 |  | 2.74 | m/s |  | 3.68 | m/s | 0.91028 | 0.0093933 | 1.0176 |  | -3 | 5.5 | 0.0055 | 185.0094 | 9.184 | 7.4802 | 0.037016 | 3.7165 | 0.14799
2025-05-19 11:12 | 111 | Remove | 2025-05-19 | 11:12 | ST | GS | - | 5.5 | g | 0 | 112.2 | 11.488 | 1134.2 | 51372 | 0:55 | 28.8 | 2.27 m/s | 34.1 | 30.8 | 3.85 m/s | 24.4 |  | 2.27 | m/s |  | 3.85 | m/s | 0.91861 | 0.0094517 | 1.027 |  | 0 | 5.5 | 0.0055 | 186.7279 | 9.6959 | 7.7337 | 0.032375 | 3.7488 | 0.14671
2025-05-19 11:12 | 112 | Remove | 2025-05-19 | 11:12 | US | GS | - | 7 | g | 0 | 112.2 | 11.463 | 1130.7 | 51382 | 0:56 | 28.9 | 2.33 m/s | 37.8 | 30.8 | 4.01 m/s | 26.1 |  | 2.33 | m/s |  | 4.01 | m/s | 0.92694 | 0.0094225 | 1.0364 |  | 1.5 | 7 | 0.007 | 148.0608 | 10.8068 | 8.2726 | 0.037039 | 3.7859 | 0.1849
2025-05-19 11:13 | 113 | Remove | 2025-05-19 | 11:13 | US | GS | - | 2.5 | g | 0 | 112.2 | 11.469 | 1131.8 | 51391 | 0:56 | 28.9 | 2.38 m/s | 35.1 | 30.8 | 4.15 m/s | 24.7 |  | 2.38 | m/s |  | 4.15 | m/s | 0.93528 | 0.0094317 | 1.0459 |  | -4.5 | 2.5 | 0.0025 | 418.343 | 10.0349 | 7.8288 | 0.035131 | 3.821 | 0.065428
2025-05-19 11:13 | 114 | Remove | 2025-05-19 | 11:13 | US | GS | - | 4.5 | g | 0 | 112.3 | 11.377 | 1120.8 | 51400 | 0:57 | 28.9 | 2.45 m/s | 33.6 | 30.8 | 3.89 m/s | 23.8 |  | 2.45 | m/s |  | 3.89 | m/s | 0.94361 | 0.00934 | 1.0552 |  | 2 | 4.5 | 0.0045 | 234.4883 | 9.6061 | 7.5436 | 0.034619 | 3.8556 | 0.11671
2025-05-19 11:14 | 115 | Remove | 2025-05-19 | 11:14 | US | GS | - | 11 | g | 0 | 112.3 | 11.379 | 1121.1 | 51410 | 0:57 | 28.9 | 2.74 m/s | 31.7 | 30.8 | 4.24 m/s | 22.5 |  | 2.74 | m/s |  | 4.24 | m/s | 0.95194 | 0.0093425 | 1.0645 |  | 6.5 | 11 | 0.011 | 96.7764 | 9.0629 | 7.1315 | 0.036527 | 3.8922 | 0.28262
2025-05-19 11:14 | 116 | Remove | 2025-05-19 | 11:14 | US | GS | - | 10 | g | 0 | 112.2 | 11.393 | 1123.2 | 51419 | 0:58 | 28.8 | 2.5 m/s | 30.8 | 30.7 | 3.76 m/s | 22 |  | 2.5 | m/s |  | 3.76 | m/s | 0.96028 | 0.00936 | 1.0739 |  | -1 | 10 | 0.01 | 107.39 | 8.7575 | 6.9356 | 0.032205 | 3.9244 | 0.25482
2025-05-19 11:15 | 117 | Remove | 2025-05-19 | 11:15 | US | GS | - | 8 | g | 0 | 112.2 | 11.419 | 1126.2 | 51429 | 0:58 | 28.8 | 2.74 m/s | 31.9 | 30.7 | 3.79 m/s | 22.5 |  | 2.74 | m/s |  | 3.79 | m/s | 0.96861 | 0.009385 | 1.0833 |  | -2 | 8 | 0.008 | 135.4106 | 9.0703 | 7.0932 | 0.036557 | 3.9609 | 0.20197
2025-05-19 11:15 | 118 | Remove | 2025-05-19 | 11:15 | ST | GS | - | 2.5 | g | 0 | 112.1 | 11.453 | 1129.8 | 51438 | 0:59 | 28.8 | 2.45 m/s | 33.1 | 30.7 | 4.04 m/s | 24.5 |  | 2.45 | m/s |  | 4.04 | m/s | 0.97722 | 0.009415 | 1.0927 |  | -5.5 | 2.5 | 0.0025 | 437.08 | 9.4115 | 7.7237 | 0.033918 | 3.9948 | 0.062581
2025-05-19 11:16 | 119 | Remove | 2025-05-19 | 11:16 | US | GS | - | 5 | g | 0 | 112.1 | 11.473 | 1132.1 | 51447 | 0:59 | 28.8 | 2.2 m/s | 37.4 | 30.8 | 3.98 m/s | 26.4 |  | 2.2 | m/s |  | 3.98 | m/s | 0.98556 | 0.0094342 | 1.1021 |  | 2.5 | 5 | 0.005 | 220.4268 | 10.6342 | 8.3677 | 0.034413 | 4.0293 | 0.12409
2025-05-19 11:16 | 120 | Remove | 2025-05-19 | 11:16 | ST | GS | + | 0 | g | 0 | 112.1 | 11.511 | 1136.9 | 51457 | 1:00 | 28.9 | 2.77 m/s | 33.6 | 30.8 | 3.76 m/s | 23.5 |  | 2.77 | m/s |  | 3.76 | m/s | 0.99389 | 0.0094742 | 1.1116 |  | -5 | 0 | 0 | 0 | 9.6061 | 7.4485 | 0.039141 | 4.0684 | 0
2025-05-19 11:17 | 121 | Keep | 2025-05-19 | 11:17 | ST | GS | + | 0 | g | 0 | 112.1 | 11.48 | 1133 | 51466 | 1:00 | 28.9 | 2.33 m/s | 32.3 | 30.8 | 4.23 m/s | 22.5 |  | 2.33 | m/s |  | 4.23 | m/s | 1.0022 | 0.0094417 | 1.121 |  | 0 | 0 | 0 | 0 | 9.2344 | 7.1315 | 0.03165 | 4.1 | 0
2025-05-19 11:17 | 122 | Remove | 2025-05-19 | 11:17 | US | GS | + | 0.5 | g | 0 | 112.1 | 11.466 | 1130.8 | 51476 | 1:01 | 28.9 | 2.16 m/s | 34.7 | 30.9 | 4.4 m/s | 24.6 |  | 2.16 | m/s |  | 4.4 | m/s | 1.0106 | 0.0094233 | 1.1305 |  | 0.5 | 0.5 | 0.0005 | 2260.9467 | 9.9206 | 7.8393 | 0.03152 | 4.1316 | 0.012102
2025-05-19 11:18 | 123 | Remove | 2025-05-19 | 11:18 | ST | GS | - | 2 | g | 0 | 112.1 | 11.475 | 1132.3 | 51485 | 1:01 | 28.9 | 2.42 m/s | 31.5 | 30.9 | 4.03 m/s | 21.8 |  | 2.42 | m/s |  | 4.03 | m/s | 1.0189 | 0.0094358 | 1.1399 |  | 1.5 | 2 | 0.002 | 569.9546 | 9.0057 | 6.947 | 0.032058 | 4.1636 | 0.048035
2025-05-19 11:18 | 124 | Remove | 2025-05-19 | 11:18 | ST | GS | - | 3 | g | 0 | 112.1 | 11.436 | 1127.9 | 51495 | 1:02 | 28.9 | 2.84 m/s | 30.7 | 30.9 | 3.86 m/s | 21.8 |  | 2.84 | m/s |  | 3.86 | m/s | 1.0272 | 0.0093992 | 1.1493 |  | 1 | 3 | 0.003 | 383.1028 | 8.777 | 6.947 | 0.036666 | 4.2003 | 0.071424
2025-05-19 11:19 | 125 | Remove | 2025-05-19 | 11:19 | US | GS | - | 13 | g | 0 | 112.2 | 11.42 | 1126.2 | 51504 | 1:02 | 28.9 | 2.37 m/s | 31.5 | 30.9 | 4.04 m/s | 22.1 |  | 2.37 | m/s |  | 4.04 | m/s | 1.0356 | 0.009385 | 1.1587 |  | 10 | 13 | 0.013 | 89.1303 | 9.0057 | 7.0426 | 0.031396 | 4.2317 | 0.30721
2025-05-19 11:19 | 126 | Remove | 2025-05-19 | 11:19 | ST | GS | - | 2.5 | g | 0 | 112.1 | 11.41 | 1123.7 | 51514 | 1:03 | 28.9 | 2.42 m/s | 31.2 | 30.9 | 3.98 m/s | 21.8 |  | 2.42 | m/s |  | 3.98 | m/s | 1.0439 | 0.0093642 | 1.1681 |  | -10.5 | 2.5 | 0.0025 | 467.223 | 8.9199 | 6.947 | 0.031753 | 4.2634 | 0.058638
2025-05-19 11:20 | 127 | Remove | 2025-05-19 | 11:20 | ST | GS | + | 1 | g | 0 | 112.2 | 11.456 | 1130.1 | 51523 | 1:03 | 28.9 | 2.47 m/s | 30.9 | 30.9 | 4.15 m/s | 21.6 |  | 2.47 | m/s |  | 4.15 | m/s | 1.0522 | 0.0094175 | 1.1775 |  | -1.5 | 1 | 0.001 | 1177.475 | 8.8342 | 6.8832 | 0.032097 | 4.2955 | 0.02328
2025-05-19 11:20 | 128 | Remove | 2025-05-19 | 11:20 | ST | GS | - | 1.5 | g | 0 | 112 | 11.495 | 1133.7 | 51533 | 1:04 | 28.9 | 2.16 m/s | 32.2 | 30.9 | 3.97 m/s | 22.5 |  | 2.16 | m/s |  | 3.97 | m/s | 1.0606 | 0.0094475 | 1.1869 |  | 0.5 | 1.5 | 0.0015 | 791.2817 | 9.2058 | 7.17 | 0.02925 | 4.3248 | 0.034684
2025-05-19 11:21 | 129 | Remove | 2025-05-19 | 11:21 | ST | GS | - | 1 | g | 0 | 112.1 | 11.521 | 1137.4 | 51542 | 1:04 | 28.9 | 2.33 m/s | 32.9 | 30.9 | 3.8 m/s | 23.3 |  | 2.33 | m/s |  | 3.8 | m/s | 1.0689 | 0.0094783 | 1.1964 |  | -0.5 | 1 | 0.001 | 1196.4008 | 9.406 | 7.425 | 0.032237 | 4.357 | 0.022951
2025-05-19 11:21 | 130 | Remove | 2025-05-19 | 11:21 | ST | GS | - | 4 | g | 0 | 112 | 11.5 | 1135.2 | 51551 | 1:05 | 28.9 | 2.09 m/s | 33.1 | 30.9 | 4.69 m/s | 23.3 |  | 2.09 | m/s |  | 4.69 | m/s | 1.0772 | 0.00946 | 1.2059 |  | 3 | 4 | 0.004 | 301.4652 | 9.4631 | 7.425 | 0.029093 | 4.3861 | 0.091197
2025-05-19 11:22 | 131 | Remove | 2025-05-19 | 11:22 | US | GS | - | 2 | g | 0 | 112.1 | 11.48 | 1133.3 | 51561 | 1:05 | 28.9 | 2.42 m/s | 32 | 30.9 | 3.9 m/s | 22.1 |  | 2.42 | m/s |  | 3.9 | m/s | 1.0856 | 0.0094442 | 1.2153 |  | -2 | 2 | 0.002 | 607.6525 | 9.1486 | 7.0426 | 0.032567 | 4.4187 | 0.045262
2025-05-19 11:22 | 132 | Remove | 2025-05-19 | 11:22 | ST | GS | - | 2.5 | g | 0 | 112.1 | 11.492 | 1134.4 | 51570 | 1:06 | 28.9 | 2.08 m/s | 32.2 | 31 | 3.96 m/s | 22.5 |  | 2.08 | m/s |  | 3.96 | m/s | 1.0939 | 0.0094533 | 1.2248 |  | 0.5 | 2.5 | 0.0025 | 489.9033 | 9.2058 | 7.2088 | 0.028166 | 4.4469 | 0.05622
2025-05-19 11:23 | 133 | Remove | 2025-05-19 | 11:23 | ST | GS | - | 3 | g | 0 | 112 | 11.526 | 1138.4 | 51580 | 1:06 | 28.9 | 2.25 m/s | 32.4 | 31 | 4.0 m/s | 22.5 |  | 2.25 | m/s |  | 4 | m/s | 1.1022 | 0.0094867 | 1.2342 |  | 0.5 | 3 | 0.003 | 411.415 | 9.263 | 7.2088 | 0.030658 | 4.4775 | 0.067002
2025-05-19 11:23 | 134 | Remove | 2025-05-19 | 11:23 | US | GS | - | 5 | g | 0 | 111.9 | 11.478 | 1131.9 | 51589 | 1:07 | 28.9 | 2.27 m/s | 31.2 | 31 | 3.96 m/s | 22.3 |  | 2.27 | m/s |  | 3.96 | m/s | 1.1106 | 0.0094325 | 1.2437 |  | 2 | 5 | 0.005 | 248.7355 | 8.9199 | 7.1447 | 0.029784 | 4.5073 | 0.11093
2025-05-19 11:24 | 135 | Remove | 2025-05-19 | 11:24 | US | GS | - | 8.5 | g | 0 | 112.2 | 11.469 | 1132.4 | 51599 | 1:07 | 28.9 | 2.47 m/s | 32.7 | 31 | 4.07 m/s | 23.2 |  | 2.47 | m/s |  | 4.07 | m/s | 1.1192 | 0.0094367 | 1.2531 |  | 3.5 | 8.5 | 0.0085 | 147.4252 | 9.3488 | 7.433 | 0.033967 | 4.5413 | 0.18717
2025-05-19 11:24 | 136 | Remove | 2025-05-19 | 11:24 | US | GS | - | 3.5 | g | 0 | 112 | 11.5 | 1135.6 | 51608 | 1:08 | 28.9 | 2.3 m/s | 31.5 | 31 | 3.84 m/s | 21.9 |  | 2.3 | m/s |  | 3.84 | m/s | 1.1275 | 0.0094633 | 1.2626 |  | -5 | 3.5 | 0.0035 | 360.7364 | 9.0057 | 7.0165 | 0.030468 | 4.5717 | 0.076557
2025-05-19 11:25 | 137 | Remove | 2025-05-19 | 11:25 | US | GS | - | 4 | g | 0 | 112.1 | 11.485 | 1133.7 | 51618 | 1:08 | 29 | 2.3 m/s | 31.9 | 31 | 4.21 m/s | 22.3 |  | 2.3 | m/s |  | 4.21 | m/s | 1.1358 | 0.0094475 | 1.272 |  | 0.5 | 4 | 0.004 | 318.0062 | 9.17 | 7.1447 | 0.031024 | 4.6028 | 0.086905
2025-05-19 11:25 | 138 | Remove | 2025-05-19 | 11:25 | ST | GS | - | 2 | g | 0 | 112 | 11.521 | 1138 | 51627 | 1:09 | 29 | 2.38 m/s | 31.7 | 31 | 3.92 m/s | 22 |  | 2.38 | m/s |  | 3.92 | m/s | 1.1442 | 0.0094833 | 1.2815 |  | -2 | 2 | 0.002 | 640.7542 | 9.1125 | 7.0486 | 0.031902 | 4.6347 | 0.043153
2025-05-19 11:26 | 139 | Remove | 2025-05-19 | 11:26 | US | GS | - | 4.5 | g | 0 | 112 | 11.473 | 1131.5 | 51637 | 1:09 | 28.9 | 2.41 m/s | 31.6 | 31 | 4.24 m/s | 22.1 |  | 2.41 | m/s |  | 4.24 | m/s | 1.1525 | 0.0094292 | 1.2909 |  | 2.5 | 4.5 | 0.0045 | 286.875 | 9.0343 | 7.0806 | 0.032027 | 4.6667 | 0.096428
2025-05-19 11:26 | 140 | Remove | 2025-05-19 | 11:26 | US | GS | - | 9 | g | 0 | 112.1 | 11.469 | 1131.8 | 51646 | 1:10 | 28.9 | 2.68 m/s | 31 | 31 | 4.0 m/s | 21.4 |  | 2.68 | m/s |  | 4 | m/s | 1.1608 | 0.0094317 | 1.3004 |  | 4.5 | 9 | 0.009 | 144.4855 | 8.8628 | 6.8563 | 0.034939 | 4.7016 | 0.19142
2025-05-19 11:27 | 141 | Remove | 2025-05-19 | 11:27 | US | GS | - | 2.5 | g | 0 | 112 | 11.463 | 1130.8 | 51656 | 1:10 | 28.9 | 2.16 m/s | 31.6 | 31 | 3.84 m/s | 21.9 |  | 2.16 | m/s |  | 3.84 | m/s | 1.1692 | 0.0094233 | 1.3098 |  | -6.5 | 2.5 | 0.0025 | 523.917 | 9.0343 | 7.0165 | 0.028705 | 4.7303 | 0.052851
2025-05-19 11:27 | 142 | Remove | 2025-05-19 | 11:27 | US | GS | - | 1.5 | g | 0 | 112.2 | 11.458 | 1129.2 | 51665 | 1:11 | 28.9 | 2.67 m/s | 30.8 | 31 | 4.24 m/s | 21.2 |  | 2.67 | m/s |  | 4.24 | m/s | 1.1775 | 0.00941 | 1.3192 |  | -1 | 1.5 | 0.0015 | 879.4683 | 8.8056 | 6.7922 | 0.034584 | 4.7649 | 0.03148
2025-05-19 11:28 | 143 | Remove | 2025-05-19 | 11:28 | ST | GS | - | 2 | g | 0 | 112.1 | 11.516 | 1137 | 51675 | 1:11 | 28.9 | 1.94 m/s | 31.5 | 31 | 4.33 m/s | 22.5 |  | 1.94 | m/s |  | 4.33 | m/s | 1.1858 | 0.009475 | 1.3287 |  | 0.5 | 2 | 0.002 | 664.3387 | 9.0057 | 7.2088 | 0.025699 | 4.7906 | 0.041748
2025-05-19 11:28 | 144 | Remove | 2025-05-19 | 11:28 | ST | GS | - | 1 | g | 0 | 112.1 | 11.507 | 1136.5 | 51684 | 1:12 | 28.9 | 1.94 m/s | 33 | 31 | 3.94 m/s | 22.6 |  | 1.94 | m/s |  | 3.94 | m/s | 1.1942 | 0.0094708 | 1.3381 |  | -1 | 1 | 0.001 | 1338.1483 | 9.4345 | 7.2408 | 0.026923 | 4.8175 | 0.020758
2025-05-19 11:29 | 145 | Remove | 2025-05-19 | 11:29 | US | GS | - | 2.5 | g | 0 | 112.2 | 11.469 | 1131.4 | 51694 | 1:12 | 28.9 | 2.04 m/s | 33.6 | 31 | 4.24 m/s | 23.1 |  | 2.04 | m/s |  | 4.24 | m/s | 1.2025 | 0.0094283 | 1.3476 |  | 1.5 | 2.5 | 0.0025 | 539.0307 | 9.6061 | 7.401 | 0.028826 | 4.8464 | 0.051585
2025-05-19 11:29 | 146 | Remove | 2025-05-19 | 11:29 | US | GS | - | 8 | g | 0 | 112.2 | 11.46 | 1130.4 | 51703 | 1:13 | 28.9 | 2.34 m/s | 32.2 | 31 | 3.97 m/s | 21.9 |  | 2.34 | m/s |  | 3.97 | m/s | 1.2108 | 0.00942 | 1.357 |  | 5.5 | 8 | 0.008 | 169.6246 | 9.2058 | 7.0165 | 0.031687 | 4.878 | 0.164
2025-05-19 11:30 | 147 | Remove | 2025-05-19 | 11:30 | US | GS | - | 3 | g | 0 | 112.3 | 11.49 | 1134.2 | 51713 | 1:13 | 28.9 | 2.35 m/s | 32.2 | 31 | 3.93 m/s | 22.5 |  | 2.35 | m/s |  | 3.93 | m/s | 1.2192 | 0.0094517 | 1.3664 |  | -5 | 3 | 0.003 | 455.4828 | 9.2058 | 7.2088 | 0.031822 | 4.9099 | 0.061101
2025-05-19 11:30 | 148 | Remove | 2025-05-19 | 11:30 | ST | GS | - | 4 | g | 0 | 112.3 | 11.519 | 1138.9 | 51722 | 1:14 | 28.9 | 2.38 m/s | 31.5 | 31 | 3.98 m/s | 22.6 |  | 2.38 | m/s |  | 3.98 | m/s | 1.2275 | 0.0094908 | 1.3759 |  | 1 | 4 | 0.004 | 343.9848 | 9.0057 | 7.2408 | 0.031528 | 4.9414 | 0.080949
2025-05-19 11:31 | 149 | Remove | 2025-05-19 | 11:31 | ST | GS | - | 4.5 | g | 0 | 112.4 | 11.495 | 1135.6 | 51732 | 1:14 | 29 | 2.68 m/s | 32.4 | 31 | 3.92 m/s | 22.2 |  | 2.68 | m/s |  | 3.92 | m/s | 1.2358 | 0.0094633 | 1.3854 |  | 0.5 | 4.5 | 0.0045 | 307.8672 | 9.3138 | 7.1126 | 0.036717 | 4.9781 | 0.090396
2025-05-19 11:31 | 150 | Remove | 2025-05-19 | 11:31 | US | GS | - | 4 | g | 0 | 112.3 | 11.515 | 1137.3 | 51741 | 1:15 | 29 | 2.04 m/s | 37 | 31 | 4.58 m/s | 25.3 |  | 2.04 | m/s |  | 4.58 | m/s | 1.2442 | 0.0094775 | 1.3949 |  | -0.5 | 4 | 0.004 | 348.72 | 10.6361 | 8.1058 | 0.031916 | 5.01 | 0.07984
2025-05-19 11:32 | 151 | Keep | 2025-05-19 | 11:32 | ST | GS | - | 5.5 | g | 0 | 112.4 | 11.427 | 1126.6 | 51750 | 1:15 | 29 | 2.91 m/s | 34 | 31 | 3.89 m/s | 23.5 |  | 2.91 | m/s |  | 3.89 | m/s | 1.2525 | 0.0093883 | 1.4043 |  | 1.5 | 5.5 | 0.0055 | 255.3215 | 9.7737 | 7.5291 | 0.041836 | 5.0519 | 0.10887
2025-05-19 11:32 | 152 | Remove | 2025-05-19 | 11:32 | ST | GS | - | 6 | g | 0 | 112.4 | 11.414 | 1124.7 | 51760 | 1:16 | 28.9 | 2.55 m/s | 32.2 | 30.9 | 3.86 m/s | 21.8 |  | 2.55 | m/s |  | 3.86 | m/s | 1.2611 | 0.0093725 | 1.4136 |  | 0.5 | 6 | 0.006 | 235.6068 | 9.2058 | 6.947 | 0.034531 | 5.0864 | 0.11796
2025-05-19 11:33 | 153 | Remove | 2025-05-19 | 11:33 | ST | GS | - | 3 | g | 0 | 112.3 | 11.478 | 1132.5 | 51769 | 1:16 | 28.9 | 2.23 m/s | 31.8 | 30.9 | 4.07 m/s | 22.1 |  | 2.23 | m/s |  | 4.07 | m/s | 1.2694 | 0.0094375 | 1.4231 |  | -3 | 3 | 0.003 | 474.3594 | 9.0915 | 7.0426 | 0.029822 | 5.1162 | 0.058637
2025-05-19 11:33 | 154 | Remove | 2025-05-19 | 11:33 | ST | GS | - | 1.5 | g | 0 | 112.3 | 11.432 | 1127.1 | 51779 | 1:17 | 28.9 | 2.51 m/s | 30.9 | 30.9 | 3.85 m/s | 21.7 |  | 2.51 | m/s |  | 3.85 | m/s | 1.2778 | 0.0093925 | 1.4325 |  | -1.5 | 1.5 | 0.0015 | 954.9806 | 8.8342 | 6.9151 | 0.032617 | 5.1488 | 0.029133
2025-05-19 11:34 | 155 | Remove | 2025-05-19 | 11:34 | ST | GS | - | 2.5 | g | 0 | 112.3 | 11.453 | 1129.3 | 51788 | 1:17 | 28.9 | 2.13 m/s | 30.2 | 30.9 | 4.16 m/s | 21.8 |  | 2.13 | m/s |  | 4.16 | m/s | 1.2861 | 0.0094108 | 1.4419 |  | 1 | 2.5 | 0.0025 | 576.7527 | 8.634 | 6.947 | 0.027052 | 5.1759 | 0.048301
2025-05-19 11:34 | 156 | Remove | 2025-05-19 | 11:34 | ST | GS | - | 3.5 | g | 0 | 112.3 | 11.47 | 1132.5 | 51798 | 1:18 | 28.9 | 2.13 m/s | 34.6 | 30.9 | 4.07 m/s | 23.9 |  | 2.13 | m/s |  | 4.07 | m/s | 1.2944 | 0.0094375 | 1.4513 |  | 1 | 3.5 | 0.0035 | 414.6626 | 9.892 | 7.6162 | 0.030993 | 5.2069 | 0.067219
2025-05-19 11:35 | 157 | Remove | 2025-05-19 | 11:35 | ST | GS | - | 3 | g | 0 | 112.4 | 11.49 | 1133.6 | 51807 | 1:18 | 28.9 | 2.23 m/s | 36.4 | 30.9 | 4.03 m/s | 24.2 |  | 2.23 | m/s |  | 4.03 | m/s | 1.3028 | 0.0094467 | 1.4608 |  | -0.5 | 3 | 0.003 | 486.9219 | 10.4066 | 7.7118 | 0.034136 | 5.241 | 0.057241
2025-05-19 11:35 | 158 | Remove | 2025-05-19 | 11:35 | US | GS | - | 4.5 | g | 0 | 112.2 | 11.625 | 1150 | 51817 | 1:19 | 28.9 | 2.19 m/s | 35.4 | 30.9 | 3.94 m/s | 24.1 |  | 2.19 | m/s |  | 3.94 | m/s | 1.3111 | 0.0095833 | 1.4703 |  | 1.5 | 4.5 | 0.0045 | 326.7443 | 10.1207 | 7.6799 | 0.032603 | 5.2736 | 0.08533
2025-05-19 11:36 | 159 | Remove | 2025-05-19 | 11:36 | US | GS | - | 4 | g | 0 | 112.1 | 11.455 | 1129.8 | 51826 | 1:19 | 28.9 | 2.34 m/s | 38 | 30.9 | 4.03 m/s | 26 |  | 2.34 | m/s |  | 4.03 | m/s | 1.3194 | 0.009415 | 1.4798 |  | -0.5 | 4 | 0.004 | 369.941 | 10.864 | 8.2854 | 0.037395 | 5.311 | 0.075315
2025-05-19 11:36 | 160 | Remove | 2025-05-19 | 11:36 | US | GS | - | 4.5 | g | 0 | 112.3 | 11.432 | 1127.1 | 51836 | 1:20 | 28.9 | 3.06 m/s | 32.9 | 30.9 | 3.97 m/s | 22 |  | 3.06 | m/s |  | 3.97 | m/s | 1.3278 | 0.0093925 | 1.4892 |  | 0.5 | 4.5 | 0.0045 | 330.9237 | 9.406 | 7.0107 | 0.042338 | 5.3533 | 0.08406
2025-05-19 11:37 | 161 | Remove | 2025-05-19 | 11:37 | ST | GS | - | 6 | g | 0 | 112.3 | 11.424 | 1126.5 | 51845 | 1:20 | 28.9 | 2.57 m/s | 38.2 | 30.9 | 4.13 m/s | 26.3 |  | 2.57 | m/s |  | 4.13 | m/s | 1.3361 | 0.0093875 | 1.4985 |  | 1.5 | 6 | 0.006 | 249.7574 | 10.9212 | 8.381 | 0.041286 | 5.3946 | 0.11122
2025-05-19 11:37 | 162 | Remove | 2025-05-19 | 11:37 | US | GS | - | 7 | g | 0 | 112.3 | 11.464 | 1131.1 | 51854 | 1:21 | 28.9 | 2.4 m/s | 33 | 30.8 | 3.88 m/s | 23.8 |  | 2.4 | m/s |  | 3.88 | m/s | 1.3444 | 0.0094258 | 1.508 |  | 1 | 7 | 0.007 | 215.4243 | 9.4345 | 7.5436 | 0.033307 | 5.4279 | 0.12896
2025-05-19 11:38 | 163 | Remove | 2025-05-19 | 11:38 | US | GS | - | 5 | g | 0 | 112.3 | 11.444 | 1128.8 | 51864 | 1:21 | 28.9 | 2.86 m/s | 31.7 | 30.8 | 3.86 m/s | 22.6 |  | 2.86 | m/s |  | 3.86 | m/s | 1.3528 | 0.0094067 | 1.5174 |  | -2 | 5 | 0.005 | 303.4753 | 9.0629 | 7.1632 | 0.038127 | 5.4661 | 0.091473
2025-05-19 11:38 | 164 | Remove | 2025-05-19 | 11:38 | ST | GS | - | 4.5 | g | 0 | 112.3 | 11.424 | 1126.2 | 51873 | 1:22 | 28.9 | 2.44 m/s | 30.4 | 30.7 | 3.76 m/s | 21.6 |  | 2.44 | m/s |  | 3.76 | m/s | 1.3611 | 0.009385 | 1.5268 |  | -0.5 | 4.5 | 0.0045 | 339.2804 | 8.6912 | 6.8094 | 0.031194 | 5.4973 | 0.081859
2025-05-19 11:39 | 165 | Remove | 2025-05-19 | 11:39 | US | GS | - | 11 | g | 0 | 112.3 | 11.479 | 1133.4 | 51883 | 1:22 | 28.9 | 2.22 m/s | 31.3 | 30.7 | 3.85 m/s | 22.5 |  | 2.22 | m/s |  | 3.85 | m/s | 1.3694 | 0.009445 | 1.5362 |  | 6.5 | 11 | 0.011 | 139.6552 | 8.9485 | 7.0932 | 0.029222 | 5.5265 | 0.19904
2025-05-19 11:39 | 166 | Remove | 2025-05-19 | 11:39 | ST | GS | - | 5.5 | g | 0 | 112.3 | 11.421 | 1126 | 51892 | 1:23 | 28.9 | 2.84 m/s | 32.8 | 30.7 | 3.72 m/s | 22.6 |  | 2.84 | m/s |  | 3.72 | m/s | 1.3778 | 0.0093833 | 1.5456 |  | -5.5 | 5.5 | 0.0055 | 281.0164 | 9.3774 | 7.1247 | 0.039174 | 5.5657 | 0.09882
2025-05-19 11:40 | 167 | Remove | 2025-05-19 | 11:40 | ST | GS | - | 8.5 | g | 0 | 112.3 | 11.456 | 1130.4 | 51902 | 1:23 | 28.9 | 2.7 m/s | 32.8 | 30.7 | 4.0 m/s | 23.1 |  | 2.7 | m/s |  | 4 | m/s | 1.3861 | 0.00942 | 1.555 |  | 3 | 8.5 | 0.0085 | 182.9424 | 9.3774 | 7.2823 | 0.037243 | 5.6029 | 0.15171
2025-05-19 11:40 | 168 | Remove | 2025-05-19 | 11:40 | US | GS | - | 1.5 | g | 0 | 112.3 | 11.451 | 1129.4 | 51911 | 1:24 | 28.9 | 2.67 m/s | 31.8 | 30.7 | 3.73 m/s | 22.5 |  | 2.67 | m/s |  | 3.73 | m/s | 1.3944 | 0.0094117 | 1.5644 |  | -7 | 1.5 | 0.0015 | 1042.9478 | 9.0915 | 7.0932 | 0.035707 | 5.6386 | 0.026602
2025-05-19 11:41 | 169 | Remove | 2025-05-19 | 11:41 | US | GS | - | 5.5 | g | 0 | 112.2 | 11.455 | 1129 | 51921 | 1:24 | 28.9 | 2.74 m/s | 36.7 | 30.8 | 3.75 m/s | 24.8 |  | 2.74 | m/s |  | 3.75 | m/s | 1.4028 | 0.0094083 | 1.5738 |  | 4 | 5.5 | 0.0055 | 286.1509 | 10.4924 | 7.8605 | 0.042289 | 5.6809 | 0.096816
2025-05-19 11:41 | 170 | Remove | 2025-05-19 | 11:41 | ST | GS | - | 2.5 | g | 0 | 112.2 | 11.486 | 1133 | 51930 | 1:25 | 28.9 | 2.5 m/s | 32.7 | 30.8 | 3.9 m/s | 22.8 |  | 2.5 | m/s |  | 3.9 | m/s | 1.4114 | 0.0094417 | 1.5833 |  | -3 | 2.5 | 0.0025 | 633.3087 | 9.3488 | 7.2266 | 0.034379 | 5.7153 | 0.043742
2025-05-19 11:42 | 171 | Remove | 2025-05-19 | 11:42 | US | GS | - | 7.5 | g | 0 | 112.2 | 11.498 | 1135.1 | 51940 | 1:25 | 28.9 | 3.02 m/s | 32.1 | 30.8 | 4.16 m/s | 22.5 |  | 3.02 | m/s |  | 4.16 | m/s | 1.4197 | 0.0094592 | 1.5927 |  | 5 | 7.5 | 0.0075 | 212.3641 | 9.1772 | 7.1315 | 0.040768 | 5.756 | 0.1303
2025-05-19 11:42 | 172 | Remove | 2025-05-19 | 11:42 | ST | GS | - | 7 | g | 0 | 112.2 | 11.522 | 1137.9 | 51949 | 1:26 | 28.9 | 2.41 m/s | 31.1 | 30.8 | 4.06 m/s | 22 |  | 2.41 | m/s |  | 4.06 | m/s | 1.4281 | 0.0094825 | 1.6022 |  | -0.5 | 7 | 0.007 | 228.8876 | 8.8913 | 6.973 | 0.03152 | 5.7876 | 0.12095
2025-05-19 11:43 | 173 | Remove | 2025-05-19 | 11:43 | ST | GS | - | 4.5 | g | 0 | 112.2 | 11.562 | 1142.4 | 51959 | 1:26 | 29 | 2.31 m/s | 33 | 30.8 | 3.86 m/s | 23.1 |  | 2.31 | m/s |  | 3.86 | m/s | 1.4364 | 0.00952 | 1.6117 |  | -2.5 | 4.5 | 0.0045 | 358.163 | 9.4863 | 7.3217 | 0.032234 | 5.8198 | 0.077322
2025-05-19 11:43 | 174 | Remove | 2025-05-19 | 11:43 | US | GS | - | 13.5 | g | 0 | 112.2 | 11.556 | 1142 | 51968 | 1:27 | 29 | 2.23 m/s | 35.2 | 30.9 | 4.13 m/s | 24.2 |  | 2.23 | m/s |  | 4.13 | m/s | 1.4447 | 0.0095167 | 1.6212 |  | 9 | 13.5 | 0.0135 | 120.0926 | 10.1187 | 7.7118 | 0.033192 | 5.853 | 0.23065
2025-05-19 11:44 | 175 | Remove | 2025-05-19 | 11:44 | US | GS | - | 12.5 | g | 0 | 112.2 | 11.541 | 1140.7 | 51978 | 1:27 | 29 | 2.3 m/s | 31.5 | 30.9 | 4.01 m/s | 21.6 |  | 2.3 | m/s |  | 4.01 | m/s | 1.4531 | 0.0095058 | 1.6308 |  | -1 | 12.5 | 0.0125 | 130.4605 | 9.0551 | 6.8832 | 0.030635 | 5.8836 | 0.21245
2025-05-19 11:44 | 176 | Remove | 2025-05-19 | 11:44 | ST | GS | - | 9.5 | g | 0 | 112.2 | 11.494 | 1134.2 | 51987 | 1:28 | 29 | 2.23 m/s | 30.2 | 30.9 | 4.0 m/s | 21 |  | 2.23 | m/s |  | 4 | m/s | 1.4614 | 0.0094517 | 1.6402 |  | -3 | 9.5 | 0.0095 | 172.6534 | 8.6814 | 6.692 | 0.028477 | 5.9121 | 0.16069
2025-05-19 11:45 | 177 | Remove | 2025-05-19 | 11:45 | US | GS | - | 10.5 | g | 0 | 112.3 | 11.449 | 1128.7 | 51997 | 1:28 | 29 | 2.25 m/s | 30 | 31 | 3.72 m/s | 21.3 |  | 2.25 | m/s |  | 3.72 | m/s | 1.4697 | 0.0094058 | 1.6496 |  | 1 | 10.5 | 0.0105 | 157.106 | 8.6239 | 6.8243 | 0.028542 | 5.9406 | 0.17675
2025-05-19 11:45 | 178 | Remove | 2025-05-19 | 11:45 | ST | GS | - | 3 | g | 0 | 112.3 | 11.524 | 1138 | 52006 | 1:29 | 29 | 2.31 m/s | 30.7 | 31 | 4.03 m/s | 21.1 |  | 2.31 | m/s |  | 4.03 | m/s | 1.4783 | 0.0094833 | 1.6591 |  | -7.5 | 3 | 0.003 | 553.0322 | 8.8251 | 6.7602 | 0.029987 | 5.9706 | 0.050246
2025-05-19 11:46 | 179 | Remove | 2025-05-19 | 11:46 | ST | GS | + | 0.5 | g | 0 | 112.2 | 11.539 | 1139.6 | 52016 | 1:29 | 29 | 2.4 m/s | 32 | 31 | 4.23 m/s | 22.1 |  | 2.4 | m/s |  | 4.23 | m/s | 1.4867 | 0.0094967 | 1.6686 |  | -2.5 | 0.5 | 0.0005 | 3337.1867 | 9.1988 | 7.0806 | 0.032475 | 6.0031 | 0.008329
2025-05-19 11:46 | 180 | Remove | 2025-05-19 | 11:46 | ST | GS | - | 3 | g | 0 | 112.3 | 11.568 | 1144.1 | 52025 | 1:30 | 29 | 2.11 m/s | 29.9 | 31 | 4.16 m/s | 21.5 |  | 2.11 | m/s |  | 4.16 | m/s | 1.495 | 0.0095342 | 1.6781 |  | 2.5 | 3 | 0.003 | 559.3758 | 8.5951 | 6.8884 | 0.026677 | 6.0298 | 0.049753
2025-05-19 11:47 | 181 | Keep | 2025-05-19 | 11:47 | US | GS | - | 17.5 | g | 0 | 112.3 | 11.53 | 1139.1 | 52035 | 1:30 | 29 | 2.26 m/s | 31.8 | 31 | 4.09 m/s | 22.3 |  | 2.26 | m/s |  | 4.09 | m/s | 1.5033 | 0.0094925 | 1.6876 |  | 14.5 | 17.5 | 0.0175 | 96.4354 | 9.1413 | 7.1447 | 0.030389 | 6.0602 | 0.28877
2025-05-19 11:47 | 182 | Remove | 2025-05-19 | 11:47 | US | GS | - | 4 | g | 0 | 112.4 | 11.48 | 1133.8 | 52044 | 1:31 | 29 | 2.74 m/s | 30.2 | 31 | 3.89 m/s | 21.2 |  | 2.74 | m/s |  | 3.89 | m/s | 1.5117 | 0.0094483 | 1.6971 |  | -13.5 | 4 | 0.004 | 424.2671 | 8.6814 | 6.7922 | 0.03499 | 6.0952 | 0.065626
2025-05-19 11:48 | 183 | Remove | 2025-05-19 | 11:48 | US | GS | - | 8 | g | 0 | 112.3 | 11.499 | 1135.7 | 52054 | 1:31 | 29 | 2.1 m/s | 31.8 | 31.1 | 3.94 m/s | 22.6 |  | 2.1 | m/s |  | 3.94 | m/s | 1.52 | 0.0094642 | 1.7065 |  | 4 | 8 | 0.008 | 213.3166 | 9.1413 | 7.2798 | 0.028238 | 6.1234 | 0.13065
2025-05-19 11:48 | 184 | Remove | 2025-05-19 | 11:48 | US | GS | - | 11.5 | g | 0 | 112.3 | 11.545 | 1141.4 | 52063 | 1:32 | 29 | 2.04 m/s | 31.5 | 31 | 4.21 m/s | 21.7 |  | 2.04 | m/s |  | 4.21 | m/s | 1.5283 | 0.0095117 | 1.716 |  | 3.5 | 11.5 | 0.0115 | 149.2212 | 9.0551 | 6.9524 | 0.027172 | 6.1506 | 0.18697
2025-05-19 11:49 | 185 | Remove | 2025-05-19 | 11:49 | ST | GS | - | 8 | g | 0 | 112.4 | 11.478 | 1133.6 | 52073 | 1:32 | 29 | 2.54 m/s | 29.1 | 31 | 3.79 m/s | 20.1 |  | 2.54 | m/s |  | 3.79 | m/s | 1.5367 | 0.0094467 | 1.7255 |  | -3.5 | 8 | 0.008 | 215.6864 | 8.3651 | 6.4398 | 0.031254 | 6.1818 | 0.12941
2025-05-19 11:49 | 186 | Remove | 2025-05-19 | 11:49 | US | GS | - | 3.5 | g | 0 | 112.3 | 11.526 | 1139 | 52082 | 1:33 | 29 | 2.25 m/s | 30.3 | 31 | 4.12 m/s | 21.9 |  | 2.25 | m/s |  | 4.12 | m/s | 1.545 | 0.0094917 | 1.735 |  | -4.5 | 3.5 | 0.0035 | 495.7093 | 8.7101 | 7.0165 | 0.028828 | 6.2107 | 0.056355
2025-05-19 11:50 | 187 | Remove | 2025-05-19 | 11:50 | US | GS | - | 4 | g | 0 | 112.3 | 11.555 | 1142.5 | 52092 | 1:33 | 29 | 2.0 m/s | 31.5 | 31 | 4.12 m/s | 22.1 |  | 2 | m/s |  | 4.12 | m/s | 1.5536 | 0.0095208 | 1.7445 |  | 0.5 | 4 | 0.004 | 436.1258 | 9.0551 | 7.0806 | 0.026639 | 6.2373 | 0.06413
2025-05-19 11:50 | 188 | Remove | 2025-05-19 | 11:50 | ST | GS | - | 7 | g | 0 | 112.2 | 11.574 | 1144.6 | 52101 | 1:34 | 29 | 2.26 m/s | 32 | 31 | 4.12 m/s | 23.4 |  | 2.26 | m/s |  | 4.12 | m/s | 1.5619 | 0.0095383 | 1.754 |  | 3 | 7 | 0.007 | 250.5774 | 9.1988 | 7.4971 | 0.03058 | 6.2679 | 0.11168
2025-05-19 11:51 | 189 | Remove | 2025-05-19 | 11:51 | ST | GS | - | 4.5 | g | 0 | 112.2 | 11.581 | 1144.6 | 52111 | 1:34 | 29 | 2.01 m/s | 35.6 | 31.1 | 4.81 m/s | 25.4 |  | 2.01 | m/s |  | 4.81 | m/s | 1.5703 | 0.0095383 | 1.7636 |  | -2.5 | 4.5 | 0.0045 | 391.9067 | 10.2337 | 8.1818 | 0.030257 | 6.2981 | 0.07145
2025-05-19 11:51 | 190 | Remove | 2025-05-19 | 11:51 | ST | GS | - | 5.5 | g | 0 | 112.4 | 11.535 | 1139.7 | 52120 | 1:35 | 29 | 2.8 m/s | 34 | 31.1 | 4.16 m/s | 22.5 |  | 2.8 | m/s |  | 4.16 | m/s | 1.5786 | 0.0094975 | 1.7731 |  | 1 | 5.5 | 0.0055 | 322.3777 | 9.7737 | 7.2476 | 0.040255 | 6.3384 | 0.086773
2025-05-19 11:52 | 191 | Remove | 2025-05-19 | 11:52 | US | GS | - | 4.5 | g | 0 | 112.2 | 11.507 | 1135.6 | 52130 | 1:35 | 29 | 2.2 m/s | 32.9 | 31.1 | 3.88 m/s | 22.5 |  | 2.2 | m/s |  | 3.88 | m/s | 1.5869 | 0.0094633 | 1.7825 |  | -1 | 4.5 | 0.0045 | 396.1202 | 9.4575 | 7.2476 | 0.030606 | 6.369 | 0.070655
2025-05-19 11:52 | 192 | Remove | 2025-05-19 | 11:52 | ST | GS | - | 5.5 | g | 0 | 112.2 | 11.545 | 1141.2 | 52139 | 1:36 | 29 | 2.15 m/s | 34.1 | 31.1 | 4.47 m/s | 25.1 |  | 2.15 | m/s |  | 4.47 | m/s | 1.5953 | 0.00951 | 1.7921 |  | 1 | 5.5 | 0.0055 | 325.8274 | 9.8025 | 8.0851 | 0.031001 | 6.4 | 0.085938
2025-05-19 11:53 | 193 | Remove | 2025-05-19 | 11:53 | US | GS | - | 11 | g | 0 | 112.2 | 11.469 | 1131.9 | 52149 | 1:36 | 29 | 2.34 m/s | 32.9 | 31.1 | 3.6 m/s | 22.5 |  | 2.34 | m/s |  | 3.6 | m/s | 1.6036 | 0.0094325 | 1.8015 |  | 5.5 | 11 | 0.011 | 163.7712 | 9.4575 | 7.2476 | 0.032553 | 6.4325 | 0.17101
2025-05-19 11:53 | 194 | Remove | 2025-05-19 | 11:53 | US | GS | - | 5.5 | g | 0 | 112.2 | 11.529 | 1138.3 | 52158 | 1:37 | 29 | 2.65 m/s | 30.9 | 31 | 3.92 m/s | 20.7 |  | 2.65 | m/s |  | 3.92 | m/s | 1.6119 | 0.0094858 | 1.811 |  | -5.5 | 5.5 | 0.0055 | 329.2671 | 8.8826 | 6.6321 | 0.034625 | 6.4672 | 0.085045
2025-05-19 11:54 | 195 | Remove | 2025-05-19 | 11:54 | ST | GS | - | 6.5 | g | 0 | 112.2 | 11.515 | 1137.4 | 52168 | 1:37 | 29 | 2.54 m/s | 30.5 | 31 | 3.89 m/s | 21.9 |  | 2.54 | m/s |  | 3.89 | m/s | 1.6203 | 0.0094783 | 1.8204 |  | 1 | 6.5 | 0.0065 | 280.0688 | 8.7676 | 7.0165 | 0.032758 | 6.4999 | 0.1
2025-05-19 11:54 | 196 | Remove | 2025-05-19 | 11:54 | US | GS | - | 10 | g | 0 | 112.2 | 11.486 | 1132.9 | 52177 | 1:38 | 29 | 2.86 m/s | 30.2 | 31 | 3.94 m/s | 20.9 |  | 2.86 | m/s |  | 3.94 | m/s | 1.6286 | 0.0094408 | 1.8299 |  | 3.5 | 10 | 0.01 | 182.9888 | 8.6814 | 6.6961 | 0.036522 | 6.5365 | 0.15299
2025-05-19 11:55 | 197 | Remove | 2025-05-19 | 11:55 | US | GS | - | 11.5 | g | 0 | 112.3 | 11.479 | 1132.6 | 52187 | 1:38 | 29 | 2.35 m/s | 31.3 | 30.9 | 3.96 m/s | 21.6 |  | 2.35 | m/s |  | 3.96 | m/s | 1.6369 | 0.0094383 | 1.8393 |  | 1.5 | 11.5 | 0.0115 | 159.9414 | 8.9976 | 6.8832 | 0.031102 | 6.5676 | 0.1751
2025-05-19 11:55 | 198 | Remove | 2025-05-19 | 11:55 | ST | GS | - | 8.5 | g | 0 | 112.3 | 11.511 | 1137.2 | 52196 | 1:39 | 29 | 2.35 m/s | 29.6 | 30.9 | 4.0 m/s | 21.3 |  | 2.35 | m/s |  | 4 | m/s | 1.6453 | 0.0094767 | 1.8488 |  | -3 | 8.5 | 0.0085 | 217.5063 | 8.5089 | 6.7876 | 0.029413 | 6.597 | 0.12885
2025-05-19 11:56 | 199 | Remove | 2025-05-19 | 11:56 | ST | GS | - | 6.5 | g | 0 | 112.3 | 11.491 | 1134.3 | 52206 | 1:39 | 29 | 2.87 m/s | 28.8 | 30.9 | 3.81 m/s | 20 |  | 2.87 | m/s |  | 3.81 | m/s | 1.6536 | 0.0094525 | 1.8583 |  | -2 | 6.5 | 0.0065 | 285.8855 | 8.2789 | 6.3734 | 0.034951 | 6.6319 | 0.098011
2025-05-19 11:56 | 200 | Remove | 2025-05-19 | 11:56 | ST | GS | - | 4 | g | 0 | 112.3 | 11.505 | 1135.9 | 52215 | 1:40 | 29 | 2.5 m/s | 28.7 | 30.9 | 3.92 m/s | 20.1 |  | 2.5 | m/s |  | 3.92 | m/s | 1.6619 | 0.0094658 | 1.8677 |  | -2.5 | 4 | 0.004 | 466.9304 | 8.2502 | 6.4052 | 0.030339 | 6.6623 | 0.06004
2025-05-19 11:57 | 201 | Remove | 2025-05-19 | 11:57 | ST | GS | - | 3.5 | g | 0 | 112.2 | 11.538 | 1140 | 52225 | 1:40 | 29 | 2.12 m/s | 29.8 | 30.9 | 4.73 m/s | 21.3 |  | 2.12 | m/s |  | 4.73 | m/s | 1.6703 | 0.0095 | 1.8772 |  | -0.5 | 3.5 | 0.0035 | 536.349 | 8.5664 | 6.7876 | 0.026714 | 6.689 | 0.052325
2025-05-19 11:57 | 202 | Remove | 2025-05-19 | 11:57 | ST | GS | - | 5.5 | g | 0 | 112.2 | 11.522 | 1137.6 | 52234 | 1:41 | 29 | 2.45 m/s | 30.1 | 31 | 4.41 m/s | 20.7 |  | 2.45 | m/s |  | 4.41 | m/s | 1.6786 | 0.00948 | 1.8867 |  | 2 | 5.5 | 0.0055 | 343.0367 | 8.6526 | 6.6321 | 0.031183 | 6.7202 | 0.081843
2025-05-19 11:58 | 203 | Remove | 2025-05-19 | 11:58 | ST | GS | - | 5.5 | g | 0 | 112.2 | 11.574 | 1143.7 | 52244 | 1:41 | 29 | 2.12 m/s | 30.1 | 31 | 4.0 m/s | 20.9 |  | 2.12 | m/s |  | 4 | m/s | 1.6869 | 0.0095308 | 1.8962 |  | 0 | 5.5 | 0.0055 | 344.7695 | 8.6526 | 6.6961 | 0.026983 | 6.7471 | 0.081516
2025-05-19 11:58 | 204 | Remove | 2025-05-19 | 11:58 | ST | GS | - | 2.5 | g | 0 | 112.2 | 11.561 | 1143.1 | 52253 | 1:42 | 29 | 2.26 m/s | 31.4 | 31 | 4.13 m/s | 22.3 |  | 2.26 | m/s |  | 4.13 | m/s | 1.6953 | 0.0095258 | 1.9058 |  | -3 | 2.5 | 0.0025 | 762.3033 | 9.0263 | 7.1447 | 0.030007 | 6.7771 | 0.036889
2025-05-19 11:59 | 205 | Remove | 2025-05-19 | 11:59 | ST | GS | - | 9.5 | g | 0 | 112.1 | 11.548 | 1141.2 | 52263 | 1:42 | 29 | 2.06 m/s | 32.6 | 31.1 | 4.24 m/s | 23.2 |  | 2.06 | m/s |  | 4.24 | m/s | 1.7039 | 0.00951 | 1.9153 |  | 7 | 9.5 | 0.0095 | 201.6072 | 9.3713 | 7.4731 | 0.028397 | 6.8055 | 0.13959
2025-05-19 11:59 | 206 | Remove | 2025-05-19 | 11:59 | US | GS | - | 11.5 | g | 0 | 112.3 | 11.526 | 1139.3 | 52273 | 1:43 | 29 | 2.54 m/s | 31 | 31.1 | 3.92 m/s | 20.9 |  | 2.54 | m/s |  | 3.92 | m/s | 1.7122 | 0.0094942 | 1.9248 |  | 2 | 11.5 | 0.0115 | 167.3707 | 8.9113 | 6.7322 | 0.033295 | 6.8388 | 0.16816
2025-05-19 12:00 | 207 | Remove | 2025-05-19 | 12:00 | US | GS | - | 8 | g | 0 | 112.2 | 11.506 | 1136.1 | 52282 | 1:43 | 29 | 2.72 m/s | 29.6 | 31.1 | 3.93 m/s | 20.6 |  | 2.72 | m/s |  | 3.93 | m/s | 1.7206 | 0.0094675 | 1.9342 |  | -3.5 | 8 | 0.008 | 241.7787 | 8.5089 | 6.6356 | 0.034044 | 6.8729 | 0.1164
2025-05-19 12:00 | 208 | Remove | 2025-05-19 | 12:00 | US | GS | - | 2.5 | g | 0 | 112.2 | 11.528 | 1138.4 | 52292 | 1:44 | 29 | 2.81 m/s | 30.7 | 31 | 3.97 m/s | 21 |  | 2.81 | m/s |  | 3.97 | m/s | 1.7289 | 0.0094867 | 1.9437 |  | -5.5 | 2.5 | 0.0025 | 777.4867 | 8.8251 | 6.7282 | 0.036478 | 6.9094 | 0.036183
2025-05-19 12:01 | 209 | Remove | 2025-05-19 | 12:01 | ST | GS | - | 7 | g | 0 | 112.3 | 11.534 | 1139.9 | 52301 | 1:44 | 29 | 2.6 m/s | 30.1 | 31 | 4.18 m/s | 21.4 |  | 2.6 | m/s |  | 4.18 | m/s | 1.7372 | 0.0094992 | 1.9532 |  | 4.5 | 7 | 0.007 | 279.0308 | 8.6526 | 6.8563 | 0.033092 | 6.9424 | 0.10083
2025-05-19 12:01 | 210 | Remove | 2025-05-19 | 12:01 | ST | GS | - | 8.5 | g | 0 | 112.2 | 11.54 | 1140.1 | 52311 | 1:45 | 29 | 2.42 m/s | 30.3 | 31 | 3.94 m/s | 20.9 |  | 2.42 | m/s |  | 3.94 | m/s | 1.7456 | 0.0095008 | 1.9627 |  | 1.5 | 8.5 | 0.0085 | 230.9078 | 8.7101 | 6.6961 | 0.031006 | 6.9735 | 0.12189
2025-05-19 12:02 | 211 | Keep | 2025-05-19 | 12:02 | US | GS | - | 13 | g | 0 | 112.2 | 11.556 | 1141.6 | 52320 | 1:45 | 29 | 2.22 m/s | 30.5 | 31 | 3.89 m/s | 21.9 |  | 2.22 | m/s |  | 3.89 | m/s | 1.7539 | 0.0095133 | 1.9722 |  | 4.5 | 13 | 0.013 | 151.71 | 8.7676 | 7.0165 | 0.028631 | 7.0021 | 0.18566
2025-05-19 12:02 | 212 | Remove | 2025-05-19 | 12:02 | US | GS | - | 9 | g | 0 | 112.3 | 11.543 | 1140.8 | 52330 | 1:46 | 29 | 2.23 m/s | 30.7 | 31 | 3.84 m/s | 21.2 |  | 2.23 | m/s |  | 3.84 | m/s | 1.7622 | 0.0095067 | 1.9817 |  | -4 | 9 | 0.009 | 220.193 | 8.8251 | 6.7922 | 0.028949 | 7.031 | 0.128
2025-05-19 12:03 | 213 | Remove | 2025-05-19 | 12:03 | US | GS | - | 9 | g | 0 | 112.2 | 11.512 | 1136.7 | 52339 | 1:46 | 29 | 2.58 m/s | 29.6 | 30.9 | 3.93 m/s | 20.7 |  | 2.58 | m/s |  | 3.93 | m/s | 1.7706 | 0.0094725 | 1.9912 |  | 0 | 9 | 0.009 | 221.2455 | 8.5089 | 6.5964 | 0.032292 | 7.0633 | 0.12742
2025-05-19 12:03 | 214 | Remove | 2025-05-19 | 12:03 | US | GS | - | 10 | g | 0 | 112.3 | 11.53 | 1138.8 | 52349 | 1:47 | 29 | 2.96 m/s | 31.3 | 30.9 | 4.3 m/s | 21.2 |  | 2.96 | m/s |  | 4.3 | m/s | 1.7789 | 0.00949 | 2.0007 |  | 1 | 10 | 0.01 | 200.0699 | 8.9976 | 6.7558 | 0.039176 | 7.1025 | 0.1408
2025-05-19 12:04 | 215 | Remove | 2025-05-19 | 12:04 | ST | GS | - | 6 | g | 0 | 112.3 | 11.527 | 1138.3 | 52358 | 1:47 | 29 | 2.38 m/s | 30.3 | 30.9 | 3.76 m/s | 23.8 |  | 2.38 | m/s |  | 3.76 | m/s | 1.7872 | 0.0094858 | 2.0102 |  | -4 | 6 | 0.006 | 335.0308 | 8.7101 | 7.5843 | 0.030493 | 7.133 | 0.084116
2025-05-19 12:04 | 216 | Remove | 2025-05-19 | 12:04 | ST | GS | - | 8.5 | g | 0 | 112.3 | 11.545 | 1140.6 | 52368 | 1:48 | 29 | 3.11 m/s | 30 | 30.9 | 3.92 m/s | 21 |  | 3.11 | m/s |  | 3.92 | m/s | 1.7956 | 0.009505 | 2.0197 |  | 2.5 | 8.5 | 0.0085 | 237.6106 | 8.6239 | 6.692 | 0.039452 | 7.1724 | 0.11851
2025-05-19 12:05 | 217 | Remove | 2025-05-19 | 12:05 | ST | GS | - | 4.5 | g | 0 | 112.1 | 11.589 | 1146.5 | 52377 | 1:48 | 29 | 2.06 m/s | 29.7 | 30.9 | 4.26 m/s | 21.6 |  | 2.06 | m/s |  | 4.26 | m/s | 1.8039 | 0.0095542 | 2.0292 |  | -4 | 4.5 | 0.0045 | 450.9431 | 8.5376 | 6.8832 | 0.025871 | 7.1983 | 0.062515
2025-05-19 12:05 | 218 | Remove | 2025-05-19 | 12:05 | ST | GS | - | 5 | g | 0 | 112.2 | 11.624 | 1150.8 | 52387 | 1:49 | 29 | 2.18 m/s | 30 | 31 | 4.16 m/s | 21.2 |  | 2.18 | m/s |  | 4.16 | m/s | 1.8122 | 0.00959 | 2.0388 |  | 0.5 | 5 | 0.005 | 407.7668 | 8.6239 | 6.7922 | 0.027654 | 7.226 | 0.069195
2025-05-19 12:06 | 219 | Remove | 2025-05-19 | 12:06 | US | GS | - | 6 | g | 0 | 112.2 | 11.583 | 1145.1 | 52396 | 1:49 | 29.1 | 2.2 m/s | 30.7 | 31 | 4.09 m/s | 21.5 |  | 2.2 | m/s |  | 4.09 | m/s | 1.8206 | 0.0095425 | 2.0484 |  | 1 | 6 | 0.006 | 341.3961 | 8.8734 | 6.8884 | 0.028715 | 7.2547 | 0.082705
2025-05-19 12:06 | 220 | Remove | 2025-05-19 | 12:06 | ST | GS | - | 6 | g | 0 | 112.2 | 11.548 | 1140.3 | 52406 | 1:50 | 29.1 | 2.52 m/s | 29.3 | 31 | 4.0 m/s | 21.7 |  | 2.52 | m/s |  | 4 | m/s | 1.8289 | 0.0095025 | 2.0579 |  | 0 | 6 | 0.006 | 342.9799 | 8.4688 | 6.9524 | 0.031392 | 7.2861 | 0.082349
2025-05-19 12:07 | 221 | Remove | 2025-05-19 | 12:07 | ST | GS | - | 6 | g | 0 | 112.2 | 11.551 | 1141.2 | 52416 | 1:50 | 29.1 | 2.57 m/s | 29.8 | 31 | 3.89 m/s | 20.5 |  | 2.57 | m/s |  | 3.89 | m/s | 1.8372 | 0.00951 | 2.0674 |  | 0 | 6 | 0.006 | 344.5649 | 8.6133 | 6.568 | 0.032561 | 7.3186 | 0.081982
2025-05-19 12:07 | 222 | Remove | 2025-05-19 | 12:07 | ST | GS | - | 6.5 | g | 0 | 112.1 | 11.537 | 1139.8 | 52425 | 1:51 | 29.1 | 2.71 m/s | 30.4 | 31 | 4.04 m/s | 20.9 |  | 2.71 | m/s |  | 4.04 | m/s | 1.8458 | 0.0094983 | 2.0769 |  | 0.5 | 6.5 | 0.0065 | 319.5212 | 8.7867 | 6.6961 | 0.035027 | 7.3537 | 0.088391
2025-05-19 12:08 | 223 | Remove | 2025-05-19 | 12:08 | US | GS | - | 11.5 | g | 0 | 112.3 | 11.535 | 1139.5 | 52435 | 1:51 | 29.1 | 2.23 m/s | 30 | 31 | 3.96 m/s | 20.7 |  | 2.23 | m/s |  | 3.96 | m/s | 1.8542 | 0.0094958 | 2.0864 |  | 5 | 11.5 | 0.0115 | 181.4246 | 8.6711 | 6.6321 | 0.028443 | 7.3821 | 0.15578
2025-05-19 12:08 | 224 | Remove | 2025-05-19 | 12:08 | US | GS | - | 10 | g | 0 | 112.1 | 11.559 | 1142.5 | 52444 | 1:52 | 29 | 2.35 m/s | 32.6 | 31 | 3.92 m/s | 22.7 |  | 2.35 | m/s |  | 3.92 | m/s | 1.8625 | 0.0095208 | 2.0959 |  | -1.5 | 10 | 0.01 | 209.5904 | 9.3713 | 7.2728 | 0.032394 | 7.4145 | 0.13487
2025-05-19 12:09 | 225 | Remove | 2025-05-19 | 12:09 | US | GS | - | 5 | g | 0 | 112.3 | 11.512 | 1136.8 | 52454 | 1:52 | 29.1 | 3.12 m/s | 31.5 | 31 | 3.93 m/s | 21.4 |  | 3.12 | m/s |  | 3.93 | m/s | 1.8708 | 0.0094733 | 2.1054 |  | -5 | 5 | 0.005 | 421.0755 | 9.1046 | 6.8563 | 0.041785 | 7.4563 | 0.067057
2025-05-19 12:09 | 226 | Remove | 2025-05-19 | 12:09 | US | GS | - | 8.5 | g | 0 | 112.2 | 11.561 | 1141.6 | 52463 | 1:53 | 29 | 2.2 m/s | 30.4 | 30.9 | 3.86 m/s | 21.7 |  | 2.2 | m/s |  | 3.86 | m/s | 1.8792 | 0.0095133 | 2.1149 |  | 3.5 | 8.5 | 0.0085 | 248.8107 | 8.7388 | 6.9151 | 0.02828 | 7.4846 | 0.11357
2025-05-19 12:10 | 227 | Remove | 2025-05-19 | 12:10 | US | GS | - | 8.5 | g | 0 | 112.1 | 11.596 | 1146.2 | 52473 | 1:53 | 29.1 | 2.37 m/s | 29.8 | 30.9 | 4.0 m/s | 21.8 |  | 2.37 | m/s |  | 4 | m/s | 1.8875 | 0.0095517 | 2.1244 |  | 0 | 8.5 | 0.0085 | 249.9344 | 8.6133 | 6.947 | 0.030028 | 7.5146 | 0.11311
2025-05-19 12:10 | 228 | Remove | 2025-05-19 | 12:10 | ST | GS | - | 7 | g | 0 | 112.2 | 11.579 | 1144.5 | 52482 | 1:54 | 29.1 | 2.2 m/s | 33.2 | 31 | 4.52 m/s | 22.8 |  | 2.2 | m/s |  | 4.52 | m/s | 1.8958 | 0.0095375 | 2.134 |  | -1.5 | 7 | 0.007 | 304.8543 | 9.596 | 7.3049 | 0.031054 | 7.5457 | 0.092769
2025-05-19 12:11 | 229 | Remove | 2025-05-19 | 12:11 | ST | GS | - | 5 | g | 0 | 112.1 | 11.625 | 1149.4 | 52492 | 1:54 | 29.1 | 2.01 m/s | 31.1 | 31 | 4.32 m/s | 22.1 |  | 2.01 | m/s |  | 4.32 | m/s | 1.9042 | 0.0095783 | 2.1436 |  | -2 | 5 | 0.005 | 428.7117 | 8.989 | 7.0806 | 0.026577 | 7.5722 | 0.066031
2025-05-19 12:11 | 230 | Remove | 2025-05-19 | 12:11 | US | GS | - | 9 | g | 0 | 112.2 | 11.601 | 1146.9 | 52501 | 1:55 | 29.1 | 2.37 m/s | 31.4 | 31 | 4.26 m/s | 21.6 |  | 2.37 | m/s |  | 4.26 | m/s | 1.9125 | 0.0095575 | 2.1531 |  | 4 | 9 | 0.009 | 239.2351 | 9.0757 | 6.9204 | 0.03164 | 7.6039 | 0.11836
2025-05-19 12:12 | 231 | Remove | 2025-05-19 | 12:12 | ST | GS | - | 5 | g | 0 | 112.1 | 11.635 | 1151.2 | 52511 | 1:55 | 29.1 | 2.0 m/s | 29.5 | 31.1 | 4.9 m/s | 21.1 |  | 2 | m/s |  | 4.9 | m/s | 1.9208 | 0.0095933 | 2.1627 |  | -4 | 5 | 0.005 | 432.5418 | 8.5266 | 6.7967 | 0.025085 | 7.629 | 0.06554
2025-05-19 12:12 | 232 | Remove | 2025-05-19 | 12:12 | US | GS | - | 6.5 | g | 0 | 112.1 | 11.57 | 1143.3 | 52521 | 1:56 | 29.1 | 2.48 m/s | 29.7 | 31.1 | 4.24 m/s | 20.4 |  | 2.48 | m/s |  | 4.24 | m/s | 1.9292 | 0.0095275 | 2.1722 |  | 1.5 | 6.5 | 0.0065 | 334.1903 | 8.5844 | 6.5712 | 0.031316 | 7.6603 | 0.084853
2025-05-19 12:13 | 233 | Remove | 2025-05-19 | 12:13 | ST | GS | - | 8 | g | 0 | 112.2 | 11.646 | 1152.7 | 52530 | 1:56 | 29.1 | 2.61 m/s | 29.4 | 31.1 | 3.74 m/s | 22.2 |  | 2.61 | m/s |  | 3.74 | m/s | 1.9375 | 0.0096058 | 2.1818 |  | 1.5 | 8 | 0.008 | 272.7303 | 8.4977 | 7.151 | 0.032624 | 7.6929 | 0.10399
2025-05-19 12:13 | 234 | Remove | 2025-05-19 | 12:13 | ST | GS | - | 6.5 | g | 0 | 112 | 11.631 | 1150.3 | 52540 | 1:57 | 29.1 | 2.3 m/s | 31.7 | 31.1 | 4.41 m/s | 22 |  | 2.3 | m/s |  | 4.41 | m/s | 1.9458 | 0.0095858 | 2.1914 |  | -1.5 | 6.5 | 0.0065 | 337.1428 | 9.1625 | 7.0866 | 0.030999 | 7.7239 | 0.084154
2025-05-19 12:14 | 235 | Remove | 2025-05-19 | 12:14 | ST | GS | - | 7.5 | g | 0 | 112.1 | 11.62 | 1149.7 | 52549 | 1:57 | 29.2 | 2.12 m/s | 31.8 | 31.1 | 3.92 m/s | 23.2 |  | 2.12 | m/s |  | 3.92 | m/s | 1.9542 | 0.0095808 | 2.201 |  | 1 | 7.5 | 0.0075 | 293.4679 | 9.2417 | 7.4731 | 0.02882 | 7.7527 | 0.09674
2025-05-19 12:14 | 236 | Remove | 2025-05-19 | 12:14 | US | GS | - | 8.5 | g | 0 | 112.2 | 11.564 | 1142.5 | 52559 | 1:58 | 29.2 | 2.22 m/s | 32.2 | 31.1 | 3.86 m/s | 22.9 |  | 2.22 | m/s |  | 3.86 | m/s | 1.9625 | 0.0095208 | 2.2105 |  | 1 | 8.5 | 0.0085 | 260.0624 | 9.3579 | 7.3765 | 0.030559 | 7.7833 | 0.10921
2025-05-19 12:15 | 237 | Remove | 2025-05-19 | 12:15 | US | GS | - | 6.5 | g | 0 | 112.1 | 11.567 | 1143.1 | 52569 | 1:58 | 29.2 | 3.2 m/s | 32.6 | 31.1 | 3.92 m/s | 22.9 |  | 3.2 | m/s |  | 3.92 | m/s | 1.9708 | 0.0095258 | 2.2201 |  | -2 | 6.5 | 0.0065 | 341.5471 | 9.4741 | 7.3765 | 0.044596 | 7.8279 | 0.083037
2025-05-19 12:15 | 238 | Remove | 2025-05-19 | 12:15 | US | GS | - | 4 | g | 0 | 112.1 | 11.528 | 1138.6 | 52578 | 1:59 | 29.1 | 3.71 m/s | 29.1 | 31 | 3.98 m/s | 22.7 |  | 3.71 | m/s |  | 3.98 | m/s | 1.9792 | 0.0094883 | 2.2295 |  | -2.5 | 4 | 0.004 | 557.386 | 8.411 | 7.2728 | 0.045901 | 7.8738 | 0.050802
2025-05-19 12:16 | 239 | Remove | 2025-05-19 | 12:16 | ST | GS | - | 7 | g | 0 | 112.2 | 11.556 | 1142.1 | 52588 | 1:59 | 29.1 | 2.47 m/s | 31 | 30.9 | 4.09 m/s | 21.4 |  | 2.47 | m/s |  | 4.09 | m/s | 1.9875 | 0.0095175 | 2.2391 |  | 3 | 7 | 0.007 | 319.866 | 8.9601 | 6.8195 | 0.032555 | 7.9063 | 0.088537
2025-05-19 12:16 | 240 | Remove | 2025-05-19 | 12:16 | ST | GS | - | 7.5 | g | 0 | 112.2 | 11.551 | 1141.7 | 52597 | 2:00 | 29.1 | 2.5 m/s | 29.6 | 30.9 | 3.81 m/s | 20.5 |  | 2.5 | m/s |  | 3.81 | m/s | 1.9961 | 0.0095142 | 2.2486 |  | 0.5 | 7.5 | 0.0075 | 299.8101 | 8.5555 | 6.5327 | 0.031462 | 7.9378 | 0.094485
2025-05-19 12:17 | 241 | Keep | 2025-05-19 | 12:17 | US | GS | - | 10 | g | 0 | 112.2 | 11.554 | 1142.3 | 52607 | 2:00 | 29.1 | 2.83 m/s | 30.1 | 30.9 | 4.2 m/s | 20.6 |  | 2.83 | m/s |  | 4.2 | m/s | 2.0044 | 0.0095192 | 2.2581 |  | 2.5 | 10 | 0.01 | 225.8095 | 8.7 | 6.5646 | 0.036217 | 7.974 | 0.12541
2025-05-19 12:17 | 242 | Remove | 2025-05-19 | 12:17 | US | GS | - | 4 | g | 0 | 112.2 | 11.56 | 1142.5 | 52616 | 2:01 | 29.1 | 2.38 m/s | 31.8 | 30.9 | 3.93 m/s | 22.1 |  | 2.38 | m/s |  | 3.93 | m/s | 2.0128 | 0.0095208 | 2.2676 |  | -6 | 4 | 0.004 | 566.904 | 9.1914 | 7.0426 | 0.032178 | 8.0062 | 0.049961
2025-05-19 12:18 | 243 | Remove | 2025-05-19 | 12:18 | ST | GS | - | 7 | g | 0 | 112.1 | 11.576 | 1145.2 | 52626 | 2:01 | 29.1 | 2.23 m/s | 31.5 | 31 | 4.35 m/s | 22.9 |  | 2.23 | m/s |  | 4.35 | m/s | 2.0211 | 0.0095433 | 2.2772 |  | 3 | 7 | 0.007 | 325.3085 | 9.1046 | 7.3369 | 0.029866 | 8.036 | 0.087108
2025-05-19 12:18 | 244 | Remove | 2025-05-19 | 12:18 | ST | GS | - | 5 | g | 0 | 112 | 11.594 | 1145.9 | 52635 | 2:02 | 29.1 | 2.35 m/s | 33.1 | 31 | 4.12 m/s | 23.3 |  | 2.35 | m/s |  | 4.12 | m/s | 2.0294 | 0.0095492 | 2.2867 |  | -2 | 5 | 0.005 | 457.3417 | 9.5671 | 7.4651 | 0.033071 | 8.0691 | 0.061965
2025-05-19 12:19 | 245 | Remove | 2025-05-19 | 12:19 | ST | GS | - | 7 | g | 0 | 112.1 | 11.612 | 1148.9 | 52645 | 2:02 | 29.1 | 2.67 m/s | 29.8 | 31 | 4.23 m/s | 20.6 |  | 2.67 | m/s |  | 4.23 | m/s | 2.0378 | 0.0095742 | 2.2963 |  | 2 | 7 | 0.007 | 328.0404 | 8.6133 | 6.6 | 0.033828 | 8.1029 | 0.086388
2025-05-19 12:19 | 246 | Remove | 2025-05-19 | 12:19 | US | GS | - | 3 | g | 0 | 112.2 | 11.608 | 1148.4 | 52655 | 2:03 | 29.1 | 2.26 m/s | 29.7 | 31.1 | 3.94 m/s | 21.4 |  | 2.26 | m/s |  | 3.94 | m/s | 2.0461 | 0.00957 | 2.3059 |  | -4 | 3 | 0.003 | 768.6175 | 8.5844 | 6.8933 | 0.028538 | 8.1315 | 0.036894
2025-05-19 12:20 | 247 | Remove | 2025-05-19 | 12:20 | ST | GS | - | 6 | g | 0 | 112.1 | 11.623 | 1150.2 | 52664 | 2:03 | 29.1 | 2.18 m/s | 29.7 | 31.1 | 4.38 m/s | 21.3 |  | 2.18 | m/s |  | 4.38 | m/s | 2.0544 | 0.009585 | 2.3154 |  | 3 | 6 | 0.006 | 385.9062 | 8.5844 | 6.8611 | 0.027528 | 8.159 | 0.073538
2025-05-19 12:20 | 248 | Remove | 2025-05-19 | 12:20 | US | GS | + | 9 | g | 0 | 112.2 | 11.588 | 1145.8 | 52674 | 2:04 | 29.2 | 2.51 m/s | 31.7 | 31.1 | 3.93 m/s | 22.2 |  | 2.51 | m/s |  | 3.93 | m/s | 2.0628 | 0.0095483 | 2.325 |  | 3 | 9 | 0.009 | 258.3318 | 9.2126 | 7.151 | 0.034014 | 8.193 | 0.10985
2025-05-19 12:21 | 249 | Remove | 2025-05-19 | 12:21 | US | GS | - | 6 | g | 0 | 112.1 | 11.621 | 1150.5 | 52683 | 2:04 | 29.2 | 2.6 m/s | 29.3 | 31.1 | 4.56 m/s | 20.5 |  | 2.6 | m/s |  | 4.56 | m/s | 2.0711 | 0.0095875 | 2.3346 |  | -3 | 6 | 0.006 | 389.0956 | 8.5151 | 6.6034 | 0.032566 | 8.2256 | 0.072943
2025-05-19 12:21 | 250 | Remove | 2025-05-19 | 12:21 | US | GS | - | 9.5 | g | 0 | 112.1 | 11.559 | 1142 | 52693 | 2:05 | 29.2 | 2.33 m/s | 29.1 | 31.1 | 3.84 m/s | 20.8 |  | 2.33 | m/s |  | 3.84 | m/s | 2.0794 | 0.0095167 | 2.3441 |  | 3.5 | 9.5 | 0.0095 | 246.7463 | 8.457 | 6.7 | 0.028985 | 8.2546 | 0.11509
2025-05-19 12:22 | 251 | Remove | 2025-05-19 | 12:22 | ST | GS | - | 6 | g | 0 | 112.1 | 11.565 | 1143.3 | 52703 | 2:05 | 29.1 | 2.38 m/s | 29.7 | 31.1 | 4.07 m/s | 20.6 |  | 2.38 | m/s |  | 4.07 | m/s | 2.0878 | 0.0095275 | 2.3536 |  | -3.5 | 6 | 0.006 | 392.2696 | 8.5844 | 6.6356 | 0.030053 | 8.2846 | 0.072423
2025-05-19 12:22 | 252 | Remove | 2025-05-19 | 12:22 | ST | GS | - | 8.5 | g | 0 | 112.2 | 11.518 | 1138.1 | 52712 | 2:06 | 29.1 | 2.48 m/s | 30.2 | 31.1 | 3.76 m/s | 20.8 |  | 2.48 | m/s |  | 3.76 | m/s | 2.0961 | 0.0094842 | 2.3631 |  | 2.5 | 8.5 | 0.0085 | 278.012 | 8.7289 | 6.7 | 0.031843 | 8.3165 | 0.10221
2025-05-19 12:23 | 253 | Remove | 2025-05-19 | 12:23 | ST | GS | - | 8 | g | 0 | 112.2 | 11.569 | 1143.9 | 52722 | 2:06 | 29.1 | 2.3 m/s | 30.2 | 31.1 | 3.6 m/s | 22.1 |  | 2.3 | m/s |  | 3.6 | m/s | 2.1044 | 0.0095325 | 2.3726 |  | -0.5 | 8 | 0.008 | 296.5793 | 8.7289 | 7.1188 | 0.029532 | 8.346 | 0.095854
2025-05-19 12:23 | 254 | Remove | 2025-05-19 | 12:23 | ST | GS | - | 8 | g | 0 | 112.3 | 11.547 | 1141.8 | 52731 | 2:07 | 29.1 | 2.48 m/s | 30.9 | 31.1 | 3.8 m/s | 21.6 |  | 2.48 | m/s |  | 3.8 | m/s | 2.1128 | 0.009515 | 2.3821 |  | 0 | 8 | 0.008 | 297.7686 | 8.9312 | 6.9577 | 0.032581 | 8.3786 | 0.095482
2025-05-19 12:24 | 255 | Remove | 2025-05-19 | 12:24 | US | GS | - | 8 | g | 0 | 112.2 | 11.596 | 1147 | 52741 | 2:07 | 29.1 | 2.26 m/s | 30.4 | 31 | 4.01 m/s | 21.1 |  | 2.26 | m/s |  | 4.01 | m/s | 2.1211 | 0.0095583 | 2.3917 |  | 0 | 8 | 0.008 | 298.9634 | 8.7867 | 6.7602 | 0.02921 | 8.4078 | 0.09515
2025-05-19 12:24 | 256 | Remove | 2025-05-19 | 12:24 | ST | GS | - | 4 | g | 0 | 112.1 | 11.567 | 1143.8 | 52750 | 2:08 | 29.1 | 3.02 m/s | 28.6 | 31 | 3.8 m/s | 21.4 |  | 3.02 | m/s |  | 3.8 | m/s | 2.1294 | 0.0095317 | 2.4012 |  | -4 | 4 | 0.004 | 600.3098 | 8.2664 | 6.8563 | 0.036722 | 8.4445 | 0.047368
2025-05-19 12:25 | 257 | Remove | 2025-05-19 | 12:25 | ST | GS | - | 5.5 | g | 0 | 112.2 | 11.542 | 1140.7 | 52760 | 2:08 | 29.1 | 2.83 m/s | 29.7 | 30.9 | 4.27 m/s | 22.5 |  | 2.83 | m/s |  | 4.27 | m/s | 2.1381 | 0.0095058 | 2.4107 |  | 1.5 | 5.5 | 0.0055 | 438.3173 | 8.5844 | 7.17 | 0.035735 | 8.4802 | 0.064857
2025-05-19 12:25 | 258 | Remove | 2025-05-19 | 12:25 | ST | GS | - | 8.5 | g | 0 | 112.1 | 11.543 | 1139.8 | 52769 | 2:09 | 29.1 | 2.64 m/s | 31.6 | 31 | 3.9 m/s | 22.1 |  | 2.64 | m/s |  | 3.9 | m/s | 2.1464 | 0.0094983 | 2.4202 |  | 3 | 8.5 | 0.0085 | 284.7345 | 9.1335 | 7.0806 | 0.035469 | 8.5157 | 0.099815
2025-05-19 12:26 | 259 | Remove | 2025-05-19 | 12:26 | ST | GS | - | 7.5 | g | 0 | 112.1 | 11.565 | 1143.4 | 52779 | 2:09 | 29.1 | 2.54 m/s | 29.6 | 30.9 | 4.0 m/s | 21.9 |  | 2.54 | m/s |  | 4 | m/s | 2.1547 | 0.0095283 | 2.4298 |  | -1 | 7.5 | 0.0075 | 323.9696 | 8.5555 | 6.9788 | 0.031965 | 8.5477 | 0.087743
2025-05-19 12:26 | 260 | Remove | 2025-05-19 | 12:26 | ST | GS | - | 7 | g | 0 | 112.1 | 11.54 | 1140.1 | 52788 | 2:10 | 29.1 | 2.97 m/s | 28.8 | 30.9 | 3.84 m/s | 21.3 |  | 2.97 | m/s |  | 3.84 | m/s | 2.1631 | 0.0095008 | 2.4393 |  | -0.5 | 7 | 0.007 | 348.4675 | 8.3242 | 6.7876 | 0.036367 | 8.584 | 0.081547
2025-05-19 12:27 | 261 | Remove | 2025-05-19 | 12:27 | US | GS | + | 0.5 | g | 0 | 112.2 | 11.535 | 1139.3 | 52798 | 2:10 | 29.1 | 2.97 m/s | 30.2 | 30.9 | 3.77 m/s | 22.5 |  | 2.97 | m/s |  | 3.77 | m/s | 2.1714 | 0.0094942 | 2.4488 |  | -6.5 | 0.5 | 0.0005 | 4897.5333 | 8.7289 | 7.17 | 0.038135 | 8.6222 | 0.005799
2025-05-19 12:27 | 262 | Remove | 2025-05-19 | 12:27 | US | GS | - | 0.5 | g | 0 | 112.2 | 11.574 | 1145 | 52808 | 2:11 | 29.1 | 3.03 m/s | 28.9 | 30.8 | 3.6 m/s | 20.9 |  | 3.03 | m/s |  | 3.6 | m/s | 2.1797 | 0.0095417 | 2.4583 |  | 0 | 0.5 | 0.0005 | 4916.6167 | 8.3531 | 6.6244 | 0.03723 | 8.6594 | 0.0057741
2025-05-19 12:28 | 263 | Remove | 2025-05-19 | 12:28 | US | GS | - | 4 | g | 0 | 112.1 | 11.533 | 1139.2 | 52817 | 2:11 | 29.1 | 3.11 m/s | 29.1 | 30.8 | 3.73 m/s | 21.1 |  | 3.11 | m/s |  | 3.73 | m/s | 2.1881 | 0.0094933 | 2.4678 |  | 3.5 | 4 | 0.004 | 616.9504 | 8.411 | 6.6878 | 0.038478 | 8.6979 | 0.045988
2025-05-19 12:28 | 264 | Remove | 2025-05-19 | 12:28 | ST | GS | - | 9.5 | g | 0 | 112.2 | 11.573 | 1144.3 | 52827 | 2:12 | 29.1 | 2.61 m/s | 29.1 | 30.7 | 3.68 m/s | 22.9 |  | 2.61 | m/s |  | 3.68 | m/s | 2.1964 | 0.0095358 | 2.4773 |  | 5.5 | 9.5 | 0.0095 | 260.7724 | 8.411 | 7.2193 | 0.032291 | 8.7302 | 0.10882
2025-05-19 12:29 | 265 | Remove | 2025-05-19 | 12:29 | ST | GS | - | 9 | g | 0 | 112.1 | 11.613 | 1148.5 | 52836 | 2:12 | 29.1 | 2.48 m/s | 29.4 | 30.8 | 3.85 m/s | 22.5 |  | 2.48 | m/s |  | 3.85 | m/s | 2.2047 | 0.0095708 | 2.4869 |  | -0.5 | 9 | 0.009 | 276.3231 | 8.4977 | 7.1315 | 0.030999 | 8.7612 | 0.10273
2025-05-19 12:29 | 266 | Remove | 2025-05-19 | 12:29 | US | GS | - | 12.5 | g | 0 | 112 | 11.654 | 1153.5 | 52846 | 2:13 | 29.1 | 2.4 m/s | 30.7 | 30.8 | 4.35 m/s | 21.7 |  | 2.4 | m/s |  | 4.35 | m/s | 2.2131 | 0.0096125 | 2.4965 |  | 3.5 | 12.5 | 0.0125 | 199.7217 | 8.8734 | 6.878 | 0.031326 | 8.7925 | 0.14217
2025-05-19 12:30 | 267 | Remove | 2025-05-19 | 12:30 | US | GS | - | 10.5 | g | 0 | 112 | 11.592 | 1146.3 | 52855 | 2:13 | 29.2 | 2.38 m/s | 31 | 30.9 | 4.0 m/s | 22.6 |  | 2.38 | m/s |  | 4 | m/s | 2.2214 | 0.0095525 | 2.5061 |  | -2 | 10.5 | 0.0105 | 238.6737 | 9.0092 | 7.2019 | 0.03154 | 8.824 | 0.11899
2025-05-19 12:30 | 268 | Remove | 2025-05-19 | 12:30 | US | GS | - | 8.5 | g | 0 | 112 | 11.616 | 1148.7 | 52865 | 2:14 | 29.2 | 2.57 m/s | 28.6 | 31 | 4.23 m/s | 20 |  | 2.57 | m/s |  | 4.23 | m/s | 2.2297 | 0.0095725 | 2.5156 |  | -2 | 8.5 | 0.0085 | 295.9583 | 8.3117 | 6.4078 | 0.031421 | 8.8555 | 0.095986
2025-05-19 12:31 | 269 | Remove | 2025-05-19 | 12:31 | US | GS | - | 6.5 | g | 0 | 111.9 | 11.643 | 1151.7 | 52875 | 2:14 | 29.2 | 2.08 m/s | 27.7 | 31 | 4.43 m/s | 21 |  | 2.08 | m/s |  | 4.43 | m/s | 2.2381 | 0.0095975 | 2.5252 |  | -2 | 6.5 | 0.0065 | 388.499 | 8.0501 | 6.7282 | 0.02463 | 8.8801 | 0.073197
2025-05-19 12:31 | 270 | Remove | 2025-05-19 | 12:31 | ST | GS | - | 9.5 | g | 0 | 112 | 11.616 | 1149 | 52884 | 2:15 | 29.2 | 2.48 m/s | 29.5 | 31 | 4.04 m/s | 22.5 |  | 2.48 | m/s |  | 4.04 | m/s | 2.2464 | 0.009575 | 2.5348 |  | 3 | 9.5 | 0.0095 | 266.823 | 8.5732 | 7.2088 | 0.031275 | 8.9114 | 0.10661
2025-05-19 12:32 | 271 | Keep | 2025-05-19 | 12:32 | ST | GS | - | 9.5 | g | 0 | 112 | 11.615 | 1148.1 | 52894 | 2:15 | 29.2 | 2.25 m/s | 27.4 | 31.1 | 4.24 m/s | 19 |  | 2.25 | m/s |  | 4.24 | m/s | 2.2547 | 0.0095675 | 2.5444 |  | 0 | 9.5 | 0.0095 | 267.8301 | 7.9629 | 6.1202 | 0.026355 | 8.9377 | 0.10629
2025-05-19 12:32 | 272 | Remove | 2025-05-19 | 12:32 | ST | GS | - | 11 | g | 0 | 111.9 | 11.631 | 1150 | 52903 | 2:16 | 29.2 | 2.2 m/s | 28.2 | 31.1 | 4.29 m/s | 19.8 |  | 2.2 | m/s |  | 4.29 | m/s | 2.2631 | 0.0095833 | 2.554 |  | 1.5 | 11 | 0.011 | 232.179 | 8.1954 | 6.3779 | 0.026521 | 8.9643 | 0.12271
2025-05-19 12:33 | 273 | Remove | 2025-05-19 | 12:33 | ST | GS | - | 17 | g | 0 | 112 | 11.595 | 1145.9 | 52913 | 2:16 | 29.2 | 2.09 m/s | 27.3 | 31.1 | 4.13 m/s | 20.2 |  | 2.09 | m/s |  | 4.13 | m/s | 2.2714 | 0.0095492 | 2.5635 |  | 6 | 17 | 0.017 | 150.7952 | 7.9339 | 6.5068 | 0.024391 | 8.9886 | 0.18913
2025-05-19 12:34 | 274 | Remove | 2025-05-19 | 12:34 | ST | GS | - | 10.5 | g | 0 | 111.9 | 11.636 | 1150.8 | 52923 | 2:17 | 29.2 | 2.18 m/s | 29.4 | 31.2 | 4.93 m/s | 21.1 |  | 2.18 | m/s |  | 4.93 | m/s | 2.28 | 0.00959 | 2.5731 |  | -6.5 | 10.5 | 0.0105 | 245.0579 | 8.5442 | 6.8333 | 0.027399 | 9.016 | 0.11646
2025-05-19 12:34 | 275 | Remove | 2025-05-19 | 12:34 | ST | GS | - | 12 | g | 0 | 111.9 | 11.638 | 1150.8 | 52932 | 2:17 | 29.3 | 2.05 m/s | 28.5 | 31.2 | 4.13 m/s | 19.8 |  | 2.05 | m/s |  | 4.13 | m/s | 2.2883 | 0.00959 | 2.5827 |  | 1.5 | 12 | 0.012 | 215.2249 | 8.3279 | 6.4123 | 0.025113 | 9.0412 | 0.13273
2025-05-19 12:34 | 276 | Remove | 2025-05-19 | 12:34 | ST | GS | - | 10 | g | 0 | 111.9 | 11.669 | 1155 | 52942 | 2:18 | 29.3 | 2.13 m/s | 27.6 | 31.2 | 4.24 m/s | 19.4 |  | 2.13 | m/s |  | 4.24 | m/s | 2.2967 | 0.009625 | 2.5923 |  | -2 | 10 | 0.01 | 259.2323 | 8.0649 | 6.2828 | 0.025269 | 9.0664 | 0.1103
2025-05-19 12:35 | 277 | Remove | 2025-05-19 | 12:35 | US | GS | - | 6 | g | 0 | 111.8 | 11.618 | 1148.8 | 52951 | 2:18 | 29.3 | 2.52 m/s | 26.1 | 31.2 | 3.86 m/s | 19.1 |  | 2.52 | m/s |  | 3.86 | m/s | 2.305 | 0.0095733 | 2.6019 |  | -4 | 6 | 0.006 | 433.6494 | 7.6266 | 6.1856 | 0.028271 | 9.0947 | 0.065973
2025-05-19 12:36 | 278 | Remove | 2025-05-19 | 12:36 | ST | GS | - | 12 | g | 0 | 111.9 | 11.632 | 1150.1 | 52961 | 2:19 | 29.3 | 2.13 m/s | 27.5 | 31.2 | 4.21 m/s | 18.8 |  | 2.13 | m/s |  | 4.21 | m/s | 2.3133 | 0.0095842 | 2.6115 |  | 6 | 12 | 0.012 | 217.6234 | 8.0357 | 6.0884 | 0.025177 | 9.1199 | 0.13158
2025-05-19 12:36 | 279 | Remove | 2025-05-19 | 12:36 | ST | GS | - | 13 | g | 0 | 111.9 | 11.565 | 1142.8 | 52971 | 2:19 | 29.3 | 2.27 m/s | 27.9 | 31.2 | 4.15 m/s | 20.5 |  | 2.27 | m/s |  | 4.15 | m/s | 2.3217 | 0.0095233 | 2.621 |  | 1 | 13 | 0.013 | 201.6157 | 8.1526 | 6.639 | 0.027222 | 9.1471 | 0.14212
2025-05-19 12:36 | 280 | Remove | 2025-05-19 | 12:36 | ST | GS | - | 11.5 | g | 0 | 111.9 | 11.606 | 1147.8 | 52980 | 2:20 | 29.2 | 2.4 m/s | 27.8 | 31.2 | 3.92 m/s | 21.7 |  | 2.4 | m/s |  | 3.92 | m/s | 2.33 | 0.009565 | 2.6306 |  | -1.5 | 11.5 | 0.0115 | 228.7451 | 8.0792 | 7.0276 | 0.028522 | 9.1756 | 0.12533
2025-05-19 12:37 | 281 | Remove | 2025-05-19 | 12:37 | ST | GS | - | 10 | g | 0 | 111.9 | 11.632 | 1150.4 | 52990 | 2:20 | 29.2 | 2.15 m/s | 29.8 | 31.2 | 3.97 m/s | 20.1 |  | 2.15 | m/s |  | 3.97 | m/s | 2.3383 | 0.0095867 | 2.6402 |  | -1.5 | 10 | 0.01 | 264.0156 | 8.6604 | 6.5095 | 0.027389 | 9.203 | 0.10866
2025-05-19 12:38 | 282 | Remove | 2025-05-19 | 12:38 | ST | GS | - | 8.5 | g | 0 | 111.9 | 11.7 | 1158.2 | 52999 | 2:21 | 29.2 | 2.19 m/s | 27.8 | 31.2 | 4.4 m/s | 19.6 |  | 2.19 | m/s |  | 4.4 | m/s | 2.3467 | 0.0096517 | 2.6498 |  | -1.5 | 8.5 | 0.0085 | 311.7421 | 8.0792 | 6.3475 | 0.026026 | 9.229 | 0.092101
2025-05-19 12:38 | 283 | Remove | 2025-05-19 | 12:38 | ST | GS | - | 12 | g | 0 | 111.8 | 11.692 | 1157.1 | 53009 | 2:21 | 29.3 | 2.34 m/s | 27.4 | 31.2 | 4.16 m/s | 21 |  | 2.34 | m/s |  | 4.16 | m/s | 2.355 | 0.0096425 | 2.6594 |  | 3.5 | 12 | 0.012 | 221.6208 | 8.0065 | 6.8009 | 0.027559 | 9.2566 | 0.12964
2025-05-19 12:38 | 284 | Remove | 2025-05-19 | 12:38 | ST | GS | - | 11.5 | g | 0 | 111.9 | 11.647 | 1151.8 | 53019 | 2:22 | 29.3 | 2.31 m/s | 27.3 | 31.2 | 3.93 m/s | 19 |  | 2.31 | m/s |  | 3.93 | m/s | 2.3633 | 0.0095983 | 2.669 |  | -0.5 | 11.5 | 0.0115 | 232.0912 | 7.9773 | 6.1532 | 0.027106 | 9.2837 | 0.12387
2025-05-19 12:39 | 285 | Remove | 2025-05-19 | 12:39 | ST | GS | - | 13 | g | 0 | 111.9 | 11.63 | 1150.8 | 53028 | 2:22 | 29.3 | 2.41 m/s | 28.7 | 31.2 | 4.09 m/s | 21.1 |  | 2.41 | m/s |  | 4.09 | m/s | 2.3717 | 0.00959 | 2.6786 |  | 1.5 | 13 | 0.013 | 206.0491 | 8.3863 | 6.8333 | 0.02973 | 9.3134 | 0.13958
2025-05-19 12:40 | 286 | Remove | 2025-05-19 | 12:39 | US | GS | - | 4 | g | 0 | 111.8 | 11.666 | 1154.6 | 53038 | 2:23 | 29.3 | 2.09 m/s | 31.5 | 31.2 | 4.1 m/s | 23.2 |  | 2.09 | m/s |  | 4.1 | m/s | 2.38 | 0.0096217 | 2.6883 |  | -9 | 4 | 0.004 | 672.065 | 9.2045 | 7.5134 | 0.028298 | 9.3417 | 0.042819
2025-05-19 12:40 | 287 | Remove | 2025-05-19 | 12:40 | US | GS | - | 9 | g | 0 | 111.9 | 11.649 | 1152.7 | 53048 | 2:23 | 29.3 | 2.71 m/s | 28.7 | 31.2 | 3.81 m/s | 19.6 |  | 2.71 | m/s |  | 3.81 | m/s | 2.3883 | 0.0096058 | 2.6979 |  | 5 | 9 | 0.009 | 299.7629 | 8.3863 | 6.3475 | 0.033431 | 9.3752 | 0.095998
2025-05-19 12:41 | 288 | Remove | 2025-05-19 | 12:41 | ST | GS | - | 10 | g | 0 | 111.8 | 11.623 | 1148.8 | 53057 | 2:24 | 29.3 | 2.34 m/s | 28.5 | 31.2 | 4.06 m/s | 20.3 |  | 2.34 | m/s |  | 4.06 | m/s | 2.3967 | 0.0095733 | 2.7074 |  | 1 | 10 | 0.01 | 270.7439 | 8.3279 | 6.5742 | 0.028665 | 9.4038 | 0.10634
2025-05-19 12:41 | 289 | Remove | 2025-05-19 | 12:41 | ST | GS | - | 10.5 | g | 0 | 111.9 | 11.66 | 1153.4 | 53067 | 2:24 | 29.3 | 2.22 m/s | 34.3 | 31.2 | 4.12 m/s | 23.6 |  | 2.22 | m/s |  | 4.12 | m/s | 2.405 | 0.0096117 | 2.7171 |  | 0.5 | 10.5 | 0.0105 | 258.7667 | 10.0227 | 7.6429 | 0.03273 | 9.4365 | 0.11127
2025-05-19 12:42 | 290 | Remove | 2025-05-19 | 12:42 | US | GS | - | 13 | g | 0 | 110.8 | 11.652 | 1149 | 53077 | 2:25 | 29.3 | 2.52 m/s | 33.1 | 31.2 | 4.03 m/s | 21.9 |  | 2.52 | m/s |  | 4.03 | m/s | 2.4133 | 0.009575 | 2.7266 |  | 2.5 | 13 | 0.013 | 209.7404 | 9.6721 | 7.0924 | 0.035853 | 9.4724 | 0.13724
2025-05-19 12:42 | 291 | Remove | 2025-05-19 | 12:42 | ST | GS | - | 14 | g | 0 | 111.2 | 11.615 | 1145.6 | 53086 | 2:25 | 29.3 | 2.47 m/s | 29.6 | 31.2 | 3.94 m/s | 20.9 |  | 2.47 | m/s |  | 3.94 | m/s | 2.4217 | 0.0095467 | 2.7362 |  | 1 | 14 | 0.014 | 195.4409 | 8.6493 | 6.7685 | 0.031425 | 9.5038 | 0.14731
2025-05-19 12:43 | 292 | Remove | 2025-05-19 | 12:43 | ST | GS | - | 13.5 | g | 0 | 111.7 | 11.613 | 1147.5 | 53096 | 2:26 | 29.3 | 2.42 m/s | 27.7 | 31.2 | 4.49 m/s | 20.3 |  | 2.42 | m/s |  | 4.49 | m/s | 2.4303 | 0.0095625 | 2.7457 |  | -0.5 | 13.5 | 0.0135 | 203.3878 | 8.0941 | 6.5742 | 0.028813 | 9.5326 | 0.14162
2025-05-19 12:43 | 293 | Remove | 2025-05-19 | 12:43 | ST | GS | - | 9 | g | 0 | 111.9 | 11.669 | 1155.1 | 53105 | 2:26 | 29.3 | 2.44 m/s | 29.1 | 31.2 | 4.2 m/s | 19.8 |  | 2.44 | m/s |  | 4.2 | m/s | 2.4386 | 0.0096258 | 2.7554 |  | -4.5 | 9 | 0.009 | 306.1512 | 8.5032 | 6.4123 | 0.030519 | 9.5632 | 0.094111
2025-05-19 12:44 | 294 | Remove | 2025-05-19 | 12:44 | ST | GS | - | 14.5 | g | 0 | 112 | 11.616 | 1149.4 | 53115 | 2:27 | 29.3 | 2.41 m/s | 28 | 31.2 | 3.79 m/s | 19 |  | 2.41 | m/s |  | 3.79 | m/s | 2.4469 | 0.0095783 | 2.7649 |  | 5.5 | 14.5 | 0.0145 | 190.6855 | 8.1818 | 6.1532 | 0.029005 | 9.5922 | 0.15117
2025-05-19 12:44 | 295 | Remove | 2025-05-19 | 12:44 | ST | GS | - | 9 | g | 0 | 112.1 | 11.707 | 1159.8 | 53125 | 2:27 | 29.3 | 2.2 m/s | 27.2 | 31.2 | 4.0 m/s | 19.1 |  | 2.2 | m/s |  | 4 | m/s | 2.4553 | 0.009665 | 2.7746 |  | -5.5 | 9 | 0.009 | 308.2894 | 7.948 | 6.1856 | 0.025721 | 9.6179 | 0.093576
2025-05-19 12:45 | 296 | Remove | 2025-05-19 | 12:45 | US | GS | - | 14.5 | g | 0 | 112.1 | 11.712 | 1160.8 | 53134 | 2:28 | 29.3 | 2.2 m/s | 28.4 | 31.3 | 4.29 m/s | 20.1 |  | 2.2 | m/s |  | 4.29 | m/s | 2.4636 | 0.0096733 | 2.7843 |  | 5.5 | 14.5 | 0.0145 | 192.0191 | 8.2987 | 6.5445 | 0.026856 | 9.6447 | 0.15034
2025-05-19 12:45 | 297 | Remove | 2025-05-19 | 12:45 | ST | GS | - | 13 | g | 0 | 112 | 11.707 | 1159.9 | 53144 | 2:28 | 29.3 | 2.22 m/s | 28.4 | 31.3 | 3.49 m/s | 20.3 |  | 2.22 | m/s |  | 3.49 | m/s | 2.4719 | 0.0096658 | 2.7939 |  | -1.5 | 13 | 0.013 | 214.9187 | 8.2987 | 6.6096 | 0.0271 | 9.6718 | 0.13441
2025-05-19 12:46 | 298 | Remove | 2025-05-19 | 12:46 | US | GS | - | 10.5 | g | 0 | 112 | 11.684 | 1157.2 | 53154 | 2:29 | 29.3 | 2.06 m/s | 27.8 | 31.3 | 4.12 m/s | 20.1 |  | 2.06 | m/s |  | 4.12 | m/s | 2.4803 | 0.0096433 | 2.8036 |  | -2.5 | 10.5 | 0.0105 | 267.0083 | 8.1234 | 6.5445 | 0.024615 | 9.6965 | 0.10829
2025-05-19 12:46 | 299 | Remove | 2025-05-19 | 12:46 | US | GS | - | 11 | g | 0 | 112 | 11.668 | 1155 | 53163 | 2:29 | 29.3 | 2.51 m/s | 30.7 | 31.3 | 4.01 m/s | 20.7 |  | 2.51 | m/s |  | 4.01 | m/s | 2.4886 | 0.009625 | 2.8132 |  | 0.5 | 11 | 0.011 | 255.7465 | 8.9708 | 6.7399 | 0.033121 | 9.7296 | 0.11306
2025-05-19 12:47 | 300 | Remove | 2025-05-19 | 12:47 | US | GS | - | 10.5 | g | 0 | 112 | 11.681 | 1156.4 | 53173 | 2:30 | 29.3 | 2.11 m/s | 31.9 | 31.3 | 3.89 m/s | 23.4 |  | 2.11 | m/s |  | 3.89 | m/s | 2.4969 | 0.0096367 | 2.8228 |  | -0.5 | 10.5 | 0.0105 | 268.8427 | 9.3214 | 7.619 | 0.028931 | 9.7585 | 0.1076
2025-05-19 12:47 | 301 | Keep | 2025-05-19 | 12:47 | ST | GS | - | 12.5 | g | 0 | 112 | 11.677 | 1156.7 | 53183 | 2:30 | 29.3 | 2.62 m/s | 27.4 | 31.3 | 3.94 m/s | 19.6 |  | 2.62 | m/s |  | 3.94 | m/s | 2.5053 | 0.0096392 | 2.8325 |  | 2 | 12.5 | 0.0125 | 226.599 | 8.0065 | 6.3817 | 0.030856 | 9.7894 | 0.12769
2025-05-19 12:48 | 302 | Remove | 2025-05-19 | 12:48 | US | GS | - | 5.5 | g | 0 | 111.9 | 11.708 | 1160 | 53192 | 2:31 | 29.3 | 2.41 m/s | 29.2 | 31.3 | 3.9 m/s | 19.7 |  | 2.41 | m/s |  | 3.9 | m/s | 2.5136 | 0.0096667 | 2.8422 |  | -7 | 5.5 | 0.0055 | 516.7553 | 8.5324 | 6.4143 | 0.030248 | 9.8196 | 0.05601
2025-05-19 12:48 | 303 | Remove | 2025-05-19 | 12:48 | US | GS | - | 8 | g | 0 | 112 | 11.705 | 1159.3 | 53202 | 2:31 | 29.3 | 2.37 m/s | 27.4 | 31.2 | 3.98 m/s | 19.8 |  | 2.37 | m/s |  | 3.98 | m/s | 2.5219 | 0.0096608 | 2.8518 |  | 2.5 | 8 | 0.008 | 356.4769 | 8.0065 | 6.4123 | 0.027912 | 9.8475 | 0.081239
2025-05-19 12:49 | 304 | Remove | 2025-05-19 | 12:49 | US | GS | - | 12.5 | g | 0 | 112 | 11.688 | 1158.5 | 53212 | 2:32 | 29.3 | 2.33 m/s | 30.5 | 31.2 | 3.8 m/s | 22.1 |  | 2.33 | m/s |  | 3.8 | m/s | 2.5303 | 0.0096542 | 2.8615 |  | 4.5 | 12.5 | 0.0125 | 228.9175 | 8.9123 | 7.1572 | 0.030546 | 9.8781 | 0.12654
2025-05-19 12:49 | 305 | Remove | 2025-05-19 | 12:49 | ST | GS | - | 14.5 | g | 0 | 112 | 11.663 | 1154.8 | 53221 | 2:32 | 29.3 | 2.67 m/s | 28.9 | 31.2 | 3.79 m/s | 20.1 |  | 2.67 | m/s |  | 3.79 | m/s | 2.5386 | 0.0096233 | 2.8711 |  | 2 | 14.5 | 0.0145 | 198.0064 | 8.4448 | 6.5095 | 0.033167 | 9.9112 | 0.1463
2025-05-19 12:50 | 306 | Remove | 2025-05-19 | 12:50 | ST | GS | - | 11.5 | g | 0 | 112 | 11.659 | 1154.4 | 53231 | 2:33 | 29.3 | 2.75 m/s | 29.8 | 31.2 | 4.01 m/s | 20.4 |  | 2.75 | m/s |  | 4.01 | m/s | 2.5469 | 0.00962 | 2.8807 |  | -3 | 11.5 | 0.0115 | 250.4967 | 8.7078 | 6.6066 | 0.035224 | 9.9465 | 0.11562
2025-05-19 12:50 | 307 | Remove | 2025-05-19 | 12:50 | ST | GS | - | 12.5 | g | 0 | 111.9 | 11.681 | 1156.2 | 53241 | 2:33 | 29.3 | 2.5 m/s | 27.9 | 31.1 | 3.81 m/s | 20 |  | 2.5 | m/s |  | 3.81 | m/s | 2.5553 | 0.009635 | 2.8903 |  | 1 | 12.5 | 0.0125 | 231.2278 | 8.1526 | 6.4423 | 0.02998 | 9.9764 | 0.1253
2025-05-19 12:51 | 308 | Remove | 2025-05-19 | 12:51 | ST | GS | - | 16 | g | 0 | 112 | 11.679 | 1156.9 | 53250 | 2:34 | 29.3 | 2.78 m/s | 27.7 | 31.1 | 3.85 m/s | 19.7 |  | 2.78 | m/s |  | 3.85 | m/s | 2.5636 | 0.0096408 | 2.9 |  | 3.5 | 16 | 0.016 | 181.2493 | 8.0941 | 6.3457 | 0.033099 | 10.0095 | 0.15985
2025-05-19 12:51 | 309 | Remove | 2025-05-19 | 12:51 | ST | GS | - | 15 | g | 0 | 112 | 11.66 | 1155.1 | 53260 | 2:34 | 29.3 | 2.64 m/s | 28.4 | 31.1 | 3.8 m/s | 22.5 |  | 2.64 | m/s |  | 3.8 | m/s | 2.5722 | 0.0096258 | 2.9096 |  | -1 | 15 | 0.015 | 193.9743 | 8.2987 | 7.2476 | 0.032227 | 10.0418 | 0.14938
2025-05-19 12:52 | 310 | Remove | 2025-05-19 | 12:52 | US | GS | - | 12 | g | 0 | 112 | 11.639 | 1151.6 | 53270 | 2:35 | 29.3 | 2.34 m/s | 28.4 | 31.1 | 3.79 m/s | 20.1 |  | 2.34 | m/s |  | 3.79 | m/s | 2.5806 | 0.0095967 | 2.9192 |  | -3 | 12 | 0.012 | 243.2676 | 8.2987 | 6.4746 | 0.028565 | 10.0703 | 0.11916
2025-05-19 12:52 | 311 | Remove | 2025-05-19 | 12:52 | US | GS | + | 1 | g | 0 | 112 | 11.676 | 1157 | 53279 | 2:35 | 29.3 | 2.18 m/s | 27.5 | 31.1 | 3.89 m/s | 20.1 |  | 2.18 | m/s |  | 3.89 | m/s | 2.5889 | 0.0096417 | 2.9289 |  | -11 | 1 | 0.001 | 2928.8525 | 8.0357 | 6.4746 | 0.025768 | 10.0961 | 0.0099048
2025-05-19 12:53 | 312 | Remove | 2025-05-19 | 12:53 | ST | GS | - | 12 | g | 0 | 112 | 11.673 | 1156.9 | 53289 | 2:36 | 29.3 | 2.5 m/s | 27.2 | 31.1 | 3.94 m/s | 20.9 |  | 2.5 | m/s |  | 3.94 | m/s | 2.5972 | 0.0096408 | 2.9385 |  | 11 | 12 | 0.012 | 244.8744 | 7.948 | 6.7322 | 0.029228 | 10.1253 | 0.11851
2025-05-19 12:53 | 313 | Remove | 2025-05-19 | 12:53 | US | GS | - | 6 | g | 0 | 111.9 | 11.633 | 1150.9 | 53299 | 2:36 | 29.3 | 2.31 m/s | 30.3 | 31.1 | 3.9 m/s | 22.1 |  | 2.31 | m/s |  | 3.9 | m/s | 2.6056 | 0.0095908 | 2.9481 |  | -6 | 6 | 0.006 | 491.3474 | 8.8539 | 7.1188 | 0.030085 | 10.1554 | 0.059082
2025-05-19 12:54 | 314 | Remove | 2025-05-19 | 12:54 | ST | GS | - | 10.5 | g | 0 | 111.9 | 11.699 | 1158.9 | 53308 | 2:37 | 29.3 | 2.25 m/s | 28.5 | 31.1 | 4.12 m/s | 21 |  | 2.25 | m/s |  | 4.12 | m/s | 2.6139 | 0.0096575 | 2.9577 |  | 4.5 | 10.5 | 0.0105 | 281.6897 | 8.3279 | 6.7645 | 0.027563 | 10.183 | 0.10311
2025-05-19 12:54 | 315 | Remove | 2025-05-19 | 12:54 | ST | GS | - | 12.5 | g | 0 | 112 | 11.672 | 1155.6 | 53318 | 2:37 | 29.3 | 2.8 m/s | 28.6 | 31.1 | 4.3 m/s | 20 |  | 2.8 | m/s |  | 4.3 | m/s | 2.6222 | 0.00963 | 2.9674 |  | 2 | 12.5 | 0.0125 | 237.3897 | 8.3571 | 6.4423 | 0.03442 | 10.2174 | 0.12234
2025-05-19 12:55 | 316 | Remove | 2025-05-19 | 12:55 | ST | GS | - | 11.5 | g | 0 | 112 | 11.673 | 1155.7 | 53328 | 2:38 | 29.3 | 2.19 m/s | 30.1 | 31.2 | 4.73 m/s | 21.8 |  | 2.19 | m/s |  | 4.73 | m/s | 2.6306 | 0.0096308 | 2.977 |  | -1 | 11.5 | 0.0115 | 258.8698 | 8.7954 | 7.06 | 0.028334 | 10.2457 | 0.11224
2025-05-19 12:55 | 317 | Remove | 2025-05-19 | 12:55 | US | GS | - | 16 | g | 0 | 111.9 | 11.679 | 1156.5 | 53337 | 2:38 | 29.3 | 2.4 m/s | 30.7 | 31.2 | 3.98 m/s | 23 |  | 2.4 | m/s |  | 3.98 | m/s | 2.6389 | 0.0096375 | 2.9866 |  | 4.5 | 16 | 0.016 | 186.665 | 8.9708 | 7.4486 | 0.03167 | 10.2774 | 0.15568
2025-05-19 12:56 | 318 | Remove | 2025-05-19 | 12:56 | US | GS | - | 15.5 | g | 0 | 112 | 11.652 | 1153.9 | 53347 | 2:39 | 29.3 | 2.75 m/s | 29.4 | 31.2 | 3.89 m/s | 21.4 |  | 2.75 | m/s |  | 3.89 | m/s | 2.6472 | 0.0096158 | 2.9963 |  | -0.5 | 15.5 | 0.0155 | 193.3068 | 8.5909 | 6.9305 | 0.034751 | 10.3121 | 0.15031
2025-05-19 12:56 | 319 | Remove | 2025-05-19 | 12:56 | US | GS | - | 13.5 | g | 0 | 112.1 | 11.656 | 1154.5 | 53357 | 2:39 | 29.3 | 2.72 m/s | 27.9 | 31.2 | 3.86 m/s | 19.8 |  | 2.72 | m/s |  | 3.86 | m/s | 2.6556 | 0.0096208 | 3.0059 |  | -2 | 13.5 | 0.0135 | 222.6575 | 8.1526 | 6.4123 | 0.032619 | 10.3448 | 0.1305
2025-05-19 12:57 | 320 | Remove | 2025-05-19 | 12:57 | ST | GS | - | 11 | g | 0 | 112.1 | 11.703 | 1160.4 | 53366 | 2:40 | 29.3 | 2.48 m/s | 28 | 31.2 | 4.13 m/s | 20.2 |  | 2.48 | m/s |  | 4.13 | m/s | 2.6639 | 0.00967 | 3.0155 |  | -2.5 | 11 | 0.011 | 274.1406 | 8.1818 | 6.5418 | 0.029847 | 10.3746 | 0.10603
2025-05-19 12:57 | 321 | Remove | 2025-05-19 | 12:57 | ST | GS | - | 17 | g | 0 | 112.2 | 11.665 | 1156.4 | 53376 | 2:40 | 29.4 | 2.52 m/s | 28.4 | 31.2 | 3.89 m/s | 19.8 |  | 2.52 | m/s |  | 3.89 | m/s | 2.6722 | 0.0096367 | 3.0252 |  | 6 | 17 | 0.017 | 177.952 | 8.344 | 6.4123 | 0.03093 | 10.4055 | 0.16337
2025-05-19 12:58 | 322 | Remove | 2025-05-19 | 12:58 | US | GS | - | 16.5 | g | 0 | 112.2 | 11.672 | 1157.4 | 53386 | 2:41 | 29.4 | 2.38 m/s | 27.8 | 31.2 | 3.77 m/s | 20 |  | 2.38 | m/s |  | 3.77 | m/s | 2.6806 | 0.009645 | 3.0348 |  | -0.5 | 16.5 | 0.0165 | 183.929 | 8.1677 | 6.4771 | 0.028594 | 10.4341 | 0.15813
2025-05-19 12:58 | 323 | Remove | 2025-05-19 | 12:58 | US | GS | - | 16 | g | 0 | 112 | 11.693 | 1158.8 | 53395 | 2:41 | 29.4 | 2.51 m/s | 27.6 | 31.1 | 3.9 m/s | 19.5 |  | 2.51 | m/s |  | 3.9 | m/s | 2.6889 | 0.0096567 | 3.0445 |  | -0.5 | 16 | 0.016 | 190.2803 | 8.109 | 6.2813 | 0.029939 | 10.4641 | 0.1529
2025-05-19 12:59 | 324 | Remove | 2025-05-19 | 12:59 | US | GS | - | 13.5 | g | 0 | 112.1 | 11.679 | 1157.2 | 53405 | 2:42 | 29.4 | 2.26 m/s | 27.1 | 31.1 | 3.94 m/s | 20 |  | 2.26 | m/s |  | 3.94 | m/s | 2.6972 | 0.0096433 | 3.0541 |  | -2.5 | 13.5 | 0.0135 | 226.2317 | 7.9621 | 6.4423 | 0.026469 | 10.4905 | 0.12869
2025-05-19 12:59 | 325 | Remove | 2025-05-19 | 12:59 | ST | GS | - | 12 | g | 0 | 112 | 11.715 | 1161.4 | 53415 | 2:42 | 29.4 | 2.38 m/s | 27 | 31.1 | 3.9 m/s | 19.1 |  | 2.38 | m/s |  | 3.9 | m/s | 2.7056 | 0.0096783 | 3.0638 |  | -1.5 | 12 | 0.012 | 255.3172 | 7.9327 | 6.1524 | 0.027772 | 10.5183 | 0.11409
2025-05-19 13:00 | 326 | Remove | 2025-05-19 | 13:00 | US | GS | - | 16.5 | g | 0 | 112 | 11.684 | 1158.2 | 53424 | 2:43 | 29.4 | 2.16 m/s | 27.1 | 31.1 | 3.77 m/s | 20.4 |  | 2.16 | m/s |  | 3.77 | m/s | 2.7142 | 0.0096517 | 3.0735 |  | 4.5 | 16.5 | 0.0165 | 186.2702 | 7.9621 | 6.5712 | 0.025298 | 10.5436 | 0.15649
2025-05-19 13:00 | 327 | Remove | 2025-05-19 | 13:00 | ST | GS | - | 13.5 | g | 0 | 112 | 11.661 | 1155.4 | 53434 | 2:43 | 29.4 | 2.42 m/s | 26.8 | 31.2 | 3.85 m/s | 20.7 |  | 2.42 | m/s |  | 3.85 | m/s | 2.7225 | 0.0096283 | 3.0831 |  | -3 | 13.5 | 0.0135 | 228.3768 | 7.8739 | 6.7038 | 0.028029 | 10.5716 | 0.1277
2025-05-19 13:01 | 328 | Remove | 2025-05-19 | 13:01 | ST | GS | - | 11.5 | g | 0 | 111.9 | 11.718 | 1161.9 | 53444 | 2:44 | 29.4 | 2.09 m/s | 27.3 | 31.2 | 4.56 m/s | 20 |  | 2.09 | m/s |  | 4.56 | m/s | 2.7308 | 0.0096825 | 3.0928 |  | -2 | 11.5 | 0.0115 | 268.9364 | 8.0208 | 6.4771 | 0.024659 | 10.5963 | 0.10853
2025-05-19 13:01 | 329 | Remove | 2025-05-19 | 13:01 | ST | GS | - | 13.5 | g | 0 | 111.9 | 11.709 | 1160.9 | 53453 | 2:44 | 29.4 | 2.61 m/s | 29 | 31.2 | 3.9 m/s | 20.9 |  | 2.61 | m/s |  | 3.9 | m/s | 2.7394 | 0.0096742 | 3.1024 |  | 2 | 13.5 | 0.0135 | 229.8106 | 8.5203 | 6.7685 | 0.032711 | 10.629 | 0.12701
2025-05-19 13:02 | 330 | Remove | 2025-05-19 | 13:02 | ST | GS | - | 12.5 | g | 0 | 111.9 | 11.749 | 1165.4 | 53463 | 2:45 | 29.4 | 1.97 m/s | 29.1 | 31.2 | 3.85 m/s | 21.9 |  | 1.97 | m/s |  | 3.85 | m/s | 2.7478 | 0.0097117 | 3.1122 |  | -1 | 12.5 | 0.0125 | 248.9724 | 8.5497 | 7.0924 | 0.024775 | 10.6538 | 0.11733
2025-05-19 13:02 | 331 | Keep | 2025-05-19 | 13:02 | ST | GS | - | 13 | g | 0 | 111.8 | 11.725 | 1162.2 | 53473 | 2:45 | 29.4 | 2.64 m/s | 29.1 | 31.2 | 3.85 m/s | 21.3 |  | 2.64 | m/s |  | 3.85 | m/s | 2.7561 | 0.009685 | 3.1218 |  | 0.5 | 13 | 0.013 | 240.1415 | 8.5497 | 6.8981 | 0.033201 | 10.687 | 0.12164
2025-05-19 13:03 | 332 | Remove | 2025-05-19 | 13:03 | US | GS | - | 11.5 | g | 0 | 111.8 | 11.758 | 1166.3 | 53482 | 2:46 | 29.5 | 2.35 m/s | 28.4 | 31.2 | 4.0 m/s | 20.3 |  | 2.35 | m/s |  | 4 | m/s | 2.7644 | 0.0097192 | 3.1316 |  | -1.5 | 11.5 | 0.0115 | 272.3095 | 8.3896 | 6.5742 | 0.029001 | 10.716 | 0.10732
2025-05-19 13:03 | 333 | Remove | 2025-05-19 | 13:03 | ST | GS | - | 14 | g | 0 | 111.7 | 11.732 | 1162.2 | 53492 | 2:46 | 29.5 | 2.13 m/s | 26.3 | 31.2 | 4.67 m/s | 20.6 |  | 2.13 | m/s |  | 4.67 | m/s | 2.7728 | 0.009685 | 3.1412 |  | 2.5 | 14 | 0.014 | 224.3746 | 7.7692 | 6.6714 | 0.024342 | 10.7403 | 0.13035
2025-05-19 13:04 | 334 | Remove | 2025-05-19 | 13:04 | ST | GS | - | 14.5 | g | 0 | 111.7 | 11.774 | 1167.8 | 53502 | 2:47 | 29.5 | 2.88 m/s | 30 | 31.2 | 3.77 m/s | 19.7 |  | 2.88 | m/s |  | 3.77 | m/s | 2.7811 | 0.0097317 | 3.151 |  | 0.5 | 14.5 | 0.0145 | 217.3087 | 8.8622 | 6.3799 | 0.037544 | 10.7779 | 0.13453
2025-05-19 13:04 | 335 | Remove | 2025-05-19 | 13:04 | ST | GS | - | 13 | g | 0 | 111.7 | 11.677 | 1155.9 | 53512 | 2:47 | 29.5 | 3.02 m/s | 32.9 | 31.2 | 3.84 m/s | 21.4 |  | 3.02 | m/s |  | 3.84 | m/s | 2.7894 | 0.0096325 | 3.1606 |  | -1.5 | 13 | 0.013 | 243.1237 | 9.7189 | 6.9305 | 0.043174 | 10.8211 | 0.12014
2025-05-19 13:05 | 336 | Remove | 2025-05-19 | 13:05 | ST | GS | - | 10.5 | g | 0 | 111.6 | 11.761 | 1166.1 | 53521 | 2:48 | 29.5 | 2.19 m/s | 28.9 | 31.2 | 3.78 m/s | 21 |  | 2.19 | m/s |  | 3.78 | m/s | 2.7978 | 0.0097175 | 3.1703 |  | -2.5 | 10.5 | 0.0105 | 301.9358 | 8.5373 | 6.8009 | 0.027502 | 10.8486 | 0.096787
2025-05-19 13:05 | 337 | Remove | 2025-05-19 | 13:05 | ST | GS | - | 18 | g | 0 | 111.7 | 11.751 | 1165.1 | 53531 | 2:48 | 29.5 | 2.26 m/s | 28.3 | 31.2 | 4.04 m/s | 20.9 |  | 2.26 | m/s |  | 4.04 | m/s | 2.8061 | 0.0097092 | 3.18 |  | 7.5 | 18 | 0.018 | 176.6686 | 8.36 | 6.7685 | 0.027792 | 10.8763 | 0.1655
2025-05-19 13:06 | 338 | Remove | 2025-05-19 | 13:06 | ST | GS | - | 12 | g | 0 | 111.7 | 11.735 | 1162.7 | 53541 | 2:49 | 29.5 | 2.42 m/s | 27.7 | 31.3 | 4.24 m/s | 20 |  | 2.42 | m/s |  | 4.24 | m/s | 2.8144 | 0.0096892 | 3.1897 |  | -6 | 12 | 0.012 | 265.8103 | 8.1828 | 6.5119 | 0.029129 | 10.9055 | 0.11004
2025-05-19 13:06 | 339 | Remove | 2025-05-19 | 13:06 | ST | GS | - | 12.5 | g | 0 | 111.6 | 11.747 | 1164.1 | 53551 | 2:49 | 29.5 | 2.44 m/s | 30.1 | 31.3 | 4.15 m/s | 20.1 |  | 2.44 | m/s |  | 4.15 | m/s | 2.8228 | 0.0097008 | 3.1994 |  | 0.5 | 12.5 | 0.0125 | 255.954 | 8.8918 | 6.5445 | 0.031914 | 10.9374 | 0.11429
2025-05-19 13:07 | 340 | Remove | 2025-05-19 | 13:07 | US | GS | - | 12 | g | 0 | 111.8 | 11.756 | 1165.4 | 53560 | 2:50 | 29.5 | 2.16 m/s | 27.9 | 31.3 | 4.06 m/s | 20.5 |  | 2.16 | m/s |  | 4.06 | m/s | 2.8311 | 0.0097117 | 3.2091 |  | -0.5 | 12 | 0.012 | 267.4281 | 8.2419 | 6.6747 | 0.026187 | 10.9636 | 0.10945
2025-05-19 13:07 | 341 | Remove | 2025-05-19 | 13:07 | US | GS | - | 14.5 | g | 0 | 111.6 | 11.798 | 1170.3 | 53570 | 2:50 | 29.5 | 2.77 m/s | 29 | 31.3 | 3.88 m/s | 19.7 |  | 2.77 | m/s |  | 3.88 | m/s | 2.8394 | 0.0097525 | 3.2189 |  | 2.5 | 14.5 | 0.0145 | 221.9924 | 8.5668 | 6.4143 | 0.034906 | 10.9985 | 0.13184
2025-05-19 13:08 | 342 | Remove | 2025-05-19 | 13:08 | US | GS | - | 12 | g | 0 | 111.5 | 11.762 | 1165.7 | 53580 | 2:51 | 29.5 | 1.94 m/s | 28.8 | 31.4 | 3.8 m/s | 20.1 |  | 1.94 | m/s |  | 3.8 | m/s | 2.8478 | 0.0097142 | 3.2286 |  | -2.5 | 12 | 0.012 | 269.0503 | 8.5077 | 6.5797 | 0.024278 | 11.0228 | 0.10887
2025-05-19 13:08 | 343 | Remove | 2025-05-19 | 13:08 | ST | GS | - | 12.5 | g | 0 | 111.7 | 11.768 | 1167 | 53590 | 2:51 | 29.5 | 2.15 m/s | 29.6 | 31.4 | 4.26 m/s | 22.3 |  | 2.15 | m/s |  | 4.26 | m/s | 2.8561 | 0.009725 | 3.2383 |  | 0.5 | 12.5 | 0.0125 | 259.0663 | 8.7441 | 7.2999 | 0.027654 | 11.0504 | 0.11312
2025-05-19 13:09 | 344 | Remove | 2025-05-19 | 13:09 | ST | GS | - | 12.5 | g | 0 | 111.6 | 11.721 | 1160.6 | 53599 | 2:52 | 29.5 | 2.6 m/s | 28.7 | 31.4 | 3.92 m/s | 21.1 |  | 2.6 | m/s |  | 3.92 | m/s | 2.8647 | 0.0096717 | 3.248 |  | 0 | 12.5 | 0.0125 | 259.84 | 8.4782 | 6.9071 | 0.032425 | 11.0828 | 0.11279
2025-05-19 13:09 | 345 | Remove | 2025-05-19 | 13:09 | US | GS | - | 14 | g | 0 | 111.8 | 11.681 | 1157 | 53609 | 2:52 | 29.5 | 2.61 m/s | 29.1 | 31.4 | 3.79 m/s | 23.6 |  | 2.61 | m/s |  | 3.79 | m/s | 2.8731 | 0.0096417 | 3.2576 |  | 1.5 | 14 | 0.014 | 232.6887 | 8.5964 | 7.7255 | 0.033003 | 11.1158 | 0.12595
2025-05-19 13:10 | 346 | Remove | 2025-05-19 | 13:10 | US | GS | - | 12 | g | 0 | 111.7 | 11.714 | 1160.4 | 53619 | 2:53 | 29.5 | 2.34 m/s | 30.4 | 31.3 | 3.68 m/s | 21.7 |  | 2.34 | m/s |  | 3.68 | m/s | 2.8814 | 0.00967 | 3.2673 |  | -2 | 12 | 0.012 | 272.276 | 8.9804 | 7.0655 | 0.030911 | 11.1468 | 0.10765
2025-05-19 13:10 | 347 | Remove | 2025-05-19 | 13:10 | US | GS | - | 12 | g | 0 | 111.6 | 11.765 | 1165.3 | 53628 | 2:53 | 29.5 | 2.25 m/s | 28.7 | 31.3 | 3.8 m/s | 21.3 |  | 2.25 | m/s |  | 3.8 | m/s | 2.8897 | 0.0097108 | 3.277 |  | 0 | 12 | 0.012 | 273.0852 | 8.4782 | 6.9352 | 0.02806 | 11.1748 | 0.10738
2025-05-19 13:11 | 348 | Remove | 2025-05-19 | 13:11 | US | GS | - | 16.5 | g | 0 | 111.7 | 11.72 | 1160.2 | 53638 | 2:54 | 29.5 | 2.74 m/s | 28 | 31.3 | 4.04 m/s | 19.5 |  | 2.74 | m/s |  | 4.04 | m/s | 2.8981 | 0.0096683 | 3.2867 |  | 4.5 | 16.5 | 0.0165 | 199.1934 | 8.2714 | 6.3491 | 0.033337 | 11.2082 | 0.14721
2025-05-19 13:11 | 349 | Remove | 2025-05-19 | 13:11 | ST | GS | - | 11.5 | g | 0 | 111.6 | 11.745 | 1163.6 | 53648 | 2:54 | 29.5 | 2.55 m/s | 29.2 | 31.3 | 3.92 m/s | 19.7 |  | 2.55 | m/s |  | 3.92 | m/s | 2.9064 | 0.0096967 | 3.2964 |  | -5 | 11.5 | 0.0115 | 286.6424 | 8.6259 | 6.4143 | 0.032355 | 11.2405 | 0.10231
2025-05-19 13:12 | 350 | Remove | 2025-05-19 | 13:12 | ST | GS | - | 14.5 | g | 0 | 111.7 | 11.726 | 1161.4 | 53658 | 2:55 | 29.5 | 2.5 m/s | 26.7 | 31.3 | 4.27 m/s | 18.9 |  | 2.5 | m/s |  | 4.27 | m/s | 2.9147 | 0.0096783 | 3.3061 |  | 3 | 14.5 | 0.0145 | 228.0045 | 7.8874 | 6.1538 | 0.029005 | 11.2695 | 0.12867
2025-05-19 13:12 | 351 | Remove | 2025-05-19 | 13:12 | US | GS | - | 18 | g | 0 | 111.7 | 11.748 | 1163.8 | 53667 | 2:55 | 29.5 | 2.23 m/s | 27.6 | 31.3 | 3.94 m/s | 19.3 |  | 2.23 | m/s |  | 3.94 | m/s | 2.9231 | 0.0096983 | 3.3158 |  | 3.5 | 18 | 0.018 | 184.2091 | 8.1533 | 6.284 | 0.026745 | 11.2963 | 0.15934
2025-05-19 13:13 | 352 | Remove | 2025-05-19 | 13:13 | US | GS | - | 15.5 | g | 0 | 111.6 | 11.753 | 1164.5 | 53677 | 2:56 | 29.5 | 2.15 m/s | 29 | 31.3 | 4.03 m/s | 20.5 |  | 2.15 | m/s |  | 4.03 | m/s | 2.9314 | 0.0097042 | 3.3255 |  | -2.5 | 15.5 | 0.0155 | 214.5463 | 8.5668 | 6.6747 | 0.027093 | 11.3234 | 0.13689
2025-05-19 13:13 | 353 | Remove | 2025-05-19 | 13:13 | US | GS | - | 24 | g | 0 | 111.5 | 11.793 | 1168.8 | 53687 | 2:56 | 29.5 | 2.34 m/s | 27 | 31.3 | 4.06 m/s | 19.5 |  | 2.34 | m/s |  | 4.06 | m/s | 2.9397 | 0.00974 | 3.3352 |  | 8.5 | 24 | 0.024 | 138.967 | 7.976 | 6.3491 | 0.027454 | 11.3508 | 0.21144
2025-05-19 13:14 | 354 | Remove | 2025-05-19 | 13:14 | US | GS | - | 23 | g | 0 | 111.5 | 11.787 | 1168.1 | 53697 | 2:57 | 29.5 | 2.35 m/s | 27.5 | 31.3 | 3.85 m/s | 19.5 |  | 2.35 | m/s |  | 3.85 | m/s | 2.9481 | 0.0097342 | 3.3449 |  | -1 | 23 | 0.023 | 145.4323 | 8.1237 | 6.3491 | 0.028082 | 11.3789 | 0.20213
2025-05-19 13:14 | 355 | Remove | 2025-05-19 | 13:14 | ST | GS | - | 16.5 | g | 0 | 111.7 | 11.707 | 1158.6 | 53706 | 2:57 | 29.5 | 3.57 m/s | 27.5 | 31.4 | 3.93 m/s | 18.7 |  | 3.57 | m/s |  | 3.93 | m/s | 2.9564 | 0.009655 | 3.3546 |  | -6.5 | 16.5 | 0.0165 | 203.3089 | 8.1237 | 6.1214 | 0.04266 | 11.4215 | 0.14446
2025-05-19 13:15 | 356 | Remove | 2025-05-19 | 13:15 | ST | GS | - | 11 | g | 0 | 111.7 | 11.738 | 1162.6 | 53716 | 2:58 | 29.5 | 2.72 m/s | 27.2 | 31.3 | 3.81 m/s | 19.8 |  | 2.72 | m/s |  | 3.81 | m/s | 2.9647 | 0.0096883 | 3.3643 |  | -5.5 | 11 | 0.011 | 305.8442 | 8.0351 | 6.4468 | 0.032149 | 11.4537 | 0.096039
2025-05-19 13:15 | 357 | Remove | 2025-05-19 | 13:15 | US | GS | - | 14.5 | g | 0 | 111.5 | 11.742 | 1162.4 | 53726 | 2:58 | 29.5 | 2.27 m/s | 27.5 | 31.3 | 3.77 m/s | 20.4 |  | 2.27 | m/s |  | 3.77 | m/s | 2.9731 | 0.0096867 | 3.374 |  | 3.5 | 14.5 | 0.0145 | 232.6878 | 8.1237 | 6.6422 | 0.027126 | 11.4808 | 0.1263
2025-05-19 13:16 | 358 | Remove | 2025-05-19 | 13:16 | ST | GS | - | 13 | g | 0 | 111.7 | 11.753 | 1164 | 53735 | 2:59 | 29.5 | 2.41 m/s | 27.7 | 31.3 | 3.96 m/s | 20.1 |  | 2.41 | m/s |  | 3.96 | m/s | 2.9814 | 0.0097 | 3.3837 |  | -1.5 | 13 | 0.013 | 260.2825 | 8.1828 | 6.5445 | 0.029008 | 11.5098 | 0.11295
2025-05-19 13:16 | 359 | Remove | 2025-05-19 | 13:16 | ST | GS | - | 10.5 | g | 0 | 111.7 | 11.74 | 1162.9 | 53745 | 2:59 | 29.5 | 2.64 m/s | 28.6 | 31.3 | 3.93 m/s | 19.8 |  | 2.64 | m/s |  | 3.93 | m/s | 2.9897 | 0.0096908 | 3.3934 |  | -2.5 | 10.5 | 0.0105 | 323.1775 | 8.4487 | 6.4468 | 0.032809 | 11.5426 | 0.090967
2025-05-19 13:17 | 360 | Remove | 2025-05-19 | 13:17 | ST | GS | - | 12.5 | g | 0 | 111.7 | 11.716 | 1160.4 | 53755 | 3:00 | 29.5 | 2.38 m/s | 29.7 | 31.3 | 3.8 m/s | 20.8 |  | 2.38 | m/s |  | 3.8 | m/s | 2.9981 | 0.00967 | 3.403 |  | 2 | 12.5 | 0.0125 | 272.2427 | 8.7736 | 6.7724 | 0.030715 | 11.5734 | 0.10801
2025-05-19 13:17 | 361 | Keep | 2025-05-19 | 13:17 | ST | GS | - | 14.5 | g | 0 | 111.6 | 11.737 | 1162.2 | 53764 | 3:00 | 29.5 | 2.33 m/s | 27.9 | 31.2 | 3.79 m/s | 20.5 |  | 2.33 | m/s |  | 3.79 | m/s | 3.0064 | 0.009685 | 3.4127 |  | 2 | 14.5 | 0.0145 | 235.3599 | 8.2419 | 6.639 | 0.028248 | 11.6016 | 0.12498
2025-05-19 13:18 | 362 | Remove | 2025-05-19 | 13:18 | ST | GS | - | 15 | g | 0 | 111.5 | 11.767 | 1165.5 | 53774 | 3:01 | 29.5 | 2.64 m/s | 29 | 31.2 | 4.0 m/s | 21.4 |  | 2.64 | m/s |  | 4 | m/s | 3.015 | 0.0097125 | 3.4224 |  | 0.5 | 15 | 0.015 | 228.1621 | 8.5668 | 6.9305 | 0.033268 | 11.6349 | 0.12892
2025-05-19 13:18 | 363 | Remove | 2025-05-19 | 13:18 | ST | GS | - | 14.5 | g | 0 | 111.5 | 11.77 | 1166.4 | 53784 | 3:01 | 29.5 | 2.05 m/s | 29.9 | 31.3 | 3.92 m/s | 21.5 |  | 2.05 | m/s |  | 3.92 | m/s | 3.0233 | 0.00972 | 3.4322 |  | -0.5 | 14.5 | 0.0145 | 236.7001 | 8.8327 | 7.0003 | 0.026635 | 11.6615 | 0.12434
2025-05-19 13:19 | 364 | Remove | 2025-05-19 | 13:19 | ST | GS | - | 11 | g | 0 | 111.5 | 11.757 | 1164.6 | 53794 | 3:02 | 29.5 | 2.51 m/s | 27.5 | 31.3 | 4.13 m/s | 19.5 |  | 2.51 | m/s |  | 4.13 | m/s | 3.0317 | 0.009705 | 3.4419 |  | -3.5 | 11 | 0.011 | 312.896 | 8.1237 | 6.3491 | 0.029994 | 11.6915 | 0.094085
2025-05-19 13:19 | 365 | Remove | 2025-05-19 | 13:19 | ST | GS | - | 13.5 | g | 0 | 111.4 | 11.79 | 1168.2 | 53803 | 3:02 | 29.5 | 2.41 m/s | 27.6 | 31.3 | 4.66 m/s | 21.1 |  | 2.41 | m/s |  | 4.66 | m/s | 3.04 | 0.009735 | 3.4516 |  | 2.5 | 13.5 | 0.0135 | 255.6734 | 8.1533 | 6.8701 | 0.028903 | 11.7204 | 0.11518
2025-05-19 13:20 | 366 | Remove | 2025-05-19 | 13:20 | US | GS | - | 15.5 | g | 0 | 111.6 | 11.743 | 1163.8 | 53813 | 3:03 | 29.6 | 2.18 m/s | 28.8 | 31.3 | 3.84 m/s | 21.2 |  | 2.18 | m/s |  | 3.84 | m/s | 3.0483 | 0.0096983 | 3.4613 |  | 2 | 15.5 | 0.0155 | 223.309 | 8.5542 | 6.9027 | 0.027431 | 11.7478 | 0.13194
2025-05-19 13:20 | 367 | Remove | 2025-05-19 | 13:20 | ST | GS | - | 13.5 | g | 0 | 111.5 | 11.723 | 1160.6 | 53823 | 3:03 | 29.6 | 2.72 m/s | 30.6 | 31.3 | 3.86 m/s | 21 |  | 2.72 | m/s |  | 3.86 | m/s | 3.0567 | 0.0096717 | 3.471 |  | -2 | 13.5 | 0.0135 | 257.1082 | 9.0888 | 6.8375 | 0.036364 | 11.7842 | 0.11456
2025-05-19 13:21 | 368 | Remove | 2025-05-19 | 13:21 | US | GS | - | 12.5 | g | 0 | 111.5 | 11.732 | 1160.9 | 53833 | 3:04 | 29.6 | 2.49 m/s | 29.5 | 31.3 | 3.93 m/s | 20.1 |  | 2.49 | m/s |  | 3.93 | m/s | 3.065 | 0.0096742 | 3.4806 |  | -1 | 12.5 | 0.0125 | 278.4508 | 8.7621 | 6.5445 | 0.032093 | 11.8163 | 0.10579
2025-05-19 13:21 | 369 | Remove | 2025-05-19 | 13:21 | ST | GS | - | 14.5 | g | 0 | 111.6 | 11.739 | 1162.4 | 53842 | 3:04 | 29.5 | 2.77 m/s | 25.3 | 31.2 | 3.86 m/s | 18.4 |  | 2.77 | m/s |  | 3.86 | m/s | 3.0733 | 0.0096867 | 3.4903 |  | 2 | 14.5 | 0.0145 | 240.7118 | 7.4738 | 5.9589 | 0.030453 | 11.8467 | 0.1224
2025-05-19 13:22 | 370 | Remove | 2025-05-19 | 13:22 | ST | GS | - | 13 | g | 0 | 111.7 | 11.731 | 1162.4 | 53852 | 3:05 | 29.5 | 2.35 m/s | 26.9 | 31.2 | 3.96 m/s | 19 |  | 2.35 | m/s |  | 3.96 | m/s | 3.0817 | 0.0096867 | 3.5 |  | -1.5 | 13 | 0.013 | 269.2314 | 7.9465 | 6.1532 | 0.027469 | 11.8742 | 0.10948
2025-05-19 13:22 | 371 | Remove | 2025-05-19 | 13:22 | US | GS | - | 14.5 | g | 0 | 111.7 | 11.722 | 1161.5 | 53862 | 3:05 | 29.5 | 2.55 m/s | 27.2 | 31.2 | 3.92 m/s | 19 |  | 2.55 | m/s |  | 3.92 | m/s | 3.09 | 0.0096792 | 3.5097 |  | 1.5 | 14.5 | 0.0145 | 242.0474 | 8.0351 | 6.1532 | 0.030139 | 11.9044 | 0.1218
2025-05-19 13:23 | 372 | Remove | 2025-05-19 | 13:23 | ST | GS | - | 14 | g | 0 | 111.7 | 11.722 | 1160.9 | 53872 | 3:06 | 29.5 | 2.62 m/s | 26.3 | 31.2 | 4.04 m/s | 19.2 |  | 2.62 | m/s |  | 4.04 | m/s | 3.0983 | 0.0096742 | 3.5194 |  | -0.5 | 14 | 0.014 | 251.383 | 7.7692 | 6.218 | 0.029942 | 11.9343 | 0.11731
2025-05-19 13:23 | 373 | Remove | 2025-05-19 | 13:23 | ST | GS | - | 16 | g | 0 | 111.8 | 11.745 | 1164.7 | 53881 | 3:06 | 29.5 | 2.22 m/s | 26.3 | 31.2 | 3.93 m/s | 19.6 |  | 2.22 | m/s |  | 3.93 | m/s | 3.1067 | 0.0097058 | 3.5291 |  | 2 | 16 | 0.016 | 220.5667 | 7.7692 | 6.3475 | 0.025371 | 11.9597 | 0.13378
2025-05-19 13:24 | 374 | Remove | 2025-05-19 | 13:24 | US | GS | - | 16 | g | 0 | 111.7 | 11.757 | 1165.5 | 53891 | 3:07 | 29.5 | 2.38 m/s | 27 | 31.2 | 3.84 m/s | 19.3 |  | 2.38 | m/s |  | 3.84 | m/s | 3.115 | 0.0097125 | 3.5388 |  | 0 | 16 | 0.016 | 221.1737 | 7.976 | 6.2504 | 0.027923 | 11.9876 | 0.13347
2025-05-19 13:24 | 375 | Remove | 2025-05-19 | 13:24 | US | GS | - | 9.5 | g | 0 | 111.6 | 11.767 | 1166.4 | 53901 | 3:07 | 29.5 | 2.16 m/s | 29.2 | 31.3 | 3.77 m/s | 20.3 |  | 2.16 | m/s |  | 3.77 | m/s | 3.1233 | 0.00972 | 3.5485 |  | -6.5 | 9.5 | 0.0095 | 373.5263 | 8.6259 | 6.6096 | 0.027407 | 12.015 | 0.079068
2025-05-19 13:25 | 376 | Remove | 2025-05-19 | 13:25 | ST | GS | - | 11.5 | g | 0 | 111.7 | 11.777 | 1167.3 | 53910 | 3:08 | 29.6 | 2.22 m/s | 28.4 | 31.3 | 4.09 m/s | 21 |  | 2.22 | m/s |  | 4.09 | m/s | 3.1317 | 0.0097275 | 3.5582 |  | 2 | 11.5 | 0.0115 | 309.4111 | 8.4353 | 6.8375 | 0.027546 | 12.0425 | 0.095495
2025-05-19 13:25 | 377 | Remove | 2025-05-19 | 13:25 | ST | GS | - | 14.5 | g | 0 | 111.8 | 11.786 | 1168.7 | 53920 | 3:08 | 29.6 | 2.51 m/s | 28.1 | 31.3 | 3.88 m/s | 19.1 |  | 2.51 | m/s |  | 3.88 | m/s | 3.14 | 0.0097392 | 3.568 |  | 3 | 14.5 | 0.0145 | 246.0667 | 8.3462 | 6.2189 | 0.030815 | 12.0734 | 0.1201
2025-05-19 13:26 | 378 | Remove | 2025-05-19 | 13:26 | US | GS | - | 12 | g | 0 | 111.7 | 11.803 | 1170.5 | 53930 | 3:09 | 29.6 | 2.38 m/s | 25.8 | 31.3 | 3.69 m/s | 18.4 |  | 2.38 | m/s |  | 3.69 | m/s | 3.1483 | 0.0097542 | 3.5777 |  | -2.5 | 12 | 0.012 | 298.1434 | 7.6631 | 5.991 | 0.026828 | 12.1002 | 0.099172
2025-05-19 13:26 | 379 | Remove | 2025-05-19 | 13:26 | ST | GS | - | 16 | g | 0 | 111.6 | 11.818 | 1172.1 | 53940 | 3:09 | 29.6 | 2.58 m/s | 26.8 | 31.3 | 4.01 m/s | 19.1 |  | 2.58 | m/s |  | 4.01 | m/s | 3.1567 | 0.0097675 | 3.5875 |  | 4 | 16 | 0.016 | 224.218 | 7.9601 | 6.2189 | 0.030209 | 12.1304 | 0.1319
2025-05-19 13:27 | 380 | Remove | 2025-05-19 | 13:27 | US | GS | - | 14.5 | g | 0 | 111.6 | 11.809 | 1170.9 | 53950 | 3:10 | 29.6 | 2.62 m/s | 26.2 | 31.3 | 3.94 m/s | 19.8 |  | 2.62 | m/s |  | 3.94 | m/s | 3.1653 | 0.0097575 | 3.5972 |  | -1.5 | 14.5 | 0.0145 | 248.0859 | 7.7819 | 6.4468 | 0.029991 | 12.1604 | 0.11924
2025-05-19 13:27 | 381 | Remove | 2025-05-19 | 13:27 | ST | GS | - | 19.5 | g | 0 | 111.6 | 11.817 | 1172.3 | 53959 | 3:10 | 29.6 | 2.42 m/s | 28.1 | 31.4 | 4.26 m/s | 20.7 |  | 2.42 | m/s |  | 4.26 | m/s | 3.1736 | 0.0097692 | 3.607 |  | 5 | 19.5 | 0.0195 | 184.9751 | 8.3462 | 6.7761 | 0.02971 | 12.1901 | 0.15997
2025-05-19 13:28 | 382 | Remove | 2025-05-19 | 13:28 | US | GS | - | 15.5 | g | 0 | 111.6 | 11.807 | 1170.9 | 53969 | 3:11 | 29.6 | 2.19 m/s | 29.6 | 31.4 | 3.85 m/s | 21.6 |  | 2.19 | m/s |  | 3.85 | m/s | 3.1819 | 0.0097575 | 3.6168 |  | -4 | 15.5 | 0.0155 | 233.3402 | 8.7918 | 7.0708 | 0.028322 | 12.2184 | 0.12686
2025-05-19 13:28 | 383 | Remove | 2025-05-19 | 13:28 | ST | GS | - | 12.5 | g | 0 | 111.5 | 11.833 | 1173.3 | 53979 | 3:11 | 29.7 | 2.38 m/s | 28.2 | 31.4 | 4.04 m/s | 20.4 |  | 2.38 | m/s |  | 4.04 | m/s | 3.1903 | 0.0097775 | 3.6265 |  | -3 | 12.5 | 0.0125 | 290.124 | 8.4216 | 6.6779 | 0.029483 | 12.2479 | 0.10206
2025-05-19 13:29 | 384 | Remove | 2025-05-19 | 13:29 | ST | GS | - | 13.5 | g | 0 | 111.5 | 11.799 | 1169.8 | 53989 | 3:12 | 29.6 | 2.06 m/s | 27.7 | 31.4 | 4.15 m/s | 19.1 |  | 2.06 | m/s |  | 4.15 | m/s | 3.1986 | 0.0097483 | 3.6363 |  | 1 | 13.5 | 0.0135 | 269.3554 | 8.2274 | 6.2524 | 0.024931 | 12.2728 | 0.11
2025-05-19 13:29 | 385 | Remove | 2025-05-19 | 13:29 | ST | GS | - | 13 | g | 0 | 111.5 | 11.852 | 1176.1 | 53999 | 3:12 | 29.6 | 2.09 m/s | 26.8 | 31.5 | 4.15 m/s | 18.8 |  | 2.09 | m/s |  | 4.15 | m/s | 3.2069 | 0.0098008 | 3.6461 |  | -0.5 | 13 | 0.013 | 280.4692 | 7.9601 | 6.1873 | 0.024472 | 12.2973 | 0.10571
2025-05-19 13:30 | 386 | Remove | 2025-05-19 | 13:30 | ST | GS | - | 14.5 | g | 0 | 111.7 | 11.783 | 1168.8 | 54008 | 3:13 | 29.7 | 2.35 m/s | 23.9 | 31.5 | 4.04 m/s | 18.3 |  | 2.35 | m/s |  | 4.04 | m/s | 3.2153 | 0.00974 | 3.6558 |  | 1.5 | 14.5 | 0.0145 | 252.1268 | 7.1375 | 6.0227 | 0.024673 | 12.322 | 0.11768
2025-05-19 13:30 | 387 | Remove | 2025-05-19 | 13:30 | US | GS | - | 17.5 | g | 0 | 111.5 | 11.833 | 1173.5 | 54018 | 3:13 | 29.7 | 2.34 m/s | 25.2 | 31.5 | 4.09 m/s | 17.6 |  | 2.34 | m/s |  | 4.09 | m/s | 3.2236 | 0.0097792 | 3.6656 |  | 3 | 17.5 | 0.0175 | 209.4639 | 7.5257 | 5.7923 | 0.025904 | 12.3479 | 0.14172
2025-05-19 13:31 | 388 | Remove | 2025-05-19 | 13:31 | US | GS | - | 17.5 | g | 0 | 111.5 | 11.782 | 1168.5 | 54028 | 3:14 | 29.7 | 2.72 m/s | 24.7 | 31.5 | 4.23 m/s | 18 |  | 2.72 | m/s |  | 4.23 | m/s | 3.2319 | 0.0097375 | 3.6754 |  | 0 | 17.5 | 0.0175 | 210.0203 | 7.3764 | 5.924 | 0.029513 | 12.3774 | 0.14139
2025-05-19 13:31 | 389 | Remove | 2025-05-19 | 13:31 | ST | GS | - | 15.5 | g | 0 | 111.5 | 11.831 | 1173.5 | 54038 | 3:14 | 29.7 | 2.12 m/s | 25.4 | 31.5 | 3.89 m/s | 18.3 |  | 2.12 | m/s |  | 3.89 | m/s | 3.2403 | 0.0097792 | 3.6851 |  | -2 | 15.5 | 0.0155 | 237.7506 | 7.5854 | 6.0227 | 0.023655 | 12.401 | 0.12499
2025-05-19 13:32 | 390 | Remove | 2025-05-19 | 13:32 | US | GS | - | 15 | g | 0 | 111.7 | 11.836 | 1175 | 54048 | 3:15 | 29.7 | 2.3 m/s | 27.1 | 31.5 | 3.72 m/s | 19.6 |  | 2.3 | m/s |  | 3.72 | m/s | 3.2486 | 0.0097917 | 3.6949 |  | -0.5 | 15 | 0.015 | 246.3284 | 8.0931 | 6.4506 | 0.027381 | 12.4284 | 0.12069
2025-05-19 13:32 | 391 | Keep | 2025-05-19 | 13:32 | US | GS | - | 13.5 | g | 0 | 111.6 | 11.831 | 1174.6 | 54057 | 3:15 | 29.7 | 2.45 m/s | 24.6 | 31.5 | 4.03 m/s | 17.9 |  | 2.45 | m/s |  | 4.03 | m/s | 3.2569 | 0.0097883 | 3.7047 |  | -1.5 | 13.5 | 0.0135 | 274.4233 | 7.3465 | 5.8911 | 0.026476 | 12.4549 | 0.10839
2025-05-19 13:33 | 392 | Remove | 2025-05-19 | 13:33 | ST | GS | - | 14.5 | g | 0 | 111.6 | 11.875 | 1179.2 | 54067 | 3:16 | 29.7 | 2.18 m/s | 25 | 31.5 | 4.2 m/s | 18.6 |  | 2.18 | m/s |  | 4.2 | m/s | 3.2653 | 0.0098267 | 3.7145 |  | 1 | 14.5 | 0.0145 | 256.1753 | 7.466 | 6.1214 | 0.023941 | 12.4788 | 0.1162
2025-05-19 13:33 | 393 | Remove | 2025-05-19 | 13:33 | US | GS | - | 17.5 | g | 0 | 111.6 | 11.8 | 1170.6 | 54077 | 3:16 | 29.7 | 2.81 m/s | 26.7 | 31.5 | 4.2 m/s | 18.6 |  | 2.81 | m/s |  | 4.2 | m/s | 3.2736 | 0.009755 | 3.7243 |  | 3 | 17.5 | 0.0175 | 212.817 | 7.9736 | 6.1214 | 0.032958 | 12.5118 | 0.13987
2025-05-19 13:34 | 394 | Remove | 2025-05-19 | 13:34 | ST | GS | - | 12 | g | 0 | 111.7 | 11.826 | 1174.3 | 54087 | 3:17 | 29.7 | 2.35 m/s | 25.1 | 31.5 | 3.65 m/s | 18.7 |  | 2.35 | m/s |  | 3.65 | m/s | 3.2819 | 0.0097858 | 3.7341 |  | -5.5 | 12 | 0.012 | 311.1735 | 7.4958 | 6.1544 | 0.025911 | 12.5377 | 0.095711
2025-05-19 13:34 | 395 | Remove | 2025-05-19 | 13:34 | ST | GS | - | 12.5 | g | 0 | 111.6 | 11.88 | 1180.1 | 54097 | 3:17 | 29.7 | 2.38 m/s | 25.8 | 31.5 | 3.93 m/s | 18.3 |  | 2.38 | m/s |  | 3.93 | m/s | 3.2903 | 0.0098342 | 3.7439 |  | 0.5 | 12.5 | 0.0125 | 299.5133 | 7.7049 | 6.0227 | 0.026974 | 12.5647 | 0.099485
2025-05-19 13:35 | 396 | Remove | 2025-05-19 | 13:35 | ST | GS | - | 14 | g | 0 | 111.6 | 11.855 | 1177.5 | 54107 | 3:18 | 29.7 | 2.23 m/s | 27 | 31.5 | 4.15 m/s | 18.7 |  | 2.23 | m/s |  | 4.15 | m/s | 3.2986 | 0.0098125 | 3.7537 |  | 1.5 | 14 | 0.014 | 268.1235 | 8.0632 | 6.1544 | 0.026449 | 12.5911 | 0.11119
2025-05-19 13:35 | 397 | Remove | 2025-05-19 | 13:35 | US | GS | - | 24.5 | g | 0 | 111.7 | 11.825 | 1174.2 | 54116 | 3:18 | 29.7 | 2.2 m/s | 25.8 | 31.5 | 3.81 m/s | 18.6 |  | 2.2 | m/s |  | 3.81 | m/s | 3.3072 | 0.009785 | 3.7635 |  | 10.5 | 24.5 | 0.0245 | 153.6128 | 7.7049 | 6.1214 | 0.024934 | 12.6161 | 0.1942
2025-05-19 13:36 | 398 | Remove | 2025-05-19 | 13:36 | US | GS | - | 12 | g | 0 | 111.7 | 11.78 | 1169 | 54126 | 3:19 | 29.7 | 2.51 m/s | 25.7 | 31.5 | 3.77 m/s | 18.7 |  | 2.51 | m/s |  | 3.77 | m/s | 3.3156 | 0.0097417 | 3.7733 |  | -12.5 | 12 | 0.012 | 314.438 | 7.675 | 6.1544 | 0.028337 | 12.6444 | 0.094904
2025-05-19 13:36 | 399 | Remove | 2025-05-19 | 13:36 | ST | GS | - | 14.5 | g | 0 | 111.7 | 11.797 | 1171 | 54136 | 3:19 | 29.7 | 2.5 m/s | 25.3 | 31.4 | 4.43 m/s | 19.5 |  | 2.5 | m/s |  | 4.43 | m/s | 3.3239 | 0.0097583 | 3.783 |  | 2.5 | 14.5 | 0.0145 | 260.8975 | 7.5556 | 6.3833 | 0.027785 | 12.6722 | 0.11442
2025-05-19 13:37 | 400 | Remove | 2025-05-19 | 13:37 | ST | GS | - | 17 | g | 0 | 111.6 | 11.834 | 1174.6 | 54146 | 3:20 | 29.7 | 2.57 m/s | 26.1 | 31.4 | 4.43 m/s | 19.5 |  | 2.57 | m/s |  | 4.43 | m/s | 3.3322 | 0.0097883 | 3.7928 |  | 2.5 | 17 | 0.017 | 223.106 | 7.7945 | 6.3833 | 0.029466 | 12.7017 | 0.13384
2025-05-19 13:37 | 401 | Remove | 2025-05-19 | 13:37 | ST | GS | - | 14 | g | 0 | 111.7 | 11.817 | 1172.8 | 54155 | 3:20 | 29.7 | 2.3 m/s | 25.6 | 31.4 | 3.89 m/s | 20 |  | 2.3 | m/s |  | 3.89 | m/s | 3.3406 | 0.0097733 | 3.8026 |  | -3 | 14 | 0.014 | 271.6126 | 7.6451 | 6.547 | 0.025865 | 12.7275 | 0.11
2025-05-19 13:38 | 402 | Remove | 2025-05-19 | 13:38 | ST | GS | - | 17.5 | g | 0 | 111.6 | 11.825 | 1173.5 | 54165 | 3:21 | 29.7 | 2.71 m/s | 25.8 | 31.4 | 4.21 m/s | 19.8 |  | 2.71 | m/s |  | 4.21 | m/s | 3.3489 | 0.0097792 | 3.8124 |  | 3.5 | 17.5 | 0.0175 | 217.8489 | 7.7049 | 6.4815 | 0.030714 | 12.7582 | 0.13717
2025-05-19 13:38 | 403 | Remove | 2025-05-19 | 13:38 | ST | GS | - | 16 | g | 0 | 111.6 | 11.833 | 1174.7 | 54175 | 3:21 | 29.7 | 2.7 m/s | 25.6 | 31.4 | 3.92 m/s | 18.2 |  | 2.7 | m/s |  | 3.92 | m/s | 3.3572 | 0.0097892 | 3.8221 |  | -1.5 | 16 | 0.016 | 238.884 | 7.6451 | 5.9578 | 0.030363 | 12.7886 | 0.12511
2025-05-19 13:39 | 404 | Remove | 2025-05-19 | 13:39 | ST | GS | - | 14.5 | g | 0 | 111.7 | 11.807 | 1171.7 | 54185 | 3:22 | 29.7 | 2.57 m/s | 26.6 | 31.4 | 3.81 m/s | 18 |  | 2.57 | m/s |  | 3.81 | m/s | 3.3656 | 0.0097642 | 3.8319 |  | -1.5 | 14.5 | 0.0145 | 264.2695 | 7.9438 | 5.8923 | 0.030031 | 12.8186 | 0.11312
2025-05-19 13:39 | 405 | Remove | 2025-05-19 | 13:39 | ST | GS | - | 15 | g | 0 | 111.7 | 11.798 | 1170.9 | 54195 | 3:22 | 29.7 | 2.26 m/s | 28.7 | 31.4 | 4.01 m/s | 18.1 |  | 2.26 | m/s |  | 4.01 | m/s | 3.3739 | 0.0097575 | 3.8417 |  | 0.5 | 15 | 0.015 | 256.1111 | 8.5709 | 5.925 | 0.028493 | 12.8471 | 0.11676
2025-05-19 13:40 | 406 | Remove | 2025-05-19 | 13:40 | ST | GS | - | 16 | g | 0 | 111.6 | 11.844 | 1175.8 | 54205 | 3:23 | 29.7 | 2.42 m/s | 25.4 | 31.4 | 3.84 m/s | 20.5 |  | 2.42 | m/s |  | 3.84 | m/s | 3.3822 | 0.0097983 | 3.8515 |  | 1 | 16 | 0.016 | 240.7165 | 7.5854 | 6.7107 | 0.027002 | 12.8741 | 0.12428
2025-05-19 13:40 | 407 | Remove | 2025-05-19 | 13:40 | US | GS | - | 21.5 | g | 0 | 111.5 | 11.844 | 1175.2 | 54214 | 3:23 | 29.7 | 2.45 m/s | 25.6 | 31.4 | 3.88 m/s | 18 |  | 2.45 | m/s |  | 3.88 | m/s | 3.3906 | 0.0097933 | 3.8613 |  | 5.5 | 21.5 | 0.0215 | 179.5934 | 7.6451 | 5.8923 | 0.027552 | 12.9017 | 0.16664
2025-05-19 13:41 | 408 | Remove | 2025-05-19 | 13:41 | US | GS | - | 16.5 | g | 0 | 111.4 | 11.846 | 1174.6 | 54224 | 3:24 | 29.7 | 2.31 m/s | 27.3 | 31.4 | 3.52 m/s | 19.8 |  | 2.31 | m/s |  | 3.52 | m/s | 3.3989 | 0.0097883 | 3.871 |  | -5 | 16.5 | 0.0165 | 234.6088 | 8.1528 | 6.4815 | 0.027703 | 12.9294 | 0.12762
2025-05-19 13:41 | 409 | Remove | 2025-05-19 | 13:41 | ST | GS | - | 20.5 | g | 0 | 111.6 | 11.842 | 1175.6 | 54234 | 3:24 | 29.7 | 2.08 m/s | 25.3 | 31.4 | 3.85 m/s | 18.7 |  | 2.08 | m/s |  | 3.85 | m/s | 3.4072 | 0.0097967 | 3.8808 |  | 4 | 20.5 | 0.0205 | 189.3094 | 7.5556 | 6.1214 | 0.023117 | 12.9525 | 0.15827
2025-05-19 13:42 | 410 | Remove | 2025-05-19 | 13:42 | US | GS | - | 16 | g | 0 | 111.6 | 11.818 | 1172.4 | 54244 | 3:25 | 29.7 | 2.48 m/s | 27.5 | 31.4 | 4.72 m/s | 18.5 |  | 2.48 | m/s |  | 4.72 | m/s | 3.4156 | 0.00977 | 3.8906 |  | -4.5 | 16 | 0.016 | 243.1633 | 8.2126 | 6.056 | 0.029959 | 12.9825 | 0.12324
2025-05-19 13:42 | 411 | Remove | 2025-05-19 | 13:42 | US | GS | - | 15 | g | 0 | 111.6 | 11.826 | 1173.5 | 54254 | 3:25 | 29.7 | 2.75 m/s | 26.2 | 31.4 | 3.96 m/s | 18.5 |  | 2.75 | m/s |  | 3.96 | m/s | 3.4239 | 0.0097792 | 3.9004 |  | -1 | 15 | 0.015 | 260.0261 | 7.8243 | 6.056 | 0.031651 | 13.0141 | 0.11526
2025-05-19 13:43 | 412 | Remove | 2025-05-19 | 13:43 | US | GS | - | 13 | g | 0 | 111.6 | 11.826 | 1173.4 | 54263 | 3:26 | 29.7 | 2.77 m/s | 26.2 | 31.4 | 3.77 m/s | 17.5 |  | 2.77 | m/s |  | 3.77 | m/s | 3.4322 | 0.0097783 | 3.9102 |  | -2 | 13 | 0.013 | 300.7823 | 7.8243 | 5.7286 | 0.031881 | 13.046 | 0.099647
2025-05-19 13:43 | 413 | Remove | 2025-05-19 | 13:43 | ST | GS | - | 18 | g | 0 | 111.6 | 11.819 | 1172.2 | 54273 | 3:26 | 29.7 | 2.45 m/s | 24.7 | 31.4 | 3.85 m/s | 18.1 |  | 2.45 | m/s |  | 3.85 | m/s | 3.4406 | 0.0097683 | 3.9199 |  | 5 | 18 | 0.018 | 217.7744 | 7.3764 | 5.925 | 0.026583 | 13.0726 | 0.13769
2025-05-19 13:44 | 414 | Remove | 2025-05-19 | 13:44 | US | GS | - | 27.5 | g | 0 | 111.6 | 11.837 | 1174.8 | 54283 | 3:27 | 29.7 | 2.44 m/s | 27.4 | 31.4 | 3.86 m/s | 18.9 |  | 2.44 | m/s |  | 3.86 | m/s | 3.4492 | 0.00979 | 3.9297 |  | 9.5 | 27.5 | 0.0275 | 142.8992 | 8.1827 | 6.1869 | 0.029369 | 13.1019 | 0.20989
2025-05-19 13:44 | 415 | Remove | 2025-05-19 | 13:44 | US | GS | - | 14.5 | g | 0 | 111.6 | 11.862 | 1177.7 | 54293 | 3:27 | 29.7 | 3.1 m/s | 23.2 | 31.4 | 4.5 m/s | 18.8 |  | 3.1 | m/s |  | 4.5 | m/s | 3.4575 | 0.0098142 | 3.9395 |  | -13 | 14.5 | 0.0145 | 271.6926 | 6.9284 | 6.1542 | 0.031593 | 13.1335 | 0.1104
2025-05-19 13:45 | 416 | Remove | 2025-05-19 | 13:45 | US | GS | - | 15 | g | 0 | 111.6 | 11.83 | 1173.9 | 54303 | 3:28 | 29.7 | 2.81 m/s | 23.3 | 31.4 | 3.76 m/s | 17.2 |  | 2.81 | m/s |  | 3.76 | m/s | 3.4658 | 0.0097825 | 3.9493 |  | 0.5 | 15 | 0.015 | 263.2883 | 6.9583 | 5.6304 | 0.028761 | 13.1623 | 0.11396
2025-05-19 13:45 | 417 | Remove | 2025-05-19 | 13:45 | ST | GS | - | 15.5 | g | 0 | 111.7 | 11.808 | 1171.2 | 54313 | 3:28 | 29.7 | 2.75 m/s | 22.5 | 31.3 | 3.69 m/s | 16.6 |  | 2.75 | m/s |  | 3.69 | m/s | 3.4742 | 0.00976 | 3.9591 |  | 0.5 | 15.5 | 0.0155 | 255.4248 | 6.7194 | 5.4049 | 0.027181 | 13.1895 | 0.11752
2025-05-19 13:46 | 418 | Remove | 2025-05-19 | 13:46 | US | GS | - | 15 | g | 0 | 111.6 | 11.842 | 1175.3 | 54322 | 3:29 | 29.7 | 2.5 m/s | 23.4 | 31.4 | 3.97 m/s | 17.3 |  | 2.5 | m/s |  | 3.97 | m/s | 3.4825 | 0.0097942 | 3.9689 |  | -0.5 | 15 | 0.015 | 264.5919 | 6.9881 | 5.6631 | 0.025698 | 13.2152 | 0.11351
2025-05-19 13:46 | 419 | Remove | 2025-05-19 | 13:46 | US | GS | - | 10 | g | 0 | 111.5 | 11.823 | 1172.4 | 54332 | 3:29 | 29.7 | 2.08 m/s | 24.8 | 31.4 | 3.96 m/s | 17.4 |  | 2.08 | m/s |  | 3.96 | m/s | 3.4908 | 0.00977 | 3.9786 |  | -5 | 10 | 0.01 | 397.8649 | 7.4062 | 5.6959 | 0.02266 | 13.2378 | 0.075541
2025-05-19 13:47 | 420 | Remove | 2025-05-19 | 13:47 | ST | GS | - | 15.5 | g | 0 | 111.6 | 11.844 | 1175.1 | 54342 | 3:30 | 29.7 | 2.44 m/s | 24.4 | 31.4 | 4.13 m/s | 18.4 |  | 2.44 | m/s |  | 4.13 | m/s | 3.4992 | 0.0097925 | 3.9884 |  | 5.5 | 15.5 | 0.0155 | 257.3188 | 7.2868 | 6.0232 | 0.026153 | 13.264 | 0.11686
2025-05-19 13:47 | 421 | Keep | 2025-05-19 | 13:47 | US | GS | - | 14 | g | 0 | 111.7 | 11.832 | 1174.9 | 54352 | 3:30 | 29.7 | 2.67 m/s | 23.4 | 31.4 | 4.23 m/s | 18 |  | 2.67 | m/s |  | 4.23 | m/s | 3.5075 | 0.0097908 | 3.9982 |  | -1.5 | 14 | 0.014 | 285.588 | 6.9881 | 5.8923 | 0.027446 | 13.2914 | 0.10533
2025-05-19 13:48 | 422 | Remove | 2025-05-19 | 13:48 | US | GS | - | 18.5 | g | 0 | 111.6 | 11.832 | 1174.1 | 54362 | 3:31 | 29.7 | 2.57 m/s | 25.2 | 31.4 | 4.06 m/s | 18.1 |  | 2.57 | m/s |  | 4.06 | m/s | 3.5158 | 0.0097842 | 4.008 |  | 4.5 | 18.5 | 0.0185 | 216.6495 | 7.5257 | 5.925 | 0.02845 | 13.3199 | 0.13889
2025-05-19 13:48 | 423 | Remove | 2025-05-19 | 13:48 | US | GS | - | 13 | g | 0 | 111.8 | 11.818 | 1172.7 | 54371 | 3:31 | 29.7 | 2.4 m/s | 29.5 | 31.4 | 3.94 m/s | 20 |  | 2.4 | m/s |  | 3.94 | m/s | 3.5242 | 0.0097725 | 4.0178 |  | -5.5 | 13 | 0.013 | 309.0607 | 8.8098 | 6.547 | 0.031101 | 13.351 | 0.097371
2025-05-19 13:49 | 424 | Remove | 2025-05-19 | 13:49 | US | GS | - | 17.5 | g | 0 | 111.7 | 11.831 | 1174 | 54381 | 3:32 | 29.7 | 2.47 m/s | 22.7 | 31.4 | 3.75 m/s | 20 |  | 2.47 | m/s |  | 3.75 | m/s | 3.5325 | 0.0097833 | 4.0276 |  | 4.5 | 17.5 | 0.0175 | 230.147 | 6.7791 | 6.547 | 0.02463 | 13.3756 | 0.13084
2025-05-19 13:49 | 425 | Remove | 2025-05-19 | 13:49 | US | GS | - | 15 | g | 0 | 111.8 | 11.812 | 1171.9 | 54391 | 3:32 | 29.7 | 2.71 m/s | 23.8 | 31.4 | 3.72 m/s | 16.6 |  | 2.71 | m/s |  | 3.72 | m/s | 3.5408 | 0.0097658 | 4.0373 |  | -2.5 | 15 | 0.015 | 269.1559 | 7.1076 | 5.434 | 0.028333 | 13.4039 | 0.11191
2025-05-19 13:50 | 426 | Remove | 2025-05-19 | 13:50 | ST | GS | - | 16 | g | 0 | 111.8 | 11.854 | 1177.3 | 54401 | 3:33 | 29.8 | 2.13 m/s | 24.8 | 31.4 | 3.79 m/s | 17.9 |  | 2.13 | m/s |  | 3.79 | m/s | 3.5492 | 0.0098108 | 4.0471 |  | 1 | 16 | 0.016 | 252.9468 | 7.4466 | 5.8596 | 0.023331 | 13.4273 | 0.11916
2025-05-19 13:50 | 427 | Remove | 2025-05-19 | 13:50 | US | GS | - | 23.5 | g | 0 | 111.6 | 11.855 | 1176.5 | 54411 | 3:33 | 29.8 | 2.37 m/s | 23.5 | 31.4 | 3.86 m/s | 17.8 |  | 2.37 | m/s |  | 3.86 | m/s | 3.5575 | 0.0098042 | 4.057 |  | 7.5 | 23.5 | 0.0235 | 172.6363 | 7.0562 | 5.8268 | 0.024599 | 13.4519 | 0.1747
2025-05-19 13:51 | 428 | Remove | 2025-05-19 | 13:51 | US | GS | - | 18 | g | 0 | 111.7 | 11.858 | 1177.1 | 54420 | 3:34 | 29.8 | 2.51 m/s | 23.8 | 31.4 | 4.16 m/s | 18.6 |  | 2.51 | m/s |  | 4.16 | m/s | 3.5658 | 0.0098092 | 4.0668 |  | -5.5 | 18 | 0.018 | 225.9313 | 7.1463 | 6.0887 | 0.026385 | 13.4783 | 0.13355
2025-05-19 13:51 | 429 | Remove | 2025-05-19 | 13:51 | ST | GS | - | 17 | g | 0 | 111.6 | 11.83 | 1173.4 | 54430 | 3:34 | 29.8 | 2.08 m/s | 22.5 | 31.4 | 3.81 m/s | 17.8 |  | 2.08 | m/s |  | 3.81 | m/s | 3.5742 | 0.0097783 | 4.0765 |  | -1 | 17 | 0.017 | 239.7965 | 6.756 | 5.8268 | 0.020671 | 13.4989 | 0.12594
2025-05-19 13:52 | 430 | Remove | 2025-05-19 | 13:52 | US | GS | - | 18 | g | 0 | 111.6 | 11.845 | 1175.6 | 54440 | 3:35 | 29.7 | 2.3 m/s | 22 | 31.4 | 3.73 m/s | 17.1 |  | 2.3 | m/s |  | 3.73 | m/s | 3.5828 | 0.0097967 | 4.0863 |  | 1 | 18 | 0.018 | 227.0188 | 6.57 | 5.5977 | 0.022228 | 13.5212 | 0.13312
2025-05-19 13:52 | 431 | Remove | 2025-05-19 | 13:52 | ST | GS | - | 17 | g | 0 | 111.5 | 11.887 | 1180.1 | 54450 | 3:35 | 29.8 | 2.37 m/s | 23 | 31.4 | 4.04 m/s | 16.4 |  | 2.37 | m/s |  | 4.04 | m/s | 3.5911 | 0.0098342 | 4.0962 |  | -1 | 17 | 0.017 | 240.9513 | 6.9061 | 5.3685 | 0.024076 | 13.5452 | 0.12551
2025-05-19 13:53 | 432 | Remove | 2025-05-19 | 13:53 | ST | GS | - | 19 | g | 0 | 111.5 | 11.849 | 1175.5 | 54460 | 3:36 | 29.8 | 2.91 m/s | 23.2 | 31.4 | 3.93 m/s | 16.7 |  | 2.91 | m/s |  | 3.93 | m/s | 3.5994 | 0.0097958 | 4.106 |  | 2 | 19 | 0.019 | 216.1036 | 6.9662 | 5.4667 | 0.029819 | 13.5751 | 0.13996
2025-05-19 13:53 | 433 | Remove | 2025-05-19 | 13:53 | US | GS | - | 20 | g | 0 | 111.6 | 11.849 | 1176.3 | 54470 | 3:36 | 29.8 | 2.54 m/s | 22.7 | 31.4 | 3.76 m/s | 16.7 |  | 2.54 | m/s |  | 3.76 | m/s | 3.6078 | 0.0098025 | 4.1158 |  | 1 | 20 | 0.02 | 205.7885 | 6.816 | 5.4667 | 0.025466 | 13.6005 | 0.14705
2025-05-19 13:54 | 434 | Remove | 2025-05-19 | 13:54 | US | GS | - | 23 | g | 0 | 111.6 | 11.903 | 1182.8 | 54480 | 3:37 | 29.8 | 2.84 m/s | 23.1 | 31.4 | 3.79 m/s | 17.2 |  | 2.84 | m/s |  | 3.79 | m/s | 3.6161 | 0.0098567 | 4.1256 |  | 3 | 23 | 0.023 | 179.3751 | 6.9361 | 5.6304 | 0.028976 | 13.6295 | 0.16875
2025-05-19 13:54 | 435 | Remove | 2025-05-19 | 13:54 | ST | GS | - | 17.5 | g | 0 | 111.6 | 11.907 | 1183.1 | 54489 | 3:37 | 29.8 | 2.94 m/s | 22.5 | 31.4 | 3.84 m/s | 17.4 |  | 2.94 | m/s |  | 3.84 | m/s | 3.6244 | 0.0098592 | 4.1355 |  | -5.5 | 17.5 | 0.0175 | 236.3135 | 6.756 | 5.6959 | 0.029217 | 13.6587 | 0.12812
2025-05-19 13:55 | 436 | Remove | 2025-05-19 | 13:55 | ST | GS | - | 16 | g | 0 | 111.7 | 11.922 | 1185.2 | 54499 | 3:38 | 29.8 | 2.11 m/s | 22.9 | 31.4 | 3.92 m/s | 16.9 |  | 2.11 | m/s |  | 3.92 | m/s | 3.6328 | 0.0098767 | 4.1454 |  | -1.5 | 16 | 0.016 | 259.0852 | 6.8761 | 5.5322 | 0.021342 | 13.6801 | 0.11696
2025-05-19 13:55 | 437 | Remove | 2025-05-19 | 13:55 | ST | GS | - | 16.5 | g | 0 | 111.6 | 11.897 | 1181.7 | 54509 | 3:38 | 29.8 | 2.19 m/s | 23.1 | 31.4 | 4.3 m/s | 17.2 |  | 2.19 | m/s |  | 4.3 | m/s | 3.6411 | 0.0098475 | 4.1552 |  | 0.5 | 16.5 | 0.0165 | 251.8309 | 6.9361 | 5.6304 | 0.022344 | 13.7024 | 0.12042
2025-05-19 13:56 | 438 | Remove | 2025-05-19 | 13:56 | ST | GS | - | 16 | g | 0 | 111.6 | 11.936 | 1186.7 | 54519 | 3:39 | 29.9 | 2.22 m/s | 24 | 31.5 | 4.01 m/s | 16.9 |  | 2.22 | m/s |  | 4.01 | m/s | 3.6494 | 0.0098892 | 4.1651 |  | -0.5 | 16 | 0.016 | 260.3187 | 7.2456 | 5.562 | 0.023661 | 13.7261 | 0.11657
2025-05-19 13:56 | 439 | Remove | 2025-05-19 | 13:56 | ST | GS | - | 18 | g | 0 | 111.7 | 11.887 | 1182 | 54529 | 3:39 | 29.9 | 2.4 m/s | 22.9 | 31.5 | 3.81 m/s | 17.6 |  | 2.4 | m/s |  | 3.81 | m/s | 3.6578 | 0.00985 | 4.1749 |  | 2 | 18 | 0.018 | 231.9416 | 6.9135 | 5.7923 | 0.024407 | 13.7505 | 0.1309
2025-05-19 13:57 | 440 | Remove | 2025-05-19 | 13:57 | ST | GS | - | 18 | g | 0 | 111.7 | 11.9 | 1182.5 | 54539 | 3:40 | 29.8 | 2.18 m/s | 24 | 31.5 | 3.93 m/s | 18.1 |  | 2.18 | m/s |  | 3.93 | m/s | 3.6661 | 0.0098542 | 4.1848 |  | 0 | 18 | 0.018 | 232.4891 | 7.2064 | 5.9569 | 0.023109 | 13.7736 | 0.13068
2025-05-19 13:57 | 441 | Remove | 2025-05-19 | 13:57 | ST | GS | - | 18 | g | 0 | 111.8 | 11.879 | 1180.5 | 54549 | 3:40 | 29.8 | 2.42 m/s | 23.8 | 31.5 | 4.43 m/s | 18.2 |  | 2.42 | m/s |  | 4.43 | m/s | 3.6744 | 0.0098375 | 4.1946 |  | 0 | 18 | 0.018 | 233.0356 | 7.1463 | 5.9898 | 0.025439 | 13.799 | 0.13044
2025-05-19 13:58 | 442 | Remove | 2025-05-19 | 13:58 | US | GS | - | 18 | g | 0 | 111.7 | 11.892 | 1181.9 | 54559 | 3:41 | 29.8 | 2.99 m/s | 24.6 | 31.5 | 3.96 m/s | 17.3 |  | 2.99 | m/s |  | 3.96 | m/s | 3.6828 | 0.0098492 | 4.2045 |  | 0 | 18 | 0.018 | 233.5828 | 7.3865 | 5.6936 | 0.032487 | 13.8315 | 0.13014
2025-05-19 13:58 | 443 | Remove | 2025-05-19 | 13:58 | ST | GS | - | 18.5 | g | 0 | 111.7 | 11.836 | 1174.8 | 54568 | 3:41 | 29.8 | 2.64 m/s | 23.6 | 31.5 | 3.85 m/s | 16.6 |  | 2.64 | m/s |  | 3.85 | m/s | 3.6911 | 0.00979 | 4.2143 |  | 0.5 | 18.5 | 0.0185 | 227.7989 | 7.0863 | 5.4632 | 0.027518 | 13.859 | 0.13349
2025-05-19 13:59 | 444 | Remove | 2025-05-19 | 13:59 | ST | GS | - | 18 | g | 0 | 111.9 | 11.831 | 1174.7 | 54578 | 3:42 | 29.8 | 2.37 m/s | 23.7 | 31.5 | 4.15 m/s | 18.8 |  | 2.37 | m/s |  | 4.15 | m/s | 3.6994 | 0.0097892 | 4.2241 |  | -0.5 | 18 | 0.018 | 234.6705 | 7.1163 | 6.1873 | 0.024809 | 13.8838 | 0.12965
2025-05-19 13:59 | 445 | Remove | 2025-05-19 | 13:59 | ST | GS | - | 19 | g | 0 | 111.9 | 11.823 | 1174.5 | 54588 | 3:42 | 29.8 | 2.31 m/s | 22.2 | 31.5 | 3.98 m/s | 16.6 |  | 2.31 | m/s |  | 3.98 | m/s | 3.7078 | 0.0097875 | 4.2339 |  | 1 | 19 | 0.019 | 222.8346 | 6.6659 | 5.4632 | 0.02265 | 13.9065 | 0.13663
2025-05-19 14:00 | 446 | Remove | 2025-05-19 | 14:00 | ST | GS | - | 17.5 | g | 0 | 111.8 | 11.849 | 1177.2 | 54598 | 3:43 | 29.8 | 2.13 m/s | 22.5 | 31.5 | 4.15 m/s | 16.4 |  | 2.13 | m/s |  | 4.15 | m/s | 3.7161 | 0.00981 | 4.2437 |  | -1.5 | 17.5 | 0.0175 | 242.4952 | 6.756 | 5.3974 | 0.021167 | 13.9276 | 0.12565
2025-05-19 14:00 | 447 | Remove | 2025-05-19 | 14:00 | ST | GS | - | 18 | g | 0 | 111.9 | 11.857 | 1177.9 | 54608 | 3:43 | 29.8 | 2.16 m/s | 23.8 | 31.5 | 3.93 m/s | 16.5 |  | 2.16 | m/s |  | 3.93 | m/s | 3.7244 | 0.0098158 | 4.2535 |  | 0.5 | 18 | 0.018 | 236.3046 | 7.1463 | 5.4303 | 0.022706 | 13.9504 | 0.12903
2025-05-19 14:01 | 448 | Remove | 2025-05-19 | 14:01 | US | GS | - | 16 | g | 0 | 111.8 | 11.872 | 1179.2 | 54618 | 3:44 | 29.8 | 2.22 m/s | 24.2 | 31.5 | 4.13 m/s | 16.3 |  | 2.22 | m/s |  | 4.13 | m/s | 3.7331 | 0.0098267 | 4.2633 |  | -2 | 16 | 0.016 | 266.4568 | 7.2664 | 5.3645 | 0.023729 | 13.9741 | 0.1145
2025-05-19 14:01 | 449 | Remove | 2025-05-19 | 14:01 | US | GS | - | 37 | g | 0 | 111.9 | 11.844 | 1176.5 | 54627 | 3:44 | 29.8 | 2.77 m/s | 25.9 | 31.5 | 4.26 m/s | 18 |  | 2.77 | m/s |  | 4.26 | m/s | 3.7414 | 0.0098042 | 4.2731 |  | 21 | 37 | 0.037 | 115.4895 | 7.7769 | 5.924 | 0.031687 | 14.0058 | 0.26418
2025-05-19 14:02 | 450 | Remove | 2025-05-19 | 14:02 | US | GS | - | 24.5 | g | 0 | 111.7 | 11.855 | 1177.3 | 54637 | 3:45 | 29.8 | 2.31 m/s | 22.1 | 31.5 | 3.89 m/s | 19.7 |  | 2.31 | m/s |  | 3.89 | m/s | 3.7497 | 0.0098108 | 4.2829 |  | -12.5 | 24.5 | 0.0245 | 174.8132 | 6.6359 | 6.4835 | 0.022548 | 14.0283 | 0.17465
2025-05-19 14:02 | 451 | Keep | 2025-05-19 | 14:02 | ST | GS | - | 18 | g | 0 | 111.8 | 11.841 | 1176.1 | 54647 | 3:45 | 29.8 | 2.33 m/s | 22.3 | 31.4 | 3.8 m/s | 17.2 |  | 2.33 | m/s |  | 3.8 | m/s | 3.7581 | 0.0098008 | 4.2927 |  | -6.5 | 18 | 0.018 | 238.4847 | 6.6959 | 5.6304 | 0.022949 | 14.0513 | 0.1281
2025-05-19 14:03 | 452 | Remove | 2025-05-19 | 14:03 | US | GS | - | 23.5 | g | 0 | 111.8 | 11.853 | 1177.6 | 54657 | 3:46 | 29.8 | 2.48 m/s | 23.7 | 31.4 | 3.94 m/s | 16.8 |  | 2.48 | m/s |  | 3.94 | m/s | 3.7664 | 0.0098133 | 4.3025 |  | 5.5 | 23.5 | 0.0235 | 183.0867 | 7.1163 | 5.4995 | 0.02596 | 14.0772 | 0.16694
2025-05-19 14:03 | 453 | Remove | 2025-05-19 | 14:03 | ST | GS | - | 22 | g | 0 | 111.8 | 11.82 | 1173.3 | 54667 | 3:46 | 29.8 | 2.42 m/s | 24.1 | 31.4 | 3.84 m/s | 17.5 |  | 2.42 | m/s |  | 3.84 | m/s | 3.7747 | 0.0097775 | 4.3123 |  | -1.5 | 22 | 0.022 | 196.0144 | 7.2364 | 5.7286 | 0.02576 | 14.103 | 0.156
2025-05-19 14:04 | 454 | Remove | 2025-05-19 | 14:04 | ST | GS | - | 21 | g | 0 | 111.9 | 11.812 | 1172.5 | 54677 | 3:47 | 29.8 | 2.19 m/s | 25.5 | 31.4 | 3.6 m/s | 17.7 |  | 2.19 | m/s |  | 3.6 | m/s | 3.7831 | 0.0097708 | 4.3221 |  | -1 | 21 | 0.021 | 205.8137 | 7.6568 | 5.7941 | 0.024666 | 14.1277 | 0.14864
2025-05-19 14:04 | 455 | Remove | 2025-05-19 | 14:04 | ST | GS | - | 25 | g | 0 | 111.8 | 11.865 | 1178.8 | 54686 | 3:47 | 29.8 | 2.42 m/s | 24.1 | 31.4 | 3.8 m/s | 19.1 |  | 2.42 | m/s |  | 3.8 | m/s | 3.7914 | 0.0098233 | 4.3319 |  | 4 | 25 | 0.025 | 173.2764 | 7.2364 | 6.2524 | 0.02576 | 14.1534 | 0.17664
2025-05-19 14:05 | 456 | Remove | 2025-05-19 | 14:05 | ST | GS | - | 21 | g | 0 | 111.8 | 11.855 | 1177.1 | 54696 | 3:48 | 29.8 | 2.33 m/s | 23.9 | 31.4 | 4.03 m/s | 17.9 |  | 2.33 | m/s |  | 4.03 | m/s | 3.7997 | 0.0098092 | 4.3417 |  | -4 | 21 | 0.021 | 206.7485 | 7.1763 | 5.8596 | 0.024596 | 14.178 | 0.14812
2025-05-19 14:05 | 457 | Remove | 2025-05-19 | 14:05 | ST | GS | - | 17.5 | g | 0 | 111.8 | 11.861 | 1178.2 | 54706 | 3:48 | 29.8 | 2.61 m/s | 22.3 | 31.4 | 3.96 m/s | 18 |  | 2.61 | m/s |  | 3.96 | m/s | 3.8081 | 0.0098183 | 4.3515 |  | -3.5 | 17.5 | 0.0175 | 248.6593 | 6.6959 | 5.8923 | 0.025707 | 14.2037 | 0.12321
2025-05-19 14:06 | 458 | Remove | 2025-05-19 | 14:06 | ST | GS | - | 19.5 | g | 0 | 111.6 | 11.884 | 1179.9 | 54716 | 3:49 | 29.8 | 2.38 m/s | 22.5 | 31.4 | 3.86 m/s | 17 |  | 2.38 | m/s |  | 3.86 | m/s | 3.8164 | 0.0098325 | 4.3614 |  | 2 | 19.5 | 0.0195 | 223.66 | 6.756 | 5.5649 | 0.023652 | 14.2274 | 0.13706
2025-05-19 14:06 | 459 | Remove | 2025-05-19 | 14:06 | ST | GS | - | 18.5 | g | 0 | 111.7 | 11.9 | 1182.8 | 54726 | 3:49 | 29.8 | 2.33 m/s | 23.7 | 31.4 | 3.92 m/s | 18.5 |  | 2.33 | m/s |  | 3.92 | m/s | 3.8247 | 0.0098567 | 4.3712 |  | -1 | 18.5 | 0.0185 | 236.2825 | 7.1163 | 6.056 | 0.02439 | 14.2518 | 0.12981
2025-05-19 14:07 | 460 | Remove | 2025-05-19 | 14:07 | US | GS | - | 21 | g | 0 | 111.7 | 11.887 | 1181 | 54736 | 3:50 | 29.8 | 2.25 m/s | 25.8 | 31.4 | 3.94 m/s | 18.1 |  | 2.25 | m/s |  | 3.94 | m/s | 3.8331 | 0.0098417 | 4.3811 |  | 2.5 | 21 | 0.021 | 208.6223 | 7.7468 | 5.925 | 0.025639 | 14.2774 | 0.14709
2025-05-19 14:07 | 461 | Remove | 2025-05-19 | 14:07 | ST | GS | - | 18.5 | g | 0 | 111.7 | 11.88 | 1180.4 | 54746 | 3:50 | 29.8 | 2.18 m/s | 26.1 | 31.5 | 3.84 m/s | 18.8 |  | 2.18 | m/s |  | 3.84 | m/s | 3.8414 | 0.0098367 | 4.3909 |  | -2.5 | 18.5 | 0.0185 | 237.3462 | 7.8369 | 6.1873 | 0.025131 | 14.3025 | 0.12935
2025-05-19 14:08 | 462 | Remove | 2025-05-19 | 14:08 | US | GS | - | 17 | g | 0 | 111.6 | 11.935 | 1186.9 | 54756 | 3:51 | 29.9 | 2.52 m/s | 24.6 | 31.5 | 4.15 m/s | 18.5 |  | 2.52 | m/s |  | 4.15 | m/s | 3.8497 | 0.0098908 | 4.4008 |  | -1.5 | 17 | 0.017 | 258.8703 | 7.4267 | 6.0885 | 0.02753 | 14.3301 | 0.11863
2025-05-19 14:08 | 463 | Remove | 2025-05-19 | 14:08 | ST | GS | - | 19.5 | g | 0 | 111.7 | 11.932 | 1186.8 | 54765 | 3:51 | 29.9 | 2.44 m/s | 24.1 | 31.5 | 4.0 m/s | 18.9 |  | 2.44 | m/s |  | 4 | m/s | 3.8581 | 0.00989 | 4.4107 |  | 2.5 | 19.5 | 0.0195 | 226.189 | 7.2758 | 6.2202 | 0.026114 | 14.3562 | 0.13583
2025-05-19 14:09 | 464 | Remove | 2025-05-19 | 14:09 | ST | GS | - | 20 | g | 0 | 111.6 | 11.994 | 1194.2 | 54775 | 3:52 | 29.9 | 2.06 m/s | 23.3 | 31.5 | 4.07 m/s | 17 |  | 2.06 | m/s |  | 4.07 | m/s | 3.8667 | 0.0099517 | 4.4206 |  | 0.5 | 20 | 0.02 | 221.0319 | 7.0343 | 5.5949 | 0.021315 | 14.3775 | 0.13911
2025-05-19 14:09 | 465 | Remove | 2025-05-19 | 14:09 | US | GS | - | 19 | g | 0 | 111.4 | 11.982 | 1191.6 | 54785 | 3:52 | 30 | 2.2 m/s | 23.3 | 31.6 | 4.18 m/s | 17.1 |  | 2.2 | m/s |  | 4.18 | m/s | 3.875 | 0.00993 | 4.4306 |  | -1 | 19 | 0.019 | 233.1878 | 7.0725 | 5.658 | 0.022888 | 14.4004 | 0.13194
2025-05-19 14:10 | 466 | Remove | 2025-05-19 | 14:10 | US | GS | - | 21 | g | 0 | 111.6 | 11.943 | 1187.7 | 54795 | 3:53 | 30 | 2.23 m/s | 22.3 | 31.6 | 4.0 m/s | 18 |  | 2.23 | m/s |  | 4 | m/s | 3.8833 | 0.0098975 | 4.4405 |  | 2 | 21 | 0.021 | 211.4507 | 6.769 | 5.9558 | 0.022204 | 14.4226 | 0.14561
2025-05-19 14:10 | 467 | Remove | 2025-05-19 | 14:10 | US | GS | - | 21 | g | 0 | 111.7 | 11.888 | 1181.4 | 54805 | 3:54 | 30 | 2.15 m/s | 24.4 | 31.6 | 3.98 m/s | 15.9 |  | 2.15 | m/s |  | 3.98 | m/s | 3.8917 | 0.009845 | 4.4503 |  | 0 | 21 | 0.021 | 211.9195 | 7.4064 | 5.261 | 0.023423 | 14.446 | 0.14537
2025-05-19 14:11 | 468 | Remove | 2025-05-19 | 14:11 | ST | GS | - | 19.5 | g | 0 | 111.6 | 11.902 | 1182.5 | 54815 | 3:54 | 30 | 2.2 m/s | 23.5 | 31.6 | 4.24 m/s | 18.2 |  | 2.2 | m/s |  | 4.24 | m/s | 3.9 | 0.0098542 | 4.4602 |  | -1.5 | 19.5 | 0.0195 | 228.7264 | 7.1332 | 6.022 | 0.023084 | 14.4691 | 0.13477
2025-05-19 14:11 | 469 | Remove | 2025-05-19 | 14:11 | ST | GS | - | 20.5 | g | 0 | 111.6 | 11.928 | 1185.9 | 54825 | 3:54 | 29.9 | 2.72 m/s | 22.2 | 31.6 | 4.21 m/s | 16.4 |  | 2.72 | m/s |  | 4.21 | m/s | 3.9083 | 0.0098825 | 4.47 |  | 1 | 20.5 | 0.0205 | 218.0511 | 6.7022 | 5.4264 | 0.026816 | 14.4959 | 0.14142
2025-05-19 14:12 | 470 | Remove | 2025-05-19 | 14:12 | ST | GS | - | 20.5 | g | 0 | 111.6 | 11.953 | 1188.5 | 54835 | 3:55 | 29.9 | 2.44 m/s | 21.5 | 31.6 | 3.89 m/s | 15.8 |  | 2.44 | m/s |  | 3.89 | m/s | 3.9167 | 0.0099042 | 4.48 |  | 0 | 20.5 | 0.0205 | 218.5342 | 6.4908 | 5.2279 | 0.023297 | 14.5192 | 0.14119
2025-05-19 14:12 | 471 | Remove | 2025-05-19 | 14:12 | ST | GS | - | 20.5 | g | 0 | 111.5 | 11.938 | 1186.1 | 54845 | 3:56 | 29.9 | 2.33 m/s | 23.1 | 31.7 | 4.12 m/s | 16.4 |  | 2.33 | m/s |  | 4.12 | m/s | 3.925 | 0.0098842 | 4.4898 |  | 0 | 20.5 | 0.0205 | 219.0163 | 6.9739 | 5.4555 | 0.023902 | 14.5431 | 0.14096
2025-05-19 14:13 | 472 | Remove | 2025-05-19 | 14:13 | ST | GS | - | 20 | g | 0 | 111.5 | 11.953 | 1188.3 | 54855 | 3:56 | 30 | 2.31 m/s | 22.5 | 31.7 | 3.86 m/s | 16.5 |  | 2.31 | m/s |  | 3.86 | m/s | 3.9333 | 0.0099025 | 4.4997 |  | -0.5 | 20 | 0.02 | 224.9869 | 6.8297 | 5.4888 | 0.023207 | 14.5663 | 0.1373
2025-05-19 14:13 | 473 | Remove | 2025-05-19 | 14:13 | ST | GS | - | 20.5 | g | 0 | 111.5 | 11.933 | 1185.7 | 54865 | 3:56 | 30 | 2.35 m/s | 21.7 | 31.7 | 3.85 m/s | 17.6 |  | 2.35 | m/s |  | 3.85 | m/s | 3.9417 | 0.0098808 | 4.5096 |  | 0.5 | 20.5 | 0.0205 | 219.9814 | 6.5869 | 5.8547 | 0.022769 | 14.5891 | 0.14052
2025-05-19 14:14 | 474 | Remove | 2025-05-19 | 14:14 | US | GS | - | 24.5 | g | 0 | 111.5 | 11.968 | 1190.1 | 54875 | 3:57 | 30 | 2.58 m/s | 21.6 | 31.7 | 4.04 m/s | 16.4 |  | 2.58 | m/s |  | 4.04 | m/s | 3.95 | 0.0099175 | 4.5195 |  | 4 | 24.5 | 0.0245 | 184.4709 | 6.5565 | 5.4555 | 0.024882 | 14.614 | 0.16765
2025-05-19 14:14 | 475 | Remove | 2025-05-19 | 14:14 | ST | GS | - | 20 | g | 0 | 111.6 | 11.955 | 1188.6 | 54884 | 3:58 | 30 | 2.11 m/s | 23.6 | 31.6 | 3.76 m/s | 16.3 |  | 2.11 | m/s |  | 3.76 | m/s | 3.9583 | 0.009905 | 4.5294 |  | -4.5 | 20 | 0.02 | 226.472 | 7.1636 | 5.3933 | 0.022234 | 14.6362 | 0.13665
2025-05-19 14:15 | 476 | Remove | 2025-05-19 | 14:15 | ST | GS | - | 22.5 | g | 0 | 111.6 | 11.961 | 1188.9 | 54894 | 3:58 | 30 | 2.48 m/s | 22.1 | 31.6 | 3.85 m/s | 17.8 |  | 2.48 | m/s |  | 3.85 | m/s | 3.9667 | 0.0099075 | 4.5393 |  | 2.5 | 22.5 | 0.0225 | 201.7488 | 6.7083 | 5.8896 | 0.024472 | 14.6607 | 0.15347
2025-05-19 14:15 | 477 | Remove | 2025-05-19 | 14:15 | ST | GS | - | 20 | g | 0 | 111.7 | 11.928 | 1185.9 | 54904 | 3:58 | 30 | 2.77 m/s | 23.2 | 31.7 | 3.84 m/s | 16.6 |  | 2.77 | m/s |  | 3.84 | m/s | 3.975 | 0.0098825 | 4.5492 |  | -2.5 | 20 | 0.02 | 227.4615 | 7.0422 | 5.5221 | 0.028694 | 14.6894 | 0.13615
2025-05-19 14:16 | 478 | Remove | 2025-05-19 | 14:16 | ST | GS | - | 19 | g | 0 | 111.7 | 11.948 | 1188 | 54914 | 3:59 | 30 | 2.02 m/s | 22.3 | 31.7 | 3.79 m/s | 16.9 |  | 2.02 | m/s |  | 3.79 | m/s | 3.9833 | 0.0099 | 4.5591 |  | -1 | 19 | 0.019 | 239.9543 | 6.769 | 5.6219 | 0.020113 | 14.7095 | 0.12917
2025-05-19 14:16 | 479 | Remove | 2025-05-19 | 14:16 | ST | GS | - | 24 | g | 0 | 111.7 | 11.955 | 1188.6 | 54924 | 4:00 | 30 | 2.35 m/s | 21 | 31.7 | 3.98 m/s | 16.7 |  | 2.35 | m/s |  | 3.98 | m/s | 3.9917 | 0.009905 | 4.569 |  | 5 | 24 | 0.024 | 190.3765 | 6.3744 | 5.5553 | 0.022035 | 14.7315 | 0.16292
2025-05-19 14:17 | 480 | Remove | 2025-05-19 | 14:17 | ST | GS | - | 20 | g | 0 | 111.6 | 11.975 | 1190.3 | 54934 | 4:00 | 30 | 2.22 m/s | 22.8 | 31.7 | 3.94 m/s | 16.1 |  | 2.22 | m/s |  | 3.94 | m/s | 4 | 0.0099192 | 4.579 |  | -4 | 20 | 0.02 | 228.9478 | 6.9207 | 5.3557 | 0.0226 | 14.7541 | 0.13556
2025-05-19 14:17 | 481 | Keep | 2025-05-19 | 14:17 | ST | GS | - | 23.5 | g | 0 | 111.6 | 11.938 | 1186.2 | 54944 | 4:01 | 30 | 2.77 m/s | 22.2 | 31.7 | 3.84 m/s | 16.8 |  | 2.77 | m/s |  | 3.84 | m/s | 4.0086 | 0.009885 | 4.5888 |  | 3.5 | 23.5 | 0.0235 | 195.2698 | 6.7386 | 5.5886 | 0.027457 | 14.7816 | 0.15898
2025-05-19 14:18 | 482 | Remove | 2025-05-19 | 14:18 | US | GS | - | 24 | g | 0 | 111.6 | 11.954 | 1187.6 | 54954 | 4:01 | 30 | 2.94 m/s | 22.7 | 31.7 | 4.29 m/s | 15.7 |  | 2.94 | m/s |  | 4.29 | m/s | 4.0169 | 0.0098967 | 4.5987 |  | 0.5 | 24 | 0.024 | 191.614 | 6.8904 | 5.2227 | 0.029798 | 14.8114 | 0.16204
2025-05-19 14:18 | 483 | Remove | 2025-05-19 | 14:18 | ST | GS | - | 22 | g | 0 | 111.7 | 11.925 | 1185.7 | 54964 | 4:02 | 30 | 2.77 m/s | 21.5 | 31.7 | 3.8 m/s | 15.8 |  | 2.77 | m/s |  | 3.8 | m/s | 4.0253 | 0.0098808 | 4.6086 |  | -2 | 22 | 0.022 | 209.4826 | 6.5261 | 5.256 | 0.026591 | 14.838 | 0.14827
2025-05-19 14:19 | 484 | Remove | 2025-05-19 | 14:19 | ST | GS | - | 20 | g | 0 | 111.6 | 11.926 | 1185.7 | 54974 | 4:02 | 30 | 2.4 m/s | 21.7 | 31.7 | 3.77 m/s | 16.1 |  | 2.4 | m/s |  | 3.77 | m/s | 4.0336 | 0.0098808 | 4.6185 |  | -2 | 20 | 0.02 | 230.9249 | 6.5869 | 5.3557 | 0.023254 | 14.8612 | 0.13458
2025-05-19 14:19 | 485 | Remove | 2025-05-19 | 14:19 | ST | GS | - | 21.5 | g | 0 | 111.6 | 11.949 | 1187.6 | 54984 | 4:03 | 30 | 2.67 m/s | 23 | 31.7 | 3.89 m/s | 16.3 |  | 2.67 | m/s |  | 3.89 | m/s | 4.0419 | 0.0098967 | 4.6284 |  | 1.5 | 21.5 | 0.0215 | 215.2742 | 6.9815 | 5.4223 | 0.027419 | 14.8886 | 0.14441
2025-05-19 14:20 | 486 | Remove | 2025-05-19 | 14:20 | ST | GS | - | 20.5 | g | 0 | 111.7 | 11.945 | 1187.4 | 54994 | 4:03 | 30 | 2.3 m/s | 21.8 | 31.7 | 4.07 m/s | 16.6 |  | 2.3 | m/s |  | 4.07 | m/s | 4.0503 | 0.009895 | 4.6383 |  | -1 | 20.5 | 0.0205 | 226.258 | 6.6172 | 5.5221 | 0.022387 | 14.911 | 0.13748
2025-05-19 14:20 | 487 | Remove | 2025-05-19 | 14:20 | US | GS | - | 24.5 | g | 0 | 111.7 | 11.9 | 1182.4 | 55003 | 4:04 | 30 | 2.34 m/s | 22.3 | 31.7 | 3.79 m/s | 15.6 |  | 2.34 | m/s |  | 3.79 | m/s | 4.0586 | 0.0098533 | 4.6481 |  | 4 | 24.5 | 0.0245 | 189.7201 | 6.769 | 5.1894 | 0.023299 | 14.9343 | 0.16405
2025-05-19 14:21 | 488 | Remove | 2025-05-19 | 14:21 | ST | GS | - | 19.5 | g | 0 | 111.5 | 11.947 | 1187.6 | 55013 | 4:04 | 30 | 2.15 m/s | 20.8 | 31.6 | 4.18 m/s | 16.1 |  | 2.15 | m/s |  | 4.18 | m/s | 4.0669 | 0.0098967 | 4.658 |  | -5 | 19.5 | 0.0195 | 238.8738 | 6.3137 | 5.3271 | 0.019967 | 14.9543 | 0.1304
2025-05-19 14:21 | 489 | Remove | 2025-05-19 | 14:21 | ST | GS | - | 21 | g | 0 | 111.6 | 11.984 | 1192.5 | 55023 | 4:05 | 30 | 2.2 m/s | 22 | 31.6 | 3.77 m/s | 16.5 |  | 2.2 | m/s |  | 3.77 | m/s | 4.0753 | 0.0099375 | 4.668 |  | 1.5 | 21 | 0.021 | 222.2846 | 6.6779 | 5.4595 | 0.021611 | 14.9759 | 0.14023
2025-05-19 14:22 | 490 | Remove | 2025-05-19 | 14:22 | ST | GS | - | 20.5 | g | 0 | 111.7 | 11.964 | 1189.4 | 55033 | 4:05 | 30 | 2.58 m/s | 22.5 | 31.6 | 4.1 m/s | 17 |  | 2.58 | m/s |  | 4.1 | m/s | 4.0836 | 0.0099117 | 4.6779 |  | -0.5 | 20.5 | 0.0205 | 228.1897 | 6.8297 | 5.6249 | 0.025919 | 15.0018 | 0.13665
2025-05-19 14:22 | 491 | Remove | 2025-05-19 | 14:22 | ST | GS | - | 21 | g | 0 | 111.7 | 11.95 | 1189 | 55043 | 4:06 | 30 | 2.08 m/s | 21.7 | 31.7 | 3.97 m/s | 16.1 |  | 2.08 | m/s |  | 3.97 | m/s | 4.0922 | 0.0099083 | 4.6878 |  | 0.5 | 21 | 0.021 | 223.2285 | 6.5869 | 5.3557 | 0.020153 | 15.022 | 0.1398
2025-05-19 14:23 | 492 | Remove | 2025-05-19 | 14:23 | ST | GS | - | 21 | g | 0 | 111.7 | 11.944 | 1188.5 | 55053 | 4:06 | 30 | 2.15 m/s | 23.1 | 31.7 | 4.07 m/s | 16.5 |  | 2.15 | m/s |  | 4.07 | m/s | 4.1006 | 0.0099042 | 4.6977 |  | 0 | 21 | 0.021 | 223.7001 | 7.0118 | 5.4888 | 0.022175 | 15.0441 | 0.13959
2025-05-19 14:23 | 493 | Remove | 2025-05-19 | 14:23 | ST | GS | - | 21.5 | g | 0 | 111.6 | 11.968 | 1190.8 | 55063 | 4:07 | 30 | 2.42 m/s | 22.1 | 31.7 | 4.16 m/s | 16.9 |  | 2.42 | m/s |  | 4.16 | m/s | 4.1089 | 0.0099233 | 4.7076 |  | 0.5 | 21.5 | 0.0215 | 218.9593 | 6.7083 | 5.6219 | 0.02388 | 15.068 | 0.14269
2025-05-19 14:24 | 494 | Remove | 2025-05-19 | 14:24 | US | GS | - | 25.5 | g | 0 | 111.6 | 11.988 | 1192.5 | 55073 | 4:07 | 30 | 2.64 m/s | 20.9 | 31.7 | 4.04 m/s | 16.6 |  | 2.64 | m/s |  | 4.04 | m/s | 4.1172 | 0.0099375 | 4.7176 |  | 4 | 25.5 | 0.0255 | 185.0025 | 6.344 | 5.5221 | 0.024636 | 15.0927 | 0.16896
2025-05-19 14:24 | 495 | Remove | 2025-05-19 | 14:24 | ST | GS | - | 24.5 | g | 0 | 111.6 | 11.964 | 1189.3 | 55083 | 4:08 | 30 | 2.47 m/s | 22.3 | 31.7 | 3.93 m/s | 16.4 |  | 2.47 | m/s |  | 3.93 | m/s | 4.1256 | 0.0099108 | 4.7275 |  | -1 | 24.5 | 0.0245 | 192.9581 | 6.769 | 5.4555 | 0.024594 | 15.1172 | 0.16207
2025-05-19 14:25 | 496 | Remove | 2025-05-19 | 14:25 | US | GS | - | 25.5 | g | 0 | 111.8 | 11.931 | 1187.1 | 55093 | 4:08 | 30 | 2.68 m/s | 22.3 | 31.7 | 4.16 m/s | 16.5 |  | 2.68 | m/s |  | 4.16 | m/s | 4.1339 | 0.0098925 | 4.7374 |  | 1 | 25.5 | 0.0255 | 185.7791 | 6.769 | 5.4888 | 0.026685 | 15.1439 | 0.16838
2025-05-19 14:25 | 497 | Remove | 2025-05-19 | 14:25 | ST | GS | - | 21 | g | 0 | 111.6 | 11.967 | 1190.2 | 55103 | 4:09 | 30 | 2.51 m/s | 22.3 | 31.7 | 3.94 m/s | 16.4 |  | 2.51 | m/s |  | 3.94 | m/s | 4.1422 | 0.0099183 | 4.7473 |  | -4.5 | 21 | 0.021 | 226.0612 | 6.769 | 5.4555 | 0.024992 | 15.1689 | 0.13844
2025-05-19 14:26 | 498 | Remove | 2025-05-19 | 14:26 | ST | GS | - | 24 | g | 0 | 111.7 | 11.974 | 1190.9 | 55113 | 4:09 | 30 | 2.71 m/s | 21.9 | 31.7 | 3.96 m/s | 16.6 |  | 2.71 | m/s |  | 3.96 | m/s | 4.1508 | 0.0099242 | 4.7572 |  | 3 | 24 | 0.024 | 198.217 | 6.6476 | 5.5221 | 0.026499 | 15.1954 | 0.15794
2025-05-19 14:26 | 499 | Remove | 2025-05-19 | 14:26 | ST | GS | - | 22 | g | 0 | 111.7 | 11.988 | 1192.6 | 55123 | 4:10 | 30 | 2.16 m/s | 22.1 | 31.7 | 4.13 m/s | 16.5 |  | 2.16 | m/s |  | 4.13 | m/s | 4.1592 | 0.0099383 | 4.7671 |  | -2 | 22 | 0.022 | 216.6885 | 6.7083 | 5.4888 | 0.021314 | 15.2167 | 0.14458
2025-05-19 14:27 | 500 | Remove | 2025-05-19 | 14:27 | ST | GS | - | 21.5 | g | 0 | 111.6 | 11.975 | 1191.1 | 55133 | 4:10 | 30 | 2.67 m/s | 21.6 | 31.7 | 4.01 m/s | 16.6 |  | 2.67 | m/s |  | 4.01 | m/s | 4.1675 | 0.0099258 | 4.7771 |  | -0.5 | 21.5 | 0.0215 | 222.1894 | 6.5565 | 5.5221 | 0.02575 | 15.2425 | 0.14105
2025-05-19 14:27 | 501 | Remove | 2025-05-19 | 14:27 | US | GS | - | 23 | g | 0 | 111.7 | 11.938 | 1187 | 55142 | 4:11 | 30.1 | 2.27 m/s | 23 | 31.7 | 4.03 m/s | 16.3 |  | 2.27 | m/s |  | 4.03 | m/s | 4.1758 | 0.0098917 | 4.787 |  | 1.5 | 23 | 0.023 | 208.1289 | 7.0194 | 5.4223 | 0.023438 | 15.2659 | 0.15066
2025-05-19 14:28 | 502 | Remove | 2025-05-19 | 14:28 | US | GS | - | 30.5 | g | 0 | 111.7 | 11.941 | 1188 | 55153 | 4:11 | 30.1 | 2.35 m/s | 23.7 | 31.7 | 3.81 m/s | 17 |  | 2.35 | m/s |  | 3.81 | m/s | 4.1842 | 0.0099 | 4.7969 |  | 7.5 | 30.5 | 0.0305 | 157.2742 | 7.233 | 5.6551 | 0.025003 | 15.2909 | 0.19946
2025-05-19 14:28 | 503 | Remove | 2025-05-19 | 14:28 | ST | GS | - | 22.5 | g | 0 | 111.7 | 11.959 | 1189.7 | 55162 | 4:12 | 30.1 | 2.51 m/s | 22.5 | 31.7 | 3.61 m/s | 16.5 |  | 2.51 | m/s |  | 3.61 | m/s | 4.1925 | 0.0099142 | 4.8068 |  | -8 | 22.5 | 0.0225 | 213.6346 | 6.8668 | 5.4888 | 0.025353 | 15.3163 | 0.1469
2025-05-19 14:29 | 504 | Remove | 2025-05-19 | 14:29 | US | GS | - | 23.5 | g | 0 | 111.7 | 11.908 | 1183.5 | 55172 | 4:12 | 30.1 | 2.45 m/s | 23.9 | 31.6 | 3.79 m/s | 17 |  | 2.45 | m/s |  | 3.79 | m/s | 4.2008 | 0.0098625 | 4.8166 |  | 1 | 23.5 | 0.0235 | 204.9634 | 7.2941 | 5.6249 | 0.026287 | 15.3426 | 0.15317
2025-05-19 14:29 | 505 | Remove | 2025-05-19 | 14:29 | ST | GS | - | 22 | g | 0 | 111.7 | 11.921 | 1184.8 | 55182 | 4:13 | 30 | 2.65 m/s | 21.6 | 31.6 | 3.98 m/s | 17.7 |  | 2.65 | m/s |  | 3.98 | m/s | 4.2092 | 0.0098733 | 4.8265 |  | -1.5 | 22 | 0.022 | 219.387 | 6.5565 | 5.8566 | 0.025558 | 15.3681 | 0.14315
2025-05-19 14:30 | 506 | Remove | 2025-05-19 | 14:30 | ST | GS | - | 21.5 | g | 0 | 111.6 | 11.94 | 1187.9 | 55192 | 4:13 | 30 | 2.13 m/s | 23.6 | 31.6 | 3.77 m/s | 16.7 |  | 2.13 | m/s |  | 3.77 | m/s | 4.2175 | 0.0098992 | 4.8364 |  | -0.5 | 21.5 | 0.0215 | 224.9495 | 7.1636 | 5.5257 | 0.022445 | 15.3906 | 0.1397
2025-05-19 14:30 | 507 | Remove | 2025-05-19 | 14:30 | ST | GS | - | 23 | g | 0 | 111.7 | 11.937 | 1187.1 | 55202 | 4:14 | 30 | 2.57 m/s | 22.1 | 31.6 | 4.41 m/s | 17.3 |  | 2.57 | m/s |  | 4.41 | m/s | 4.2258 | 0.0098925 | 4.8463 |  | 1.5 | 23 | 0.023 | 210.7089 | 6.7083 | 5.7242 | 0.02536 | 15.4159 | 0.1492
2025-05-19 14:31 | 508 | Remove | 2025-05-19 | 14:31 | ST | GS | - | 21.5 | g | 0 | 111.7 | 11.953 | 1189.4 | 55212 | 4:14 | 30 | 2.26 m/s | 23.2 | 31.6 | 4.13 m/s | 17 |  | 2.26 | m/s |  | 4.13 | m/s | 4.2342 | 0.0099117 | 4.8562 |  | -1.5 | 21.5 | 0.0215 | 225.8706 | 7.0422 | 5.6249 | 0.023411 | 15.4393 | 0.13925
2025-05-19 14:31 | 509 | Remove | 2025-05-19 | 14:31 | ST | GS | - | 21.5 | g | 0 | 111.6 | 11.992 | 1192.8 | 55222 | 4:15 | 30.1 | 2.15 m/s | 22.6 | 31.6 | 4.0 m/s | 16.7 |  | 2.15 | m/s |  | 4 | m/s | 4.2425 | 0.00994 | 4.8662 |  | 0 | 21.5 | 0.0215 | 226.3329 | 6.8973 | 5.5257 | 0.021813 | 15.4612 | 0.13906
2025-05-19 14:32 | 510 | Remove | 2025-05-19 | 14:32 | ST | GS | - | 22 | g | 0 | 111.7 | 11.951 | 1188.7 | 55232 | 4:15 | 30.1 | 2.5 m/s | 23.4 | 31.6 | 4.15 m/s | 17.8 |  | 2.5 | m/s |  | 4.15 | m/s | 4.2508 | 0.0099058 | 4.8761 |  | 0.5 | 22 | 0.022 | 221.6392 | 7.1415 | 5.8896 | 0.026262 | 15.4874 | 0.14205
2025-05-19 14:32 | 511 | Keep | 2025-05-19 | 14:32 | ST | GS | - | 23 | g | 0 | 111.6 | 11.907 | 1183.3 | 55242 | 4:16 | 30.1 | 2.05 m/s | 22.5 | 31.6 | 3.93 m/s | 16.9 |  | 2.05 | m/s |  | 3.93 | m/s | 4.2592 | 0.0098608 | 4.8859 |  | 1 | 23 | 0.023 | 212.4315 | 6.8668 | 5.5918 | 0.020707 | 15.5081 | 0.14831
2025-05-19 14:33 | 512 | Remove | 2025-05-19 | 14:33 | ST | GS | - | 23 | g | 0 | 111.6 | 11.966 | 1189.5 | 55252 | 4:16 | 30.1 | 2.42 m/s | 22.1 | 31.6 | 3.69 m/s | 17.9 |  | 2.42 | m/s |  | 3.69 | m/s | 4.2675 | 0.0099125 | 4.8958 |  | 0 | 23 | 0.023 | 212.8625 | 6.7447 | 5.9227 | 0.024009 | 15.5321 | 0.14808
2025-05-19 14:33 | 513 | Remove | 2025-05-19 | 14:33 | ST | GS | - | 24.5 | g | 0 | 111.5 | 11.903 | 1182.4 | 55262 | 4:17 | 30 | 2.27 m/s | 22.7 | 31.6 | 4.04 m/s | 16.9 |  | 2.27 | m/s |  | 4.04 | m/s | 4.2758 | 0.0098533 | 4.9057 |  | 1.5 | 24.5 | 0.0245 | 200.2322 | 6.8904 | 5.5918 | 0.023008 | 15.5551 | 0.1575
2025-05-19 14:34 | 514 | Remove | 2025-05-19 | 14:34 | US | GS | - | 22.5 | g | 0 | 111.6 | 11.935 | 1186.2 | 55272 | 4:17 | 30 | 2.26 m/s | 20.9 | 31.6 | 3.94 m/s | 16.7 |  | 2.26 | m/s |  | 3.94 | m/s | 4.2842 | 0.009885 | 4.9156 |  | -2 | 22.5 | 0.0225 | 218.47 | 6.344 | 5.5257 | 0.02109 | 15.5762 | 0.14445
2025-05-19 14:34 | 515 | Remove | 2025-05-19 | 14:34 | ST | GS | - | 29.5 | g | 0 | 111.7 | 11.991 | 1194 | 55282 | 4:18 | 30.1 | 2.51 m/s | 21.1 | 31.6 | 3.92 m/s | 16 |  | 2.51 | m/s |  | 3.92 | m/s | 4.2928 | 0.00995 | 4.9255 |  | 7 | 29.5 | 0.0295 | 166.9669 | 6.4395 | 5.2941 | 0.023776 | 15.6 | 0.1891
2025-05-19 14:35 | 516 | Remove | 2025-05-19 | 14:35 | ST | GS | - | 23.5 | g | 0 | 111.6 | 11.95 | 1188.6 | 55292 | 4:18 | 30.1 | 2.37 m/s | 24.3 | 31.6 | 3.81 m/s | 17.3 |  | 2.37 | m/s |  | 3.81 | m/s | 4.3011 | 0.009905 | 4.9354 |  | -6 | 23.5 | 0.0235 | 210.0183 | 7.4161 | 5.7242 | 0.025854 | 15.6259 | 0.15039
2025-05-19 14:35 | 517 | Remove | 2025-05-19 | 14:35 | ST | GS | - | 23 | g | 0 | 111.6 | 11.952 | 1188.4 | 55301 | 4:19 | 30.1 | 2.27 m/s | 23.2 | 31.6 | 3.77 m/s | 17.6 |  | 2.27 | m/s |  | 3.77 | m/s | 4.3094 | 0.0099033 | 4.9453 |  | -0.5 | 23 | 0.023 | 215.0145 | 7.0804 | 5.8235 | 0.023642 | 15.6495 | 0.14697
2025-05-19 14:36 | 518 | Remove | 2025-05-19 | 14:36 | ST | GS | - | 23 | g | 0 | 111.6 | 11.982 | 1192.3 | 55312 | 4:19 | 30.1 | 2.23 m/s | 23.6 | 31.7 | 4.04 m/s | 17.2 |  | 2.23 | m/s |  | 4.04 | m/s | 4.3178 | 0.0099358 | 4.9553 |  | 0 | 23 | 0.023 | 215.4465 | 7.2025 | 5.7217 | 0.023626 | 15.6731 | 0.14675
2025-05-19 14:36 | 519 | Remove | 2025-05-19 | 14:36 | ST | GS | - | 24 | g | 0 | 111.4 | 11.94 | 1186.4 | 55321 | 4:20 | 30.1 | 2.3 m/s | 21.3 | 31.7 | 4.1 m/s | 17 |  | 2.3 | m/s |  | 4.1 | m/s | 4.3261 | 0.0098867 | 4.9652 |  | 1 | 24 | 0.024 | 206.8815 | 6.5006 | 5.6551 | 0.021993 | 15.6951 | 0.15291
2025-05-19 14:37 | 520 | Remove | 2025-05-19 | 14:37 | US | GS | - | 23 | g | 0 | 111.6 | 11.933 | 1186.3 | 55331 | 4:20 | 30.1 | 2.08 m/s | 21.4 | 31.7 | 3.67 m/s | 16.2 |  | 2.08 | m/s |  | 3.67 | m/s | 4.3344 | 0.0098858 | 4.975 |  | -1 | 23 | 0.023 | 216.3062 | 6.5311 | 5.389 | 0.019983 | 15.7151 | 0.14636
2025-05-19 14:37 | 521 | Remove | 2025-05-19 | 14:37 | ST | GS | - | 23.5 | g | 0 | 111.6 | 11.932 | 1185.7 | 55341 | 4:21 | 30.1 | 2.18 m/s | 20.5 | 31.7 | 4.01 m/s | 16 |  | 2.18 | m/s |  | 4.01 | m/s | 4.3428 | 0.0098808 | 4.9849 |  | 0.5 | 23.5 | 0.0235 | 212.1244 | 6.2564 | 5.3225 | 0.020062 | 15.7352 | 0.14935
2025-05-19 14:38 | 522 | Remove | 2025-05-19 | 14:38 | US | GS | - | 29 | g | 0 | 111.5 | 11.995 | 1193.2 | 55351 | 4:21 | 30.1 | 2.48 m/s | 21.5 | 31.7 | 4.24 m/s | 15.5 |  | 2.48 | m/s |  | 4.24 | m/s | 4.3511 | 0.0099433 | 4.9949 |  | 5.5 | 29 | 0.029 | 172.2368 | 6.5616 | 5.1562 | 0.023937 | 15.7591 | 0.18402
2025-05-19 14:38 | 523 | Remove | 2025-05-19 | 14:38 | ST | GS | - | 25 | g | 0 | 111.4 | 11.995 | 1193.3 | 55361 | 4:22 | 30.1 | 2.48 m/s | 21.5 | 31.7 | 3.88 m/s | 15.8 |  | 2.48 | m/s |  | 3.88 | m/s | 4.3594 | 0.0099442 | 5.0048 |  | -4 | 25 | 0.025 | 200.1924 | 6.5616 | 5.256 | 0.023937 | 15.783 | 0.1584
2025-05-19 14:39 | 524 | Remove | 2025-05-19 | 14:39 | ST | GS | - | 25 | g | 0 | 111.5 | 11.951 | 1188.3 | 55371 | 4:22 | 30.1 | 2.34 m/s | 22.5 | 31.7 | 3.96 m/s | 19.2 |  | 2.34 | m/s |  | 3.96 | m/s | 4.3678 | 0.0099025 | 5.0147 |  | 0 | 25 | 0.025 | 200.5885 | 6.8668 | 6.387 | 0.023636 | 15.8067 | 0.15816
2025-05-19 14:39 | 525 | Remove | 2025-05-19 | 14:39 | US | GS | - | 24 | g | 0 | 111.6 | 11.945 | 1187.3 | 55381 | 4:23 | 30.1 | 2.19 m/s | 24.5 | 31.7 | 3.97 m/s | 17.2 |  | 2.19 | m/s |  | 3.97 | m/s | 4.3761 | 0.0098942 | 5.0246 |  | -1 | 24 | 0.024 | 209.3586 | 7.4772 | 5.7217 | 0.024087 | 15.8308 | 0.1516
2025-05-19 14:40 | 526 | Remove | 2025-05-19 | 14:40 | US | GS | - | 32.5 | g | 0 | 111.5 | 11.968 | 1189.7 | 55391 | 4:23 | 30.1 | 2.35 m/s | 26.3 | 31.7 | 4.16 m/s | 17.7 |  | 2.35 | m/s |  | 4.16 | m/s | 4.3844 | 0.0099142 | 5.0345 |  | 8.5 | 32.5 | 0.0325 | 154.9083 | 8.0265 | 5.888 | 0.027746 | 15.8585 | 0.20494
2025-05-19 14:40 | 527 | Remove | 2025-05-19 | 14:40 | US | GS | - | 24.5 | g | 0 | 111.5 | 11.964 | 1189.1 | 55401 | 4:24 | 30.1 | 2.15 m/s | 29.7 | 31.7 | 4.1 m/s | 20.7 |  | 2.15 | m/s |  | 4.1 | m/s | 4.3928 | 0.0099092 | 5.0444 |  | -8 | 24.5 | 0.0245 | 205.8951 | 9.0642 | 6.886 | 0.028666 | 15.8872 | 0.15421
2025-05-19 14:41 | 528 | Remove | 2025-05-19 | 14:41 | ST | GS | - | 23.5 | g | 0 | 111.5 | 11.923 | 1185.2 | 55411 | 4:24 | 30.1 | 2.15 m/s | 26.1 | 31.7 | 3.84 m/s | 17.6 |  | 2.15 | m/s |  | 3.84 | m/s | 4.4011 | 0.0098767 | 5.0543 |  | -1 | 23.5 | 0.0235 | 215.0769 | 7.9655 | 5.8547 | 0.025191 | 15.9124 | 0.14768
2025-05-19 14:41 | 529 | Remove | 2025-05-19 | 14:41 | US | GS | - | 23.5 | g | 0 | 111.4 | 11.974 | 1191 | 55421 | 4:25 | 30.1 | 2.65 m/s | 25.1 | 31.7 | 3.8 m/s | 17.2 |  | 2.65 | m/s |  | 3.8 | m/s | 4.4094 | 0.009925 | 5.0642 |  | 0 | 23.5 | 0.0235 | 215.4992 | 7.6603 | 5.7217 | 0.02986 | 15.9422 | 0.14741
2025-05-19 14:42 | 530 | Remove | 2025-05-19 | 14:42 | ST | GS | - | 23.5 | g | 0 | 111.5 | 11.978 | 1191.3 | 55431 | 4:25 | 30.1 | 2.15 m/s | 23.2 | 31.6 | 3.76 m/s | 17 |  | 2.15 | m/s |  | 3.76 | m/s | 4.4178 | 0.0099275 | 5.0742 |  | 0 | 23.5 | 0.0235 | 215.9217 | 7.0804 | 5.6249 | 0.022392 | 15.9646 | 0.1472
2025-05-19 14:42 | 531 | Remove | 2025-05-19 | 14:42 | ST | GS | - | 23 | g | 0 | 111.6 | 11.965 | 1190.8 | 55441 | 4:26 | 30.2 | 2.22 m/s | 22.6 | 31.7 | 4.03 m/s | 17.2 |  | 2.22 | m/s |  | 4.03 | m/s | 4.4261 | 0.0099233 | 5.0841 |  | -0.5 | 23 | 0.023 | 221.0471 | 6.9348 | 5.7217 | 0.022646 | 15.9873 | 0.14386
2025-05-19 14:43 | 532 | Remove | 2025-05-19 | 14:43 | ST | GS | - | 25.5 | g | 0 | 111.5 | 12.013 | 1195.3 | 55451 | 4:26 | 30.1 | 2.13 m/s | 22.5 | 31.7 | 3.94 m/s | 17.2 |  | 2.13 | m/s |  | 3.94 | m/s | 4.4344 | 0.0099608 | 5.094 |  | 2.5 | 25.5 | 0.0255 | 199.7664 | 6.8668 | 5.7217 | 0.021515 | 16.0088 | 0.15929
2025-05-19 14:43 | 533 | Remove | 2025-05-19 | 14:43 | ST | GS | - | 23.5 | g | 0 | 111.5 | 12.017 | 1197 | 55461 | 4:27 | 30.2 | 2.04 m/s | 22.1 | 31.7 | 4.07 m/s | 17 |  | 2.04 | m/s |  | 4.07 | m/s | 4.4431 | 0.009975 | 5.104 |  | -2 | 23.5 | 0.0235 | 217.1923 | 6.7814 | 5.6551 | 0.020349 | 16.0291 | 0.14661
2025-05-19 14:44 | 534 | Remove | 2025-05-19 | 14:44 | US | GS | - | 26.5 | g | 0 | 111.5 | 12.026 | 1197.3 | 55471 | 4:27 | 30.2 | 2.35 m/s | 22 | 31.7 | 3.93 m/s | 16.2 |  | 2.35 | m/s |  | 3.93 | m/s | 4.4514 | 0.0099775 | 5.114 |  | 3 | 26.5 | 0.0265 | 192.981 | 6.7507 | 5.389 | 0.023335 | 16.0525 | 0.16508
2025-05-19 14:44 | 535 | Remove | 2025-05-19 | 14:44 | ST | GS | - | 23 | g | 0 | 111.6 | 11.956 | 1189.7 | 55481 | 4:28 | 30.2 | 2.37 m/s | 21.6 | 31.7 | 3.84 m/s | 16.5 |  | 2.37 | m/s |  | 3.84 | m/s | 4.4597 | 0.0099142 | 5.1239 |  | -3.5 | 23 | 0.023 | 222.7787 | 6.6279 | 5.4888 | 0.023106 | 16.0756 | 0.14307
2025-05-19 14:45 | 536 | Remove | 2025-05-19 | 14:45 | US | GS | - | 21 | g | 0 | 111.5 | 12 | 1194.5 | 55490 | 4:28 | 30.2 | 2.41 m/s | 21.6 | 31.7 | 3.9 m/s | 15.8 |  | 2.41 | m/s |  | 3.9 | m/s | 4.4681 | 0.0099542 | 5.1339 |  | -2 | 21 | 0.021 | 244.4697 | 6.6279 | 5.256 | 0.023496 | 16.0991 | 0.13044
2025-05-19 14:45 | 537 | Remove | 2025-05-19 | 14:45 | US | GS | - | 31 | g | 0 | 111.6 | 11.962 | 1190.1 | 55501 | 4:29 | 30.2 | 2.22 m/s | 21.7 | 31.7 | 3.73 m/s | 15.7 |  | 2.22 | m/s |  | 3.73 | m/s | 4.4764 | 0.0099175 | 5.1438 |  | 10 | 31 | 0.031 | 165.9284 | 6.6586 | 5.2227 | 0.021744 | 16.1208 | 0.1923
2025-05-19 14:46 | 538 | Remove | 2025-05-19 | 14:46 | ST | GS | - | 24 | g | 0 | 111.6 | 11.994 | 1194 | 55510 | 4:29 | 30.1 | 2.52 m/s | 21 | 31.7 | 4.15 m/s | 15.7 |  | 2.52 | m/s |  | 4.15 | m/s | 4.4847 | 0.00995 | 5.1537 |  | -7 | 24 | 0.024 | 214.7388 | 6.409 | 5.2227 | 0.023757 | 16.1446 | 0.14866
2025-05-19 14:46 | 539 | Remove | 2025-05-19 | 14:46 | ST | GS | - | 24 | g | 0 | 111.5 | 11.968 | 1190.5 | 55520 | 4:30 | 30.2 | 2.18 m/s | 21.3 | 31.7 | 3.93 m/s | 16.7 |  | 2.18 | m/s |  | 3.93 | m/s | 4.4931 | 0.0099208 | 5.1637 |  | 0 | 24 | 0.024 | 215.1522 | 6.5359 | 5.5553 | 0.020959 | 16.1655 | 0.14846
2025-05-19 14:47 | 540 | Remove | 2025-05-19 | 14:47 | US | GS | - | 27.5 | g | 0 | 111.5 | 11.983 | 1191.9 | 55530 | 4:30 | 30.2 | 2.12 m/s | 24.4 | 31.7 | 3.88 m/s | 17.4 |  | 2.12 | m/s |  | 3.88 | m/s | 4.5014 | 0.0099325 | 5.1736 |  | 3.5 | 27.5 | 0.0275 | 188.1304 | 7.4871 | 5.7882 | 0.023348 | 16.1889 | 0.16987
2025-05-19 14:47 | 541 | Keep | 2025-05-19 | 14:47 | US | GS | - | 23.5 | g | 0 | 111.6 | 11.96 | 1190 | 55540 | 4:31 | 30.2 | 2.18 m/s | 23.1 | 31.7 | 4.18 m/s | 17.5 |  | 2.18 | m/s |  | 4.18 | m/s | 4.5097 | 0.0099167 | 5.1835 |  | -4 | 23.5 | 0.0235 | 220.5745 | 7.0882 | 5.8215 | 0.02273 | 16.2116 | 0.14496
2025-05-19 14:48 | 542 | Remove | 2025-05-19 | 14:48 | ST | GS | - | 22.5 | g | 0 | 111.6 | 11.958 | 1190 | 55550 | 4:31 | 30.2 | 2.57 m/s | 22.5 | 31.7 | 3.92 m/s | 17.9 |  | 2.57 | m/s |  | 3.92 | m/s | 4.5181 | 0.0099167 | 5.1934 |  | -1 | 22.5 | 0.0225 | 230.8186 | 6.9041 | 5.9545 | 0.0261 | 16.2377 | 0.13857
2025-05-19 14:48 | 543 | Remove | 2025-05-19 | 14:48 | ST | GS | - | 24.5 | g | 0 | 111.5 | 11.99 | 1192.5 | 55560 | 4:32 | 30.1 | 2.27 m/s | 23.3 | 31.7 | 3.96 m/s | 17.2 |  | 2.27 | m/s |  | 3.96 | m/s | 4.5264 | 0.0099375 | 5.2034 |  | 2 | 24.5 | 0.0245 | 212.3819 | 7.111 | 5.7217 | 0.023744 | 16.2614 | 0.15066
2025-05-19 14:49 | 544 | Remove | 2025-05-19 | 14:49 | US | GS | - | 25.5 | g | 0 | 111.6 | 11.961 | 1189.9 | 55570 | 4:32 | 30.1 | 2.34 m/s | 21.7 | 31.7 | 3.84 m/s | 16.2 |  | 2.34 | m/s |  | 3.84 | m/s | 4.5347 | 0.0099158 | 5.2133 |  | 1 | 25.5 | 0.0255 | 204.442 | 6.6226 | 5.389 | 0.022796 | 16.2842 | 0.15659
2025-05-19 14:49 | 545 | Remove | 2025-05-19 | 14:49 | US | GS | - | 32 | g | 0 | 111.6 | 11.966 | 1190.8 | 55580 | 4:33 | 30.1 | 2.52 m/s | 21.5 | 31.7 | 3.85 m/s | 16.2 |  | 2.52 | m/s |  | 3.85 | m/s | 4.5431 | 0.0099233 | 5.2232 |  | 6.5 | 32 | 0.032 | 163.2248 | 6.5616 | 5.389 | 0.024323 | 16.3086 | 0.19622
2025-05-19 14:50 | 546 | Remove | 2025-05-19 | 14:50 | ST | GS | - | 26 | g | 0 | 111.6 | 11.964 | 1190.7 | 55590 | 4:33 | 30.2 | 2.22 m/s | 22 | 31.7 | 4.04 m/s | 16.6 |  | 2.22 | m/s |  | 4.04 | m/s | 4.5514 | 0.0099225 | 5.2331 |  | -6 | 26 | 0.026 | 201.2738 | 6.7507 | 5.5221 | 0.022045 | 16.3306 | 0.15921
2025-05-19 14:50 | 547 | Remove | 2025-05-19 | 14:50 | ST | GS | - | 24.5 | g | 0 | 111.6 | 11.954 | 1188.9 | 55600 | 4:34 | 30.2 | 2.35 m/s | 20.9 | 31.7 | 4.04 m/s | 15.9 |  | 2.35 | m/s |  | 4.04 | m/s | 4.5597 | 0.0099075 | 5.243 |  | -1.5 | 24.5 | 0.0245 | 214.001 | 6.4131 | 5.2892 | 0.022169 | 16.3528 | 0.14982
2025-05-19 14:51 | 548 | Remove | 2025-05-19 | 14:51 | US | GS | - | 21.5 | g | 0 | 111.5 | 11.993 | 1192.8 | 55610 | 4:34 | 30.2 | 2.16 m/s | 22.2 | 31.7 | 4.12 m/s | 17.4 |  | 2.16 | m/s |  | 4.12 | m/s | 4.5681 | 0.00994 | 5.253 |  | -3 | 21.5 | 0.0215 | 244.324 | 6.812 | 5.7882 | 0.021644 | 16.3744 | 0.1313
2025-05-19 14:51 | 549 | Remove | 2025-05-19 | 14:51 | ST | GS | - | 24.5 | g | 0 | 111.6 | 11.992 | 1192.4 | 55620 | 4:35 | 30.2 | 2.06 m/s | 20.9 | 31.7 | 4.06 m/s | 15.8 |  | 2.06 | m/s |  | 4.06 | m/s | 4.5764 | 0.0099367 | 5.2629 |  | 3 | 24.5 | 0.0245 | 214.8123 | 6.4131 | 5.256 | 0.019433 | 16.3939 | 0.14945
2025-05-19 14:52 | 550 | Remove | 2025-05-19 | 14:52 | ST | GS | - | 25.5 | g | 0 | 111.5 | 11.967 | 1189.8 | 55630 | 4:35 | 30.2 | 2.54 m/s | 20.6 | 31.7 | 3.79 m/s | 16.7 |  | 2.54 | m/s |  | 3.79 | m/s | 4.5847 | 0.009915 | 5.2728 |  | 1 | 25.5 | 0.0255 | 206.7771 | 6.3211 | 5.5553 | 0.023617 | 16.4175 | 0.15532
2025-05-19 14:52 | 551 | Remove | 2025-05-19 | 14:52 | US | GS | - | 29.5 | g | 0 | 111.5 | 11.956 | 1188.8 | 55640 | 4:36 | 30.2 | 2.67 m/s | 22.3 | 31.7 | 3.85 m/s | 16.6 |  | 2.67 | m/s |  | 3.85 | m/s | 4.5933 | 0.0099067 | 5.2827 |  | 4 | 29.5 | 0.0295 | 179.0754 | 6.8427 | 5.5221 | 0.026875 | 16.4443 | 0.17939
2025-05-19 14:53 | 552 | Remove | 2025-05-19 | 14:53 | ST | GS | - | 24 | g | 0 | 111.5 | 11.963 | 1188.8 | 55650 | 4:36 | 30.2 | 2.96 m/s | 21.7 | 31.7 | 4.12 m/s | 15.7 |  | 2.96 | m/s |  | 4.12 | m/s | 4.6017 | 0.0099067 | 5.2926 |  | -5.5 | 24 | 0.024 | 220.5263 | 6.6586 | 5.2227 | 0.028992 | 16.4733 | 0.14569
2025-05-19 14:53 | 553 | Remove | 2025-05-19 | 14:53 | ST | GS | - | 27.5 | g | 0 | 111.5 | 11.942 | 1187.3 | 55660 | 4:37 | 30.1 | 2.86 m/s | 21.6 | 31.7 | 4.06 m/s | 16.6 |  | 2.86 | m/s |  | 4.06 | m/s | 4.61 | 0.0098942 | 5.3025 |  | 3.5 | 27.5 | 0.0275 | 192.8191 | 6.5921 | 5.5221 | 0.027733 | 16.5011 | 0.16666
2025-05-19 14:54 | 554 | Remove | 2025-05-19 | 14:54 | ST | GS | - | 26 | g | 0 | 111.5 | 11.982 | 1191.9 | 55670 | 4:37 | 30.1 | 2.38 m/s | 22.1 | 31.7 | 3.81 m/s | 16.4 |  | 2.38 | m/s |  | 3.81 | m/s | 4.6183 | 0.0099325 | 5.3125 |  | -1.5 | 26 | 0.026 | 204.3253 | 6.7447 | 5.4555 | 0.023613 | 16.5247 | 0.15734
2025-05-19 14:54 | 555 | Remove | 2025-05-19 | 14:54 | US | GS | - | 31.5 | g | 0 | 111.4 | 11.953 | 1188.6 | 55680 | 4:38 | 30.2 | 2.45 m/s | 22.5 | 31.6 | 3.94 m/s | 17.7 |  | 2.45 | m/s |  | 3.94 | m/s | 4.6267 | 0.009905 | 5.3224 |  | 5.5 | 31.5 | 0.0315 | 168.9639 | 6.9041 | 5.8566 | 0.024881 | 16.5496 | 0.19034
2025-05-19 14:55 | 556 | Remove | 2025-05-19 | 14:55 | US | GS | - | 33 | g | 0 | 111.4 | 11.977 | 1191 | 55690 | 4:38 | 30.2 | 2.35 m/s | 23.7 | 31.6 | 3.9 m/s | 17.3 |  | 2.35 | m/s |  | 3.9 | m/s | 4.635 | 0.009925 | 5.3323 |  | 1.5 | 33 | 0.033 | 161.5844 | 7.2723 | 5.7242 | 0.025139 | 16.5747 | 0.1991
2025-05-19 14:55 | 557 | Remove | 2025-05-19 | 14:55 | ST | GS | - | 25 | g | 0 | 111.5 | 11.967 | 1190.1 | 55700 | 4:39 | 30.2 | 2.21 m/s | 22.1 | 31.6 | 4.01 m/s | 17.6 |  | 2.21 | m/s |  | 4.01 | m/s | 4.6433 | 0.0099175 | 5.3422 |  | -8 | 25 | 0.025 | 213.6882 | 6.7814 | 5.8235 | 0.022045 | 16.5968 | 0.15063
2025-05-19 14:56 | 558 | Remove | 2025-05-19 | 14:56 | ST | GS | - | 26 | g | 0 | 111.5 | 11.961 | 1188.6 | 55709 | 4:39 | 30.2 | 3.08 m/s | 21.8 | 31.6 | 3.72 m/s | 16.7 |  | 3.08 | m/s |  | 3.72 | m/s | 4.6517 | 0.009905 | 5.3521 |  | 1 | 26 | 0.026 | 205.8504 | 6.6893 | 5.5257 | 0.030306 | 16.6271 | 0.15637
2025-05-19 14:56 | 559 | Remove | 2025-05-19 | 14:56 | ST | GS | - | 27 | g | 0 | 111.3 | 11.98 | 1190.5 | 55719 | 4:40 | 30.1 | 2.62 m/s | 22 | 31.6 | 4.01 m/s | 15.8 |  | 2.62 | m/s |  | 4.01 | m/s | 4.66 | 0.0099208 | 5.362 |  | 1 | 27 | 0.027 | 198.5937 | 6.7142 | 5.2279 | 0.025876 | 16.6529 | 0.16213
2025-05-19 14:57 | 560 | Remove | 2025-05-19 | 14:57 | ST | GS | - | 27 | g | 0 | 111.4 | 11.938 | 1185.5 | 55729 | 4:40 | 30.1 | 2.12 m/s | 23.5 | 31.6 | 4.0 m/s | 18.9 |  | 2.12 | m/s |  | 4 | m/s | 4.6683 | 0.0098792 | 5.3719 |  | 0 | 27 | 0.027 | 198.9596 | 7.172 | 6.2536 | 0.022365 | 16.6753 | 0.16192
2025-05-19 14:57 | 561 | Remove | 2025-05-19 | 14:57 | ST | GS | - | 25.5 | g | 0 | 111.4 | 11.975 | 1190.8 | 55739 | 4:41 | 30.1 | 2.27 m/s | 24.4 | 31.6 | 4.2 m/s | 17 |  | 2.27 | m/s |  | 4.2 | m/s | 4.6767 | 0.0099233 | 5.3818 |  | -1.5 | 25.5 | 0.0255 | 211.0523 | 7.4467 | 5.6249 | 0.024865 | 16.7002 | 0.15269
2025-05-19 14:58 | 562 | Remove | 2025-05-19 | 14:58 | US | GS | - | 27.5 | g | 0 | 111.3 | 11.984 | 1191.8 | 55749 | 4:41 | 30.1 | 2.11 m/s | 23.5 | 31.6 | 3.92 m/s | 17.7 |  | 2.11 | m/s |  | 3.92 | m/s | 4.685 | 0.0099317 | 5.3918 |  | 2 | 27.5 | 0.0275 | 196.0642 | 7.172 | 5.8566 | 0.02226 | 16.7224 | 0.16445
2025-05-19 14:58 | 563 | Remove | 2025-05-19 | 14:58 | ST | GS | - | 26 | g | 0 | 111.3 | 11.981 | 1191 | 55759 | 4:42 | 30.2 | 2.27 m/s | 20.7 | 31.6 | 3.75 m/s | 16.1 |  | 2.27 | m/s |  | 3.75 | m/s | 4.6933 | 0.009925 | 5.4017 |  | -1.5 | 26 | 0.026 | 207.7573 | 6.3518 | 5.3271 | 0.021209 | 16.7436 | 0.15528
2025-05-19 14:59 | 564 | Remove | 2025-05-19 | 14:59 | ST | GS | - | 28 | g | 0 | 111.3 | 11.986 | 1191.3 | 55769 | 4:42 | 30.2 | 2.48 m/s | 21.7 | 31.6 | 3.77 m/s | 15.9 |  | 2.48 | m/s |  | 3.77 | m/s | 4.7017 | 0.0099275 | 5.4116 |  | 2 | 28 | 0.028 | 193.272 | 6.6586 | 5.261 | 0.024291 | 16.7679 | 0.16699
2025-05-19 14:59 | 565 | Remove | 2025-05-19 | 14:59 | ST | GS | - | 26 | g | 0 | 111.3 | 11.999 | 1193.5 | 55779 | 4:43 | 30.2 | 2.08 m/s | 21.1 | 31.6 | 4.2 m/s | 16.7 |  | 2.08 | m/s |  | 4.2 | m/s | 4.71 | 0.0099458 | 5.4216 |  | -2 | 26 | 0.026 | 208.5216 | 6.4745 | 5.5257 | 0.019809 | 16.7877 | 0.15487
2025-05-19 15:00 | 566 | Remove | 2025-05-19 | 15:00 | US | GS | - | 29.5 | g | 0 | 111.3 | 12.014 | 1194.5 | 55789 | 4:43 | 30.2 | 2.37 m/s | 20.2 | 31.6 | 3.97 m/s | 16.3 |  | 2.37 | m/s |  | 3.97 | m/s | 4.7183 | 0.0099542 | 5.4315 |  | 3.5 | 29.5 | 0.0295 | 184.1192 | 6.1983 | 5.3933 | 0.021609 | 16.8093 | 0.1755
2025-05-19 15:00 | 567 | Remove | 2025-05-19 | 15:00 | US | GS | - | 25.5 | g | 0 | 111.3 | 11.994 | 1192.9 | 55799 | 4:44 | 30.2 | 2.19 m/s | 21.6 | 31.6 | 3.88 m/s | 15.6 |  | 2.19 | m/s |  | 3.88 | m/s | 4.7267 | 0.0099408 | 5.4415 |  | -4 | 25.5 | 0.0255 | 213.3905 | 6.6279 | 5.1617 | 0.021351 | 16.8307 | 0.15151
2025-05-19 15:01 | 568 | Remove | 2025-05-19 | 15:01 | ST | GS | - | 26.5 | g | 0 | 111.3 | 12.03 | 1197.6 | 55809 | 4:44 | 30.2 | 2.23 m/s | 22.1 | 31.7 | 4.35 m/s | 16.9 |  | 2.23 | m/s |  | 4.35 | m/s | 4.7353 | 0.00998 | 5.4514 |  | 1 | 26.5 | 0.0265 | 205.7146 | 6.7814 | 5.6219 | 0.022245 | 16.8529 | 0.15724
2025-05-19 15:01 | 569 | Remove | 2025-05-19 | 15:01 | US | GS | - | 29 | g | 0 | 111.3 | 12.028 | 1196.2 | 55819 | 4:45 | 30.2 | 2.02 m/s | 21.9 | 31.7 | 3.88 m/s | 15.7 |  | 2.02 | m/s |  | 3.88 | m/s | 4.7436 | 0.0099683 | 5.4614 |  | 2.5 | 29 | 0.029 | 188.3243 | 6.72 | 5.2227 | 0.019967 | 16.8729 | 0.17187
2025-05-19 15:02 | 570 | Remove | 2025-05-19 | 15:02 | ST | GS | - | 25.5 | g | 0 | 111.3 | 11.991 | 1192.8 | 55829 | 4:45 | 30.3 | 2.65 m/s | 21.8 | 31.7 | 3.89 m/s | 16.3 |  | 2.65 | m/s |  | 3.89 | m/s | 4.7519 | 0.00994 | 5.4713 |  | -3.5 | 25.5 | 0.0255 | 214.5626 | 6.7256 | 5.4223 | 0.026217 | 16.8991 | 0.1509
2025-05-19 15:02 | 571 | Keep | 2025-05-19 | 15:02 | ST | GS | - | 26 | g | 0 | 111.5 | 11.981 | 1191.9 | 55839 | 4:46 | 30.2 | 2.77 m/s | 21.1 | 31.7 | 3.97 m/s | 16.1 |  | 2.77 | m/s |  | 3.97 | m/s | 4.7603 | 0.0099325 | 5.4813 |  | 0.5 | 26 | 0.026 | 210.8184 | 6.4745 | 5.3557 | 0.026381 | 16.9255 | 0.15361
2025-05-19 15:03 | 572 | Remove | 2025-05-19 | 15:03 | ST | GS | - | 29 | g | 0 | 111.4 | 11.935 | 1186.4 | 55849 | 4:46 | 30.2 | 2.25 m/s | 21.4 | 31.7 | 4.13 m/s | 16.1 |  | 2.25 | m/s |  | 4.13 | m/s | 4.7686 | 0.0098867 | 5.4912 |  | 3 | 29 | 0.029 | 189.3505 | 6.5666 | 5.3557 | 0.021733 | 16.9472 | 0.17112
2025-05-19 15:03 | 573 | Remove | 2025-05-19 | 15:03 | US | GS | - | 26.5 | g | 0 | 111.4 | 11.989 | 1191.7 | 55859 | 4:47 | 30.2 | 2.23 m/s | 21.8 | 31.7 | 3.96 m/s | 15.6 |  | 2.23 | m/s |  | 3.96 | m/s | 4.7769 | 0.0099308 | 5.5011 |  | -2.5 | 26.5 | 0.0265 | 207.5885 | 6.6893 | 5.1894 | 0.021943 | 16.9692 | 0.15617
2025-05-19 15:04 | 574 | Remove | 2025-05-19 | 15:04 | US | GS | - | 31 | g | 0 | 111.3 | 11.996 | 1192.5 | 55869 | 4:47 | 30.2 | 2.45 m/s | 21.4 | 31.7 | 4.15 m/s | 15.5 |  | 2.45 | m/s |  | 4.15 | m/s | 4.7853 | 0.0099375 | 5.511 |  | 4.5 | 31 | 0.031 | 177.7753 | 6.5666 | 5.1562 | 0.023665 | 16.9928 | 0.18243
2025-05-19 15:04 | 575 | Remove | 2025-05-19 | 15:04 | ST | GS | - | 27.5 | g | 0 | 111.2 | 12.031 | 1195.8 | 55879 | 4:48 | 30.2 | 2.05 m/s | 22.3 | 31.7 | 4.5 m/s | 16.4 |  | 2.05 | m/s |  | 4.5 | m/s | 4.7936 | 0.009965 | 5.521 |  | -3.5 | 27.5 | 0.0275 | 200.7636 | 6.8427 | 5.4555 | 0.020634 | 17.0135 | 0.16164
2025-05-19 15:05 | 576 | Remove | 2025-05-19 | 15:05 | US | GS | - | 29.5 | g | 0 | 111.3 | 11.999 | 1192.7 | 55889 | 4:48 | 30.2 | 2.18 m/s | 22.2 | 31.7 | 3.79 m/s | 16.8 |  | 2.18 | m/s |  | 3.79 | m/s | 4.8019 | 0.0099392 | 5.5309 |  | 2 | 29.5 | 0.0295 | 187.4894 | 6.812 | 5.5886 | 0.021844 | 17.0353 | 0.17317
2025-05-19 15:05 | 577 | Remove | 2025-05-19 | 15:05 | US | GS | - | 24.5 | g | 0 | 111.3 | 12.001 | 1193.2 | 55899 | 4:49 | 30.2 | 2.42 m/s | 20.7 | 31.7 | 3.75 m/s | 15.7 |  | 2.42 | m/s |  | 3.75 | m/s | 4.8103 | 0.0099433 | 5.5409 |  | -5 | 24.5 | 0.0245 | 226.1584 | 6.3518 | 5.2227 | 0.022611 | 17.0579 | 0.14363
2025-05-19 15:06 | 578 | Remove | 2025-05-19 | 15:06 | US | GS | - | 30 | g | 0 | 111.3 | 11.981 | 1191.2 | 55909 | 4:49 | 30.2 | 2.38 m/s | 20.9 | 31.7 | 3.93 m/s | 15.9 |  | 2.38 | m/s |  | 3.93 | m/s | 4.8186 | 0.0099267 | 5.5508 |  | 5.5 | 30 | 0.03 | 185.0269 | 6.4131 | 5.2892 | 0.022452 | 17.0804 | 0.17564
2025-05-19 15:06 | 579 | Remove | 2025-05-19 | 15:06 | ST | GS | - | 28 | g | 0 | 111.3 | 11.936 | 1184.8 | 55919 | 4:50 | 30.3 | 2.52 m/s | 22.5 | 31.7 | 4.43 m/s | 17.3 |  | 2.52 | m/s |  | 4.43 | m/s | 4.8269 | 0.0098733 | 5.5607 |  | -2 | 28 | 0.028 | 198.5957 | 6.9416 | 5.7549 | 0.025731 | 17.1061 | 0.16368
2025-05-19 15:07 | 580 | Remove | 2025-05-19 | 15:07 | US | GS | - | 32 | g | 0 | 111.3 | 11.981 | 1190.2 | 55929 | 4:50 | 30.2 | 2.61 m/s | 25.2 | 31.7 | 4.55 m/s | 18.7 |  | 2.61 | m/s |  | 4.55 | m/s | 4.8353 | 0.0099183 | 5.5706 |  | 4 | 32 | 0.032 | 174.0812 | 7.7326 | 6.2207 | 0.029687 | 17.1358 | 0.18674
2025-05-19 15:07 | 581 | Remove | 2025-05-19 | 15:07 | ST | GS | - | 31 | g | 0 | 111.3 | 11.945 | 1187 | 55939 | 4:51 | 30.2 | 2.26 m/s | 20.9 | 31.7 | 3.79 m/s | 15.4 |  | 2.26 | m/s |  | 3.79 | m/s | 4.8436 | 0.0098917 | 5.5805 |  | -1 | 31 | 0.031 | 180.0158 | 6.4131 | 5.1229 | 0.02132 | 17.1571 | 0.18068
2025-05-19 15:08 | 582 | Remove | 2025-05-19 | 15:08 | ST | GS | - | 28.5 | g | 0 | 111.2 | 12 | 1192.1 | 55949 | 4:51 | 30.2 | 2.02 m/s | 21.6 | 31.7 | 4.91 m/s | 16.8 |  | 2.02 | m/s |  | 4.91 | m/s | 4.8519 | 0.0099342 | 5.5904 |  | -2.5 | 28.5 | 0.0285 | 196.1553 | 6.6279 | 5.5886 | 0.019694 | 17.1768 | 0.16592
2025-05-19 15:08 | 583 | Remove | 2025-05-19 | 15:08 | ST | GS | - | 26.5 | g | 0 | 111.3 | 12 | 1192.6 | 55959 | 4:52 | 30.3 | 2.38 m/s | 25 | 31.7 | 3.85 m/s | 17.2 |  | 2.38 | m/s |  | 3.85 | m/s | 4.8603 | 0.0099383 | 5.6004 |  | -2 | 26.5 | 0.0265 | 211.3345 | 7.7128 | 5.7217 | 0.027002 | 17.2038 | 0.15404
2025-05-19 15:09 | 584 | Remove | 2025-05-19 | 15:09 | ST | GS | - | 28.5 | g | 0 | 111.3 | 11.999 | 1193.3 | 55968 | 4:52 | 30.2 | 2.25 m/s | 20.9 | 31.7 | 3.88 m/s | 15 |  | 2.25 | m/s |  | 3.88 | m/s | 4.8686 | 0.0099442 | 5.6103 |  | 2 | 28.5 | 0.0285 | 196.8529 | 6.4131 | 4.9898 | 0.021225 | 17.225 | 0.16546
2025-05-19 15:09 | 585 | Remove | 2025-05-19 | 15:09 | US | GS | - | 31 | g | 0 | 111.2 | 11.995 | 1192.5 | 55978 | 4:53 | 30.3 | 1.97 m/s | 22.3 | 31.7 | 3.67 m/s | 16 |  | 1.97 | m/s |  | 3.67 | m/s | 4.8772 | 0.0099375 | 5.6202 |  | 2.5 | 31 | 0.031 | 181.2982 | 6.8799 | 5.3225 | 0.019936 | 17.245 | 0.17976
2025-05-19 15:10 | 586 | Remove | 2025-05-19 | 15:10 | ST | GS | - | 28 | g | 0 | 111.2 | 12.038 | 1197 | 55988 | 4:53 | 30.3 | 2.57 m/s | 21.3 | 31.7 | 4.5 m/s | 15.8 |  | 2.57 | m/s |  | 4.5 | m/s | 4.8856 | 0.009975 | 5.6302 |  | -3 | 28 | 0.028 | 201.0793 | 6.5713 | 5.256 | 0.024842 | 17.2698 | 0.16213
2025-05-19 15:10 | 587 | Remove | 2025-05-19 | 15:10 | ST | GS | - | 28 | g | 0 | 111.2 | 12.026 | 1195.3 | 55998 | 4:54 | 30.3 | 2.15 m/s | 22.6 | 31.7 | 4.32 m/s | 16.6 |  | 2.15 | m/s |  | 4.32 | m/s | 4.8939 | 0.0099608 | 5.6402 |  | 0 | 28 | 0.028 | 201.435 | 6.9724 | 5.5221 | 0.022051 | 17.2919 | 0.16193
2025-05-19 15:11 | 588 | Remove | 2025-05-19 | 15:11 | ST | GS | - | 27 | g | 0 | 111.1 | 12.037 | 1196 | 56008 | 4:54 | 30.3 | 2.11 m/s | 21.1 | 31.7 | 4.58 m/s | 16.6 |  | 2.11 | m/s |  | 4.58 | m/s | 4.9022 | 0.0099667 | 5.6501 |  | -1 | 27 | 0.027 | 209.2647 | 6.5096 | 5.5221 | 0.020204 | 17.3121 | 0.15596
2025-05-19 15:11 | 589 | Remove | 2025-05-19 | 15:11 | ST | GS | - | 28.5 | g | 0 | 111.1 | 12.012 | 1193.5 | 56018 | 4:55 | 30.3 | 2.31 m/s | 22 | 31.7 | 4.35 m/s | 16 |  | 2.31 | m/s |  | 4.35 | m/s | 4.9106 | 0.0099458 | 5.6601 |  | 1.5 | 28.5 | 0.0285 | 198.5998 | 6.7873 | 5.3225 | 0.023063 | 17.3351 | 0.16441
2025-05-19 15:12 | 590 | Remove | 2025-05-19 | 15:12 | US | GS | - | 32 | g | 0 | 111.2 | 11.968 | 1188.8 | 56028 | 4:55 | 30.3 | 2.68 m/s | 21.4 | 31.7 | 4.21 m/s | 16.1 |  | 2.68 | m/s |  | 4.21 | m/s | 4.9189 | 0.0099067 | 5.67 |  | 3.5 | 32 | 0.032 | 177.1875 | 6.6022 | 5.3557 | 0.026027 | 17.3612 | 0.18432
2025-05-19 15:12 | 591 | Remove | 2025-05-19 | 15:12 | ST | GS | - | 29.5 | g | 0 | 111.2 | 12.004 | 1193.3 | 56038 | 4:56 | 30.3 | 2.31 m/s | 20.9 | 31.7 | 4.26 m/s | 15.6 |  | 2.31 | m/s |  | 4.26 | m/s | 4.9272 | 0.0099442 | 5.6799 |  | -2.5 | 29.5 | 0.0295 | 192.5405 | 6.4479 | 5.1894 | 0.02191 | 17.3831 | 0.16971
2025-05-19 15:13 | 592 | Remove | 2025-05-19 | 15:13 | ST | GS | - | 29.5 | g | 0 | 111.2 | 12.004 | 1192.6 | 56048 | 4:56 | 30.3 | 2.06 m/s | 20.9 | 31.7 | 4.53 m/s | 15.6 |  | 2.06 | m/s |  | 4.53 | m/s | 4.9356 | 0.0099383 | 5.6899 |  | 0 | 29.5 | 0.0295 | 192.8774 | 6.4479 | 5.1894 | 0.019538 | 17.4026 | 0.16951
2025-05-19 15:13 | 593 | Remove | 2025-05-19 | 15:13 | US | GS | - | 37 | g | 0 | 111.2 | 12.017 | 1194.6 | 56058 | 4:57 | 30.3 | 2.81 m/s | 21.5 | 31.7 | 3.98 m/s | 16 |  | 2.81 | m/s |  | 3.98 | m/s | 4.9439 | 0.009955 | 5.6998 |  | 7.5 | 37 | 0.037 | 154.0497 | 6.633 | 5.3225 | 0.027417 | 17.43 | 0.21228
2025-05-19 15:14 | 594 | Remove | 2025-05-19 | 15:14 | ST | GS | - | 29 | g | 0 | 111.2 | 11.984 | 1191.3 | 56068 | 4:57 | 30.3 | 2.44 m/s | 21.2 | 31.7 | 3.9 m/s | 15.9 |  | 2.44 | m/s |  | 3.9 | m/s | 4.9522 | 0.0099275 | 5.7098 |  | -8 | 29 | 0.029 | 196.8884 | 6.5405 | 5.2892 | 0.023475 | 17.4535 | 0.16616
2025-05-19 15:14 | 595 | Remove | 2025-05-19 | 15:14 | US | GS | - | 27.5 | g | 0 | 111.2 | 12.01 | 1193.7 | 56078 | 4:58 | 30.3 | 2.13 m/s | 20.8 | 31.7 | 4.2 m/s | 15.9 |  | 2.13 | m/s |  | 4.2 | m/s | 4.9606 | 0.0099475 | 5.7197 |  | -1.5 | 27.5 | 0.0275 | 207.9895 | 6.4171 | 5.2892 | 0.020106 | 17.4736 | 0.15738
2025-05-19 15:15 | 596 | Remove | 2025-05-19 | 15:15 | ST | GS | - | 29.5 | g | 0 | 111.2 | 12.003 | 1192.2 | 56088 | 4:58 | 30.3 | 2.31 m/s | 21.4 | 31.7 | 3.92 m/s | 15.9 |  | 2.31 | m/s |  | 3.92 | m/s | 4.9689 | 0.009935 | 5.7296 |  | 2 | 29.5 | 0.0295 | 194.2253 | 6.6022 | 5.2892 | 0.022434 | 17.496 | 0.16861
2025-05-19 15:15 | 597 | Remove | 2025-05-19 | 15:15 | ST | GS | - | 30.5 | g | 0 | 111.3 | 12.023 | 1195.6 | 56098 | 4:59 | 30.3 | 2.26 m/s | 21.5 | 31.7 | 4.16 m/s | 15.7 |  | 2.26 | m/s |  | 4.16 | m/s | 4.9772 | 0.0099633 | 5.7396 |  | 1 | 30.5 | 0.0305 | 188.184 | 6.633 | 5.2227 | 0.022051 | 17.5181 | 0.17411
2025-05-19 15:16 | 598 | Remove | 2025-05-19 | 15:16 | US | GS | - | 30 | g | 0 | 111.2 | 12.062 | 1200.1 | 56108 | 4:59 | 30.3 | 2.04 m/s | 21.4 | 31.7 | 4.26 m/s | 16.1 |  | 2.04 | m/s |  | 4.26 | m/s | 4.9856 | 0.010001 | 5.7496 |  | -0.5 | 30 | 0.03 | 191.6537 | 6.6022 | 5.3557 | 0.019812 | 17.5379 | 0.17106
2025-05-19 15:16 | 599 | Remove | 2025-05-19 | 15:16 | US | GS | - | 28.5 | g | 0 | 111.3 | 12.017 | 1194.5 | 56118 | 5:00 | 30.3 | 2.15 m/s | 21.5 | 31.7 | 3.94 m/s | 16.3 |  | 2.15 | m/s |  | 3.94 | m/s | 4.9939 | 0.0099542 | 5.7596 |  | -1.5 | 28.5 | 0.0285 | 202.09 | 6.633 | 5.4223 | 0.020977 | 17.5589 | 0.16231
2025-05-19 15:17 | 600 | Remove | 2025-05-19 | 15:17 | ST | GS | - | 31.5 | g | 0 | 111.2 | 12.048 | 1198.4 | 56128 | 5:00 | 30.4 | 1.87 m/s | 23.1 | 31.7 | 4.03 m/s | 17.3 |  | 1.87 | m/s |  | 4.03 | m/s | 5.0022 | 0.0099867 | 5.7696 |  | 3 | 31.5 | 0.0315 | 183.1604 | 7.1653 | 5.7549 | 0.01971 | 17.5786 | 0.1792
2025-05-19 15:17 | 601 | Keep | 2025-05-19 | 15:17 | US | GS | - | 28 | g | 0 | 111.1 | 12.042 | 1197.1 | 56138 | 5:01 | 30.4 | 2.57 m/s | 22.5 | 31.7 | 3.93 m/s | 18.2 |  | 2.57 | m/s |  | 3.93 | m/s | 5.0106 | 0.0099758 | 5.7795 |  | -3.5 | 28 | 0.028 | 206.4117 | 6.9792 | 6.0543 | 0.026384 | 17.605 | 0.15905
2025-05-19 15:18 | 602 | Remove | 2025-05-19 | 15:18 | US | GS | - | 31 | g | 0 | 111.2 | 12.049 | 1199.1 | 56148 | 5:01 | 30.4 | 2.38 m/s | 21.4 | 31.6 | 3.8 m/s | 16.5 |  | 2.38 | m/s |  | 3.8 | m/s | 5.0192 | 0.0099925 | 5.7895 |  | 3 | 31 | 0.031 | 186.7587 | 6.638 | 5.4595 | 0.023239 | 17.6282 | 0.17585
2025-05-19 15:18 | 603 | Remove | 2025-05-19 | 15:18 | ST | GS | - | 31 | g | 0 | 111.2 | 12.024 | 1195.5 | 56158 | 5:02 | 30.4 | 2.25 m/s | 20.7 | 31.6 | 3.88 m/s | 15.5 |  | 2.25 | m/s |  | 3.88 | m/s | 5.0275 | 0.0099625 | 5.7995 |  | 0 | 31 | 0.031 | 187.0801 | 6.4209 | 5.1286 | 0.021251 | 17.6495 | 0.17564
2025-05-19 15:19 | 604 | Remove | 2025-05-19 | 15:19 | US | GS | - | 30 | g | 0 | 111.2 | 12.015 | 1194.6 | 56168 | 5:02 | 30.4 | 2.33 m/s | 20.6 | 31.6 | 3.71 m/s | 15.9 |  | 2.33 | m/s |  | 3.71 | m/s | 5.0358 | 0.009955 | 5.8094 |  | -1 | 30 | 0.03 | 193.6479 | 6.3898 | 5.261 | 0.0219 | 17.6714 | 0.16977
2025-05-19 15:19 | 605 | Remove | 2025-05-19 | 15:19 | ST | GS | - | 30 | g | 0 | 111.2 | 12.041 | 1196.8 | 56178 | 5:03 | 30.3 | 2.34 m/s | 21.1 | 31.6 | 3.98 m/s | 16 |  | 2.34 | m/s |  | 3.98 | m/s | 5.0442 | 0.0099733 | 5.8194 |  | 0 | 30 | 0.03 | 193.9804 | 6.5096 | 5.2941 | 0.022407 | 17.6938 | 0.16955
2025-05-19 15:20 | 606 | Remove | 2025-05-19 | 15:20 | ST | GS | - | 31 | g | 0 | 111.1 | 12.041 | 1196.6 | 56188 | 5:03 | 30.3 | 2.72 m/s | 21.6 | 31.5 | 3.52 m/s | 15.8 |  | 2.72 | m/s |  | 3.52 | m/s | 5.0525 | 0.0099717 | 5.8294 |  | 1 | 31 | 0.031 | 188.0446 | 6.6639 | 5.1999 | 0.026662 | 17.7204 | 0.17494
2025-05-19 15:20 | 607 | Remove | 2025-05-19 | 15:20 | US | GS | - | 42.5 | g | 0 | 111 | 12.074 | 1200.3 | 56198 | 5:04 | 30.3 | 2.35 m/s | 21.4 | 31.5 | 3.85 m/s | 17 |  | 2.35 | m/s |  | 3.85 | m/s | 5.0608 | 0.010002 | 5.8394 |  | 11.5 | 42.5 | 0.0425 | 137.3973 | 6.6022 | 5.5949 | 0.022822 | 17.7433 | 0.23953
2025-05-19 15:21 | 608 | Remove | 2025-05-19 | 15:21 | ST | GS | - | 30.5 | g | 0 | 111 | 12.053 | 1197.6 | 56208 | 5:04 | 30.3 | 2.42 m/s | 21 | 31.5 | 3.96 m/s | 17.2 |  | 2.42 | m/s |  | 3.96 | m/s | 5.0692 | 0.00998 | 5.8494 |  | -12 | 30.5 | 0.0305 | 191.7825 | 6.4788 | 5.6607 | 0.023063 | 17.7663 | 0.17167
2025-05-19 15:21 | 609 | Remove | 2025-05-19 | 15:21 | ST | GS | - | 30 | g | 0 | 111.1 | 12.043 | 1196.8 | 56218 | 5:05 | 30.3 | 2.0 m/s | 22.5 | 31.5 | 3.9 m/s | 17.9 |  | 2 | m/s |  | 3.9 | m/s | 5.0775 | 0.0099733 | 5.8593 |  | -0.5 | 30 | 0.03 | 195.3113 | 6.9416 | 5.8911 | 0.020422 | 17.7867 | 0.16866
2025-05-19 15:22 | 610 | Remove | 2025-05-19 | 15:22 | US | GS | - | 31.5 | g | 0 | 111.1 | 12.066 | 1199.9 | 56228 | 5:05 | 30.3 | 2.47 m/s | 21.7 | 31.5 | 4.03 m/s | 18.6 |  | 2.47 | m/s |  | 4.03 | m/s | 5.0858 | 0.0099992 | 5.8693 |  | 1.5 | 31.5 | 0.0315 | 186.3282 | 6.6947 | 6.1214 | 0.024324 | 17.8111 | 0.17686
2025-05-19 15:22 | 611 | Remove | 2025-05-19 | 15:22 | ST | GS | - | 30 | g | 0 | 111.1 | 12.07 | 1199.9 | 56238 | 5:06 | 30.3 | 1.95 m/s | 21.7 | 31.5 | 4.21 m/s | 17.4 |  | 1.95 | m/s |  | 4.21 | m/s | 5.0942 | 0.0099992 | 5.8793 |  | -1.5 | 30 | 0.03 | 195.9779 | 6.6947 | 5.7265 | 0.019203 | 17.8303 | 0.16825
2025-05-19 15:23 | 612 | Remove | 2025-05-19 | 15:23 | US | GS | - | 33.5 | g | 0 | 111 | 12.071 | 1199.9 | 56248 | 5:06 | 30.3 | 2.18 m/s | 20.9 | 31.6 | 3.92 m/s | 16.9 |  | 2.18 | m/s |  | 3.92 | m/s | 5.1025 | 0.0099992 | 5.8893 |  | 3.5 | 33.5 | 0.0335 | 175.8011 | 6.4479 | 5.5918 | 0.020677 | 17.8509 | 0.18767
2025-05-19 15:23 | 613 | Remove | 2025-05-19 | 15:23 | ST | GS | - | 30 | g | 0 | 110.9 | 12.074 | 1200.3 | 56258 | 5:07 | 30.4 | 2.25 m/s | 21.7 | 31.6 | 4.32 m/s | 17 |  | 2.25 | m/s |  | 4.32 | m/s | 5.1108 | 0.010002 | 5.8993 |  | -3.5 | 30 | 0.03 | 196.6446 | 6.7311 | 5.6249 | 0.022278 | 17.8732 | 0.16785
2025-05-19 15:24 | 614 | Remove | 2025-05-19 | 15:24 | ST | GS | - | 33.5 | g | 0 | 111 | 12.02 | 1193.6 | 56268 | 5:07 | 30.3 | 2.15 m/s | 21.2 | 31.6 | 3.76 m/s | 15.6 |  | 2.15 | m/s |  | 3.76 | m/s | 5.1192 | 0.0099467 | 5.9093 |  | 3.5 | 33.5 | 0.0335 | 176.3966 | 6.5405 | 5.1617 | 0.020685 | 17.8939 | 0.18721
2025-05-19 15:24 | 615 | Remove | 2025-05-19 | 15:24 | US | GS | - | 35 | g | 0 | 111.1 | 12.028 | 1195 | 56278 | 5:08 | 30.3 | 2.38 m/s | 22 | 31.6 | 3.76 m/s | 16.2 |  | 2.38 | m/s |  | 3.76 | m/s | 5.1275 | 0.0099583 | 5.9192 |  | 1.5 | 35 | 0.035 | 169.1213 | 6.7873 | 5.3602 | 0.023762 | 17.9177 | 0.19534
2025-05-19 15:25 | 616 | Remove | 2025-05-19 | 15:25 | US | GS | - | 35 | g | 0 | 111 | 12.04 | 1196.5 | 56288 | 5:08 | 30.4 | 2.15 m/s | 24 | 31.6 | 3.89 m/s | 18.1 |  | 2.15 | m/s |  | 3.89 | m/s | 5.1358 | 0.0099708 | 5.9292 |  | 0 | 35 | 0.035 | 169.4061 | 7.4445 | 5.9889 | 0.023544 | 17.9412 | 0.19508
2025-05-19 15:25 | 617 | Remove | 2025-05-19 | 15:25 | ST | GS | - | 33.5 | g | 0 | 111 | 12.011 | 1192.5 | 56298 | 5:09 | 30.3 | 2.22 m/s | 20.6 | 31.5 | 3.69 m/s | 15.9 |  | 2.22 | m/s |  | 3.69 | m/s | 5.1442 | 0.0099375 | 5.9392 |  | -1.5 | 33.5 | 0.0335 | 177.2881 | 6.3554 | 5.2328 | 0.020754 | 17.962 | 0.18651
2025-05-19 15:26 | 618 | Remove | 2025-05-19 | 15:26 | US | GS | - | 34.5 | g | 0 | 111.1 | 12.017 | 1193.8 | 56308 | 5:09 | 30.3 | 2.22 m/s | 20.7 | 31.5 | 3.88 m/s | 15.7 |  | 2.22 | m/s |  | 3.88 | m/s | 5.1525 | 0.0099483 | 5.9491 |  | 1 | 34.5 | 0.0345 | 172.4377 | 6.3862 | 5.167 | 0.020855 | 17.9828 | 0.19185
2025-05-19 15:26 | 619 | Remove | 2025-05-19 | 15:26 | US | GS | - | 31 | g | 0 | 111 | 12.044 | 1197 | 56318 | 5:10 | 30.3 | 2.31 m/s | 20.3 | 31.5 | 3.75 m/s | 15.7 |  | 2.31 | m/s |  | 3.75 | m/s | 5.1611 | 0.009975 | 5.9591 |  | -3.5 | 31 | 0.031 | 192.2283 | 6.2628 | 5.167 | 0.021281 | 18.0041 | 0.17218
2025-05-19 15:27 | 620 | Remove | 2025-05-19 | 15:27 | ST | GS | - | 32 | g | 0 | 111.1 | 12.018 | 1194.7 | 56328 | 5:10 | 30.3 | 2.06 m/s | 20 | 31.5 | 3.79 m/s | 17.6 |  | 2.06 | m/s |  | 3.79 | m/s | 5.1694 | 0.0099558 | 5.969 |  | 1 | 32 | 0.032 | 186.5322 | 6.1703 | 5.7923 | 0.018697 | 18.0228 | 0.17755
2025-05-19 15:27 | 621 | Remove | 2025-05-19 | 15:27 | ST | GS | - | 32 | g | 0 | 111.1 | 12.04 | 1196.4 | 56338 | 5:11 | 30.3 | 2.15 m/s | 22.2 | 31.5 | 3.92 m/s | 16.1 |  | 2.15 | m/s |  | 3.92 | m/s | 5.1778 | 0.00997 | 5.979 |  | 0 | 32 | 0.032 | 186.8438 | 6.849 | 5.2987 | 0.02166 | 18.0445 | 0.17734
2025-05-19 15:28 | 622 | Remove | 2025-05-19 | 15:28 | ST | GS | - | 31 | g | 0 | 111.1 | 12.026 | 1195.1 | 56348 | 5:11 | 30.3 | 1.9 m/s | 21.6 | 31.5 | 4.41 m/s | 17.7 |  | 1.9 | m/s |  | 4.41 | m/s | 5.1861 | 0.0099592 | 5.989 |  | -1 | 31 | 0.031 | 193.1923 | 6.6639 | 5.8252 | 0.018624 | 18.0631 | 0.17162
2025-05-19 15:28 | 623 | Remove | 2025-05-19 | 15:28 | US | GS | - | 31.5 | g | 0 | 111.1 | 12.042 | 1196 | 56358 | 5:12 | 30.3 | 2.09 m/s | 20.6 | 31.6 | 4.09 m/s | 16.1 |  | 2.09 | m/s |  | 4.09 | m/s | 5.1944 | 0.0099667 | 5.9989 |  | 0.5 | 31.5 | 0.0315 | 190.4421 | 6.3554 | 5.3271 | 0.019538 | 18.0826 | 0.1742
2025-05-19 15:29 | 624 | Remove | 2025-05-19 | 15:29 | US | GS | - | 31 | g | 0 | 111.2 | 12.013 | 1193.9 | 56368 | 5:12 | 30.4 | 2.0 m/s | 22.8 | 31.6 | 3.76 m/s | 17.1 |  | 2 | m/s |  | 3.76 | m/s | 5.2028 | 0.0099492 | 6.0089 |  | -0.5 | 31 | 0.031 | 193.8347 | 7.0723 | 5.658 | 0.020806 | 18.1034 | 0.17124
2025-05-19 15:29 | 625 | Remove | 2025-05-19 | 15:29 | US | GS | - | 33.5 | g | 0 | 111.1 | 12.025 | 1195.2 | 56378 | 5:13 | 30.4 | 2.6 m/s | 20.3 | 31.6 | 4.24 m/s | 15.1 |  | 2.6 | m/s |  | 4.24 | m/s | 5.2111 | 0.00996 | 6.0188 |  | 2.5 | 33.5 | 0.0335 | 179.6668 | 6.2968 | 4.9963 | 0.024082 | 18.1275 | 0.1848
2025-05-19 15:30 | 626 | Remove | 2025-05-19 | 15:30 | ST | GS | - | 30 | g | 0 | 111.2 | 12.007 | 1193 | 56388 | 5:13 | 30.3 | 2.33 m/s | 21.4 | 31.6 | 3.96 m/s | 15.7 |  | 2.33 | m/s |  | 3.96 | m/s | 5.2194 | 0.0099417 | 6.0288 |  | -3.5 | 30 | 0.03 | 200.9593 | 6.6022 | 5.1948 | 0.022628 | 18.1501 | 0.16529
2025-05-19 15:30 | 627 | Remove | 2025-05-19 | 15:30 | ST | GS | - | 32.5 | g | 0 | 111.2 | 11.985 | 1190.4 | 56398 | 5:14 | 30.3 | 2.33 m/s | 21 | 31.6 | 3.8 m/s | 15.5 |  | 2.33 | m/s |  | 3.8 | m/s | 5.2278 | 0.00992 | 6.0387 |  | 2.5 | 32.5 | 0.0325 | 185.8061 | 6.4788 | 5.1286 | 0.022205 | 18.1723 | 0.17884
2025-05-19 15:31 | 628 | Remove | 2025-05-19 | 15:31 | ST | GS | - | 31 | g | 0 | 111.1 | 12.066 | 1199.2 | 56408 | 5:14 | 30.3 | 2.26 m/s | 22.6 | 31.6 | 4.15 m/s | 16.7 |  | 2.26 | m/s |  | 4.15 | m/s | 5.2361 | 0.0099933 | 6.0487 |  | -1.5 | 31 | 0.031 | 195.1191 | 6.9724 | 5.5257 | 0.023179 | 18.1955 | 0.17037
2025-05-19 15:31 | 629 | Remove | 2025-05-19 | 15:31 | US | GS | - | 32.5 | g | 0 | 111.1 | 12.041 | 1196.3 | 56418 | 5:15 | 30.3 | 2.01 m/s | 22.3 | 31.6 | 4.41 m/s | 19.3 |  | 2.01 | m/s |  | 4.41 | m/s | 5.2444 | 0.0099692 | 6.0587 |  | 1.5 | 32.5 | 0.0325 | 186.4203 | 6.8799 | 6.386 | 0.020341 | 18.2159 | 0.17842
2025-05-19 15:32 | 630 | Remove | 2025-05-19 | 15:32 | ST | GS | - | 30 | g | 0 | 111.1 | 12.07 | 1199.6 | 56428 | 5:15 | 30.3 | 2.35 m/s | 21.5 | 31.6 | 4.16 m/s | 15.8 |  | 2.35 | m/s |  | 4.16 | m/s | 5.2528 | 0.0099967 | 6.0687 |  | -2.5 | 30 | 0.03 | 202.2886 | 6.633 | 5.2279 | 0.022929 | 18.2388 | 0.16448
2025-05-19 15:32 | 631 | Keep | 2025-05-19 | 15:32 | US | GS | - | 40 | g | 0 | 111.2 | 12.039 | 1196.4 | 56438 | 5:16 | 30.3 | 2.23 m/s | 20.6 | 31.6 | 4.06 m/s | 16.2 |  | 2.23 | m/s |  | 4.06 | m/s | 5.2611 | 0.00997 | 6.0786 |  | 10 | 40 | 0.04 | 151.9657 | 6.3554 | 5.3602 | 0.020847 | 18.2596 | 0.21906
2025-05-19 15:33 | 632 | Remove | 2025-05-19 | 15:33 | ST | GS | - | 31.5 | g | 0 | 111 | 12.048 | 1196.4 | 56448 | 5:16 | 30.3 | 2.15 m/s | 21.4 | 31.6 | 4.07 m/s | 16.3 |  | 2.15 | m/s |  | 4.07 | m/s | 5.2694 | 0.00997 | 6.0886 |  | -8.5 | 31.5 | 0.0315 | 193.2888 | 6.6022 | 5.3933 | 0.02088 | 18.2805 | 0.17231
2025-05-19 15:33 | 633 | Remove | 2025-05-19 | 15:33 | ST | GS | - | 31.5 | g | 0 | 111.3 | 12.031 | 1195.8 | 56458 | 5:17 | 30.3 | 1.94 m/s | 21.5 | 31.7 | 4.21 m/s | 16 |  | 1.94 | m/s |  | 4.21 | m/s | 5.2778 | 0.009965 | 6.0986 |  | 0 | 31.5 | 0.0315 | 193.6052 | 6.633 | 5.3225 | 0.018929 | 18.2995 | 0.17214
2025-05-19 15:34 | 634 | Remove | 2025-05-19 | 15:34 | ST | GS | - | 31 | g | 0 | 111.1 | 12.054 | 1197.9 | 56468 | 5:17 | 30.4 | 1.79 m/s | 21.5 | 31.7 | 4.15 m/s | 16.3 |  | 1.79 | m/s |  | 4.15 | m/s | 5.2861 | 0.0099825 | 6.1085 |  | -0.5 | 31 | 0.031 | 197.0498 | 6.669 | 5.4223 | 0.01756 | 18.317 | 0.16924
2025-05-19 15:34 | 635 | Remove | 2025-05-19 | 15:34 | US | GS | - | 28 | g | 0 | 111.1 | 12.065 | 1199.3 | 56478 | 5:18 | 30.4 | 1.85 m/s | 22.7 | 31.7 | 3.98 m/s | 17.3 |  | 1.85 | m/s |  | 3.98 | m/s | 5.2944 | 0.0099942 | 6.1185 |  | -3 | 28 | 0.028 | 218.5193 | 7.0412 | 5.7549 | 0.019161 | 18.3362 | 0.1527
2025-05-19 15:35 | 636 | Remove | 2025-05-19 | 15:35 | ST | GS | - | 31.5 | g | 0 | 111.2 | 12.092 | 1203.1 | 56488 | 5:18 | 30.4 | 1.9 m/s | 20.7 | 31.7 | 4.18 m/s | 15.8 |  | 1.9 | m/s |  | 4.18 | m/s | 5.3031 | 0.010026 | 6.1286 |  | 3.5 | 31.5 | 0.0315 | 194.5576 | 6.4209 | 5.256 | 0.017945 | 18.3541 | 0.17162
2025-05-19 15:35 | 637 | Remove | 2025-05-19 | 15:35 | ST | GS | - | 33 | g | 0 | 111.1 | 12.113 | 1205.2 | 56498 | 5:19 | 30.4 | 1.63 m/s | 20.6 | 31.7 | 3.9 m/s | 16.7 |  | 1.63 | m/s |  | 3.9 | m/s | 5.3114 | 0.010043 | 6.1386 |  | 1.5 | 33 | 0.033 | 186.0184 | 6.3898 | 5.5553 | 0.015321 | 18.3694 | 0.17965
2025-05-19 15:36 | 638 | Remove | 2025-05-19 | 15:36 | ST | GS | - | 31.5 | g | 0 | 111.1 | 12.089 | 1202.8 | 56508 | 5:19 | 30.5 | 1.93 m/s | 21.6 | 31.7 | 3.92 m/s | 16.1 |  | 1.93 | m/s |  | 3.92 | m/s | 5.3197 | 0.010023 | 6.1486 |  | -1.5 | 31.5 | 0.0315 | 195.1947 | 6.7363 | 5.3557 | 0.019124 | 18.3886 | 0.1713
2025-05-19 15:36 | 639 | Remove | 2025-05-19 | 15:36 | ST | GS | - | 34 | g | 0 | 111.1 | 12.007 | 1193.1 | 56518 | 5:20 | 30.5 | 2.02 m/s | 20.2 | 31.7 | 4.06 m/s | 16 |  | 2.02 | m/s |  | 4.06 | m/s | 5.3281 | 0.0099425 | 6.1586 |  | 2.5 | 34 | 0.034 | 181.1345 | 6.2997 | 5.3225 | 0.018719 | 18.4073 | 0.18471
2025-05-19 15:37 | 640 | Remove | 2025-05-19 | 15:37 | ST | GS | - | 33.5 | g | 0 | 111.2 | 12.026 | 1196.1 | 56528 | 5:20 | 30.4 | 2.42 m/s | 20.6 | 31.7 | 4.16 m/s | 15.2 |  | 2.42 | m/s |  | 4.16 | m/s | 5.3364 | 0.0099675 | 6.1685 |  | -0.5 | 33.5 | 0.0335 | 184.1356 | 6.3898 | 5.0564 | 0.022746 | 18.43 | 0.18177
2025-05-19 15:37 | 641 | Remove | 2025-05-19 | 15:37 | US | GS | - | 32 | g | 0 | 111.1 | 12.051 | 1197.9 | 56538 | 5:21 | 30.3 | 2.01 m/s | 20.7 | 31.7 | 3.9 m/s | 16.6 |  | 2.01 | m/s |  | 3.9 | m/s | 5.3447 | 0.0099825 | 6.1785 |  | -1.5 | 32 | 0.032 | 193.0789 | 6.3862 | 5.5221 | 0.018882 | 18.4489 | 0.17345
2025-05-19 15:38 | 642 | Remove | 2025-05-19 | 15:38 | ST | GS | - | 34 | g | 0 | 111.2 | 12.04 | 1196.9 | 56548 | 5:21 | 30.3 | 3.16 m/s | 20.9 | 31.7 | 4.04 m/s | 15.5 |  | 3.16 | m/s |  | 4.04 | m/s | 5.3531 | 0.0099742 | 6.1885 |  | 2 | 34 | 0.034 | 182.0147 | 6.4479 | 5.1562 | 0.029972 | 18.4789 | 0.18399
2025-05-19 15:38 | 643 | Remove | 2025-05-19 | 15:38 | ST | GS | - | 32 | g | 0 | 111.2 | 12.062 | 1198.9 | 56558 | 5:22 | 30.3 | 2.15 m/s | 21.7 | 31.7 | 3.97 m/s | 16.3 |  | 2.15 | m/s |  | 3.97 | m/s | 5.3614 | 0.0099908 | 6.1985 |  | -2 | 32 | 0.032 | 193.7028 | 6.6947 | 5.4223 | 0.021173 | 18.5001 | 0.17297
2025-05-19 15:39 | 644 | Remove | 2025-05-19 | 15:39 | ST | GS | - | 33 | g | 0 | 111.2 | 12.076 | 1200.6 | 56568 | 5:22 | 30.3 | 1.85 m/s | 20.4 | 31.7 | 3.92 m/s | 16.2 |  | 1.85 | m/s |  | 3.92 | m/s | 5.3697 | 0.010005 | 6.2085 |  | 1 | 33 | 0.033 | 188.1362 | 6.2937 | 5.389 | 0.017127 | 18.5172 | 0.17821
2025-05-19 15:39 | 645 | Remove | 2025-05-19 | 15:39 | US | GS | - | 36 | g | 0 | 111.1 | 12.041 | 1196.7 | 56578 | 5:23 | 30.3 | 1.89 m/s | 21.7 | 31.7 | 4.06 m/s | 16.7 |  | 1.89 | m/s |  | 4.06 | m/s | 5.3781 | 0.0099725 | 6.2185 |  | 3 | 36 | 0.036 | 172.7352 | 6.6947 | 5.5553 | 0.018612 | 18.5358 | 0.19422
2025-05-19 15:40 | 646 | Remove | 2025-05-19 | 15:40 | US | GS | - | 35 | g | 0 | 111.1 | 12.007 | 1192.6 | 56588 | 5:23 | 30.3 | 1.98 m/s | 20.8 | 31.7 | 3.81 m/s | 16 |  | 1.98 | m/s |  | 3.81 | m/s | 5.3864 | 0.0099383 | 6.2284 |  | -1 | 35 | 0.035 | 177.9544 | 6.4171 | 5.3225 | 0.01869 | 18.5545 | 0.18863
2025-05-19 15:40 | 647 | Remove | 2025-05-19 | 15:40 | ST | GS | - | 34 | g | 0 | 111.1 | 12.046 | 1197.9 | 56598 | 5:24 | 30.3 | 2.06 m/s | 20.4 | 31.7 | 4.1 m/s | 15.2 |  | 2.06 | m/s |  | 4.1 | m/s | 5.3947 | 0.0099825 | 6.2384 |  | -1 | 34 | 0.034 | 183.482 | 6.2937 | 5.0564 | 0.019071 | 18.5736 | 0.18306
2025-05-19 15:41 | 648 | Remove | 2025-05-19 | 15:41 | ST | GS | - | 35 | g | 0 | 111.1 | 12.018 | 1194.2 | 56608 | 5:24 | 30.3 | 2.08 m/s | 20.7 | 31.7 | 3.81 m/s | 16.2 |  | 2.08 | m/s |  | 3.81 | m/s | 5.4031 | 0.0099517 | 6.2483 |  | 1 | 35 | 0.035 | 178.524 | 6.3862 | 5.389 | 0.019539 | 18.5931 | 0.18824
2025-05-19 15:41 | 649 | Remove | 2025-05-19 | 15:41 | US | GS | - | 34.5 | g | 0 | 111 | 12.045 | 1197.2 | 56618 | 5:25 | 30.4 | 1.88 m/s | 22.7 | 31.7 | 4.12 m/s | 17.6 |  | 1.88 | m/s |  | 4.12 | m/s | 5.4114 | 0.0099767 | 6.2583 |  | -0.5 | 34.5 | 0.0345 | 181.4005 | 7.0412 | 5.8547 | 0.019472 | 18.6126 | 0.18536
2025-05-19 15:42 | 650 | Remove | 2025-05-19 | 15:42 | ST | GS | - | 32 | g | 0 | 111.1 | 12.074 | 1200 | 56628 | 5:25 | 30.3 | 2.01 m/s | 20.3 | 31.7 | 4.12 m/s | 15 |  | 2.01 | m/s |  | 4.12 | m/s | 5.42 | 0.01 | 6.2683 |  | -2.5 | 32 | 0.032 | 195.8849 | 6.2628 | 4.9898 | 0.018517 | 18.6311 | 0.17176
2025-05-19 15:42 | 651 | Remove | 2025-05-19 | 15:42 | ST | GS | - | 33 | g | 0 | 111.1 | 12.047 | 1197.1 | 56638 | 5:26 | 30.3 | 1.85 m/s | 20.9 | 31.7 | 4.1 m/s | 15.6 |  | 1.85 | m/s |  | 4.1 | m/s | 5.4283 | 0.0099758 | 6.2783 |  | 1 | 33 | 0.033 | 190.2513 | 6.4479 | 5.1894 | 0.017547 | 18.6486 | 0.17696
2025-05-19 15:43 | 652 | Remove | 2025-05-19 | 15:43 | ST | GS | - | 36 | g | 0 | 111.2 | 12.032 | 1195.8 | 56648 | 5:26 | 30.3 | 2.05 m/s | 20.5 | 31.7 | 3.77 m/s | 16.3 |  | 2.05 | m/s |  | 3.77 | m/s | 5.4367 | 0.009965 | 6.2883 |  | 3 | 36 | 0.036 | 174.6738 | 6.3245 | 5.4223 | 0.019071 | 18.6677 | 0.19285
2025-05-19 15:43 | 653 | Remove | 2025-05-19 | 15:43 | ST | GS | - | 34 | g | 0 | 111 | 12.043 | 1197.2 | 56658 | 5:27 | 30.3 | 2.25 m/s | 21 | 31.7 | 3.86 m/s | 16 |  | 2.25 | m/s |  | 3.86 | m/s | 5.4453 | 0.0099767 | 6.2982 |  | -2 | 34 | 0.034 | 185.2422 | 6.4788 | 5.3225 | 0.021443 | 18.6891 | 0.18192
2025-05-19 15:44 | 654 | Remove | 2025-05-19 | 15:44 | ST | GS | - | 35 | g | 0 | 111.2 | 12.029 | 1195.7 | 56668 | 5:27 | 30.3 | 2.18 m/s | 21.7 | 31.6 | 3.71 m/s | 16 |  | 2.18 | m/s |  | 3.71 | m/s | 5.4536 | 0.0099642 | 6.3082 |  | 1 | 35 | 0.035 | 180.2342 | 6.6947 | 5.2941 | 0.021468 | 18.7106 | 0.18706
2025-05-19 15:44 | 655 | Remove | 2025-05-19 | 15:44 | ST | GS | - | 33 | g | 0 | 111.2 | 12.024 | 1194.9 | 56678 | 5:28 | 30.4 | 1.81 m/s | 22.5 | 31.6 | 4.41 m/s | 18.3 |  | 1.81 | m/s |  | 4.41 | m/s | 5.4619 | 0.0099575 | 6.3182 |  | -2 | 33 | 0.033 | 191.4592 | 6.9792 | 6.0551 | 0.018582 | 18.7292 | 0.1762
2025-05-19 15:45 | 656 | Remove | 2025-05-19 | 15:45 | US | GS | - | 35 | g | 0 | 111.1 | 12.072 | 1200.4 | 56688 | 5:28 | 30.3 | 2.16 m/s | 21.9 | 31.6 | 3.92 m/s | 15.7 |  | 2.16 | m/s |  | 3.92 | m/s | 5.4703 | 0.010003 | 6.3282 |  | 2 | 35 | 0.035 | 180.8045 | 6.7565 | 5.1948 | 0.021467 | 18.7507 | 0.18666
2025-05-19 15:45 | 657 | Remove | 2025-05-19 | 15:45 | US | GS | - | 35.5 | g | 0 | 111.1 | 12.061 | 1198.9 | 56698 | 5:29 | 30.4 | 2.15 m/s | 20.2 | 31.6 | 3.88 m/s | 15.9 |  | 2.15 | m/s |  | 3.88 | m/s | 5.4786 | 0.0099908 | 6.3381 |  | 0.5 | 35.5 | 0.0355 | 178.5394 | 6.2658 | 5.261 | 0.019816 | 18.7705 | 0.18913
2025-05-19 15:46 | 658 | Remove | 2025-05-19 | 15:46 | ST | GS | - | 35.5 | g | 0 | 111.2 | 12.045 | 1197.2 | 56708 | 5:29 | 30.3 | 1.98 m/s | 24 | 31.6 | 4.03 m/s | 17.1 |  | 1.98 | m/s |  | 4.03 | m/s | 5.4869 | 0.0099767 | 6.3481 |  | 0 | 35.5 | 0.0355 | 178.8204 | 7.4043 | 5.658 | 0.021565 | 18.792 | 0.18891
2025-05-19 15:46 | 659 | Remove | 2025-05-19 | 15:46 | ST | GS | - | 33.5 | g | 0 | 111.1 | 12.093 | 1202.1 | 56718 | 5:30 | 30.3 | 1.77 m/s | 22.6 | 31.6 | 4.12 m/s | 17 |  | 1.77 | m/s |  | 4.12 | m/s | 5.4953 | 0.010017 | 6.3581 |  | -2 | 33.5 | 0.0335 | 189.7953 | 6.9724 | 5.6249 | 0.018153 | 18.8102 | 0.17809
2025-05-19 15:47 | 660 | Remove | 2025-05-19 | 15:47 | US | GS | - | 34.5 | g | 0 | 111.1 | 12.064 | 1199.7 | 56728 | 5:30 | 30.4 | 1.71 m/s | 21.4 | 31.7 | 4.18 m/s | 19 |  | 1.71 | m/s |  | 4.18 | m/s | 5.5036 | 0.0099975 | 6.3681 |  | 1 | 34.5 | 0.0345 | 184.5838 | 6.638 | 6.3204 | 0.016697 | 18.8269 | 0.18325
2025-05-19 15:47 | 661 | Keep | 2025-05-19 | 15:47 | ST | GS | - | 34 | g | 0 | 111.2 | 12.046 | 1197.8 | 56738 | 5:31 | 30.4 | 1.73 m/s | 22 | 31.7 | 3.96 m/s | 17.2 |  | 1.73 | m/s |  | 3.96 | m/s | 5.5119 | 0.0099817 | 6.3781 |  | -0.5 | 34 | 0.034 | 187.5918 | 6.8241 | 5.7217 | 0.017366 | 18.8443 | 0.18043
2025-05-19 15:48 | 662 | Remove | 2025-05-19 | 15:48 | ST | GS | - | 34.5 | g | 0 | 111 | 12.078 | 1201.4 | 56749 | 5:31 | 30.4 | 2.04 m/s | 21.8 | 31.7 | 3.85 m/s | 15.9 |  | 2.04 | m/s |  | 3.85 | m/s | 5.5203 | 0.010012 | 6.3881 |  | 0.5 | 34.5 | 0.0345 | 185.1633 | 6.7621 | 5.2892 | 0.020291 | 18.8645 | 0.18288
2025-05-19 15:48 | 663 | Remove | 2025-05-19 | 15:48 | ST | GS | - | 35 | g | 0 | 111 | 12.049 | 1198.1 | 56759 | 5:32 | 30.4 | 1.98 m/s | 22.9 | 31.7 | 3.94 m/s | 17.4 |  | 1.98 | m/s |  | 3.94 | m/s | 5.5286 | 0.0099842 | 6.3981 |  | 0.5 | 35 | 0.035 | 182.8034 | 7.1033 | 5.7882 | 0.020688 | 18.8852 | 0.18533
2025-05-19 15:49 | 664 | Remove | 2025-05-19 | 15:49 | ST | GS | - | 35.5 | g | 0 | 111.1 | 12.05 | 1198.5 | 56769 | 5:32 | 30.4 | 1.85 m/s | 22.7 | 31.7 | 3.73 m/s | 18.8 |  | 1.85 | m/s |  | 3.73 | m/s | 5.5369 | 0.0099875 | 6.4081 |  | 0.5 | 35.5 | 0.0355 | 180.51 | 7.0412 | 6.2539 | 0.019161 | 18.9044 | 0.18779
2025-05-19 15:49 | 665 | Remove | 2025-05-19 | 15:49 | ST | GS | - | 37.5 | g | 0 | 111 | 12.056 | 1198.3 | 56779 | 5:33 | 30.4 | 1.82 m/s | 23.3 | 31.6 | 4.18 m/s | 18.8 |  | 1.82 | m/s |  | 4.18 | m/s | 5.5453 | 0.0099858 | 6.4181 |  | 2 | 37.5 | 0.0375 | 171.1491 | 7.2273 | 6.2205 | 0.019349 | 18.9237 | 0.19816
2025-05-19 15:50 | 666 | Remove | 2025-05-19 | 15:50 | US | GS | - | 35 | g | 0 | 111 | 12.08 | 1201.5 | 56789 | 5:33 | 30.4 | 1.93 m/s | 25.1 | 31.6 | 3.89 m/s | 18.3 |  | 1.93 | m/s |  | 3.89 | m/s | 5.5536 | 0.010012 | 6.4281 |  | -2.5 | 35 | 0.035 | 183.6601 | 7.7857 | 6.0551 | 0.022103 | 18.9459 | 0.18474
2025-05-19 15:50 | 667 | Remove | 2025-05-19 | 15:50 | ST | GS | - | 35.5 | g | 0 | 110.9 | 12.068 | 1199.1 | 56799 | 5:34 | 30.4 | 1.75 m/s | 21.7 | 31.7 | 3.72 m/s | 16.6 |  | 1.75 | m/s |  | 3.72 | m/s | 5.5619 | 0.0099925 | 6.4381 |  | 0.5 | 35.5 | 0.0355 | 181.3548 | 6.7311 | 5.5221 | 0.017327 | 18.9632 | 0.1872
2025-05-19 15:51 | 668 | Remove | 2025-05-19 | 15:51 | US | GS | - | 34 | g | 0 | 110.9 | 12.064 | 1199.5 | 56809 | 5:34 | 30.4 | 1.81 m/s | 22.3 | 31.7 | 4.12 m/s | 17 |  | 1.81 | m/s |  | 4.12 | m/s | 5.5703 | 0.0099958 | 6.4481 |  | -1.5 | 34 | 0.034 | 189.6498 | 6.9172 | 5.6551 | 0.018417 | 18.9816 | 0.17912
2025-05-19 15:51 | 669 | Remove | 2025-05-19 | 15:51 | ST | GS | - | 35 | g | 0 | 110.9 | 12.051 | 1196.9 | 56819 | 5:35 | 30.4 | 2.12 m/s | 23.4 | 31.7 | 3.92 m/s | 18 |  | 2.12 | m/s |  | 3.92 | m/s | 5.5786 | 0.0099742 | 6.4581 |  | 1 | 35 | 0.035 | 184.5162 | 7.2584 | 5.9878 | 0.022635 | 19.0042 | 0.18417
2025-05-19 15:52 | 670 | Remove | 2025-05-19 | 15:52 | US | GS | - | 37 | g | 0 | 111 | 12.039 | 1196.4 | 56829 | 5:35 | 30.4 | 2.01 m/s | 22 | 31.7 | 4.36 m/s | 16.8 |  | 2.01 | m/s |  | 4.36 | m/s | 5.5869 | 0.00997 | 6.468 |  | 2 | 37 | 0.037 | 174.8118 | 6.8241 | 5.5886 | 0.020176 | 19.0244 | 0.19449
2025-05-19 15:52 | 671 | Remove | 2025-05-19 | 15:52 | ST | GS | - | 34.5 | g | 0 | 111.1 | 12.039 | 1196.4 | 56839 | 5:36 | 30.4 | 1.82 m/s | 21.9 | 31.7 | 4.12 m/s | 16.4 |  | 1.82 | m/s |  | 4.12 | m/s | 5.5953 | 0.00997 | 6.478 |  | -2.5 | 34.5 | 0.0345 | 187.7683 | 6.7931 | 5.4555 | 0.018186 | 19.0426 | 0.18117
2025-05-19 15:53 | 672 | Remove | 2025-05-19 | 15:53 | ST | GS | - | 33 | g | 0 | 111.1 | 12.084 | 1201.9 | 56849 | 5:36 | 30.4 | 1.85 m/s | 21.4 | 31.7 | 4.18 m/s | 17.2 |  | 1.85 | m/s |  | 4.18 | m/s | 5.6039 | 0.010016 | 6.488 |  | -1.5 | 33 | 0.033 | 196.6067 | 6.638 | 5.7217 | 0.018064 | 19.0607 | 0.17313
2025-05-19 15:53 | 673 | Remove | 2025-05-19 | 15:53 | ST | GS | - | 34.5 | g | 0 | 111 | 12.048 | 1197.1 | 56859 | 5:37 | 30.4 | 2.02 m/s | 22.3 | 31.7 | 3.86 m/s | 16.3 |  | 2.02 | m/s |  | 3.86 | m/s | 5.6122 | 0.0099758 | 6.498 |  | 1.5 | 34.5 | 0.0345 | 188.3478 | 6.9172 | 5.4223 | 0.020553 | 19.0812 | 0.18081
2025-05-19 15:54 | 674 | Remove | 2025-05-19 | 15:54 | ST | GS | - | 35 | g | 0 | 111 | 12.077 | 1201 | 56869 | 5:37 | 30.4 | 1.83 m/s | 21.6 | 31.7 | 3.84 m/s | 16.5 |  | 1.83 | m/s |  | 3.84 | m/s | 5.6206 | 0.010008 | 6.508 |  | 0.5 | 35 | 0.035 | 185.943 | 6.7 | 5.4888 | 0.018036 | 19.0992 | 0.18325
2025-05-19 15:54 | 675 | Remove | 2025-05-19 | 15:54 | ST | GS | - | 34.5 | g | 0 | 111.1 | 12.076 | 1201.1 | 56879 | 5:38 | 30.4 | 1.74 m/s | 21.5 | 31.7 | 4.61 m/s | 16.8 |  | 1.74 | m/s |  | 4.61 | m/s | 5.6289 | 0.010009 | 6.518 |  | -0.5 | 34.5 | 0.0345 | 188.928 | 6.669 | 5.5886 | 0.017069 | 19.1163 | 0.18047
2025-05-19 15:55 | 676 | Remove | 2025-05-19 | 15:55 | ST | GS | - | 36 | g | 0 | 111 | 12.11 | 1205.4 | 56889 | 5:38 | 30.4 | 1.81 m/s | 20.1 | 31.7 | 3.89 m/s | 15.6 |  | 1.81 | m/s |  | 3.89 | m/s | 5.6372 | 0.010045 | 6.5281 |  | 1.5 | 36 | 0.036 | 181.335 | 6.2348 | 5.1894 | 0.0166 | 19.1329 | 0.18816
2025-05-19 15:55 | 677 | Remove | 2025-05-19 | 15:55 | ST | GS | - | 35 | g | 0 | 111 | 12.055 | 1199 | 56899 | 5:39 | 30.4 | 1.93 m/s | 20.6 | 31.7 | 3.94 m/s | 16.6 |  | 1.93 | m/s |  | 3.94 | m/s | 5.6456 | 0.0099917 | 6.5381 |  | -1 | 35 | 0.035 | 186.8015 | 6.3898 | 5.5221 | 0.018141 | 19.1511 | 0.18276
2025-05-19 15:56 | 678 | Remove | 2025-05-19 | 15:56 | US | GS | - | 38 | g | 0 | 111.1 | 12.047 | 1197.9 | 56909 | 5:39 | 30.4 | 2.0 m/s | 21.3 | 31.7 | 4.18 m/s | 16.5 |  | 2 | m/s |  | 4.18 | m/s | 5.6539 | 0.0099825 | 6.548 |  | 3 | 38 | 0.038 | 172.3167 | 6.607 | 5.4888 | 0.019437 | 19.1705 | 0.19822
2025-05-19 15:56 | 679 | Remove | 2025-05-19 | 15:56 | US | GS | - | 38.5 | g | 0 | 111.1 | 12.026 | 1196 | 56919 | 5:40 | 30.4 | 2.48 m/s | 21.9 | 31.7 | 3.69 m/s | 16.2 |  | 2.48 | m/s |  | 3.69 | m/s | 5.6622 | 0.0099667 | 6.558 |  | 0.5 | 38.5 | 0.0385 | 170.3377 | 6.7931 | 5.389 | 0.024781 | 19.1953 | 0.20057
2025-05-19 15:57 | 680 | Remove | 2025-05-19 | 15:57 | US | GS | - | 37.5 | g | 0 | 111.1 | 12.07 | 1200.6 | 56929 | 5:40 | 30.4 | 1.87 m/s | 20.9 | 31.7 | 4.35 m/s | 15.9 |  | 1.87 | m/s |  | 4.35 | m/s | 5.6706 | 0.010005 | 6.568 |  | -1 | 37.5 | 0.0375 | 175.1468 | 6.4829 | 5.2892 | 0.017833 | 19.2131 | 0.19518
2025-05-19 15:57 | 681 | Remove | 2025-05-19 | 15:57 | ST | GS | - | 37.5 | g | 0 | 111.1 | 12.049 | 1198.3 | 56939 | 5:41 | 30.3 | 2.26 m/s | 21.7 | 31.7 | 4.16 m/s | 16.2 |  | 2.26 | m/s |  | 4.16 | m/s | 5.6789 | 0.0099858 | 6.578 |  | 0 | 37.5 | 0.0375 | 175.4131 | 6.6947 | 5.389 | 0.022256 | 19.2354 | 0.19495
2025-05-19 15:58 | 682 | Remove | 2025-05-19 | 15:58 | ST | GS | - | 39.5 | g | 0 | 111 | 12.04 | 1195.6 | 56949 | 5:41 | 30.3 | 2.34 m/s | 20.7 | 31.6 | 3.92 m/s | 15.8 |  | 2.34 | m/s |  | 3.92 | m/s | 5.6872 | 0.0099633 | 6.588 |  | 2 | 39.5 | 0.0395 | 166.7837 | 6.3862 | 5.2279 | 0.021982 | 19.2573 | 0.20512
2025-05-19 15:58 | 683 | Remove | 2025-05-19 | 15:58 | US | GS | - | 35.5 | g | 0 | 111.1 | 12.075 | 1200.6 | 56959 | 5:42 | 30.4 | 1.83 m/s | 22.8 | 31.6 | 4.07 m/s | 16.9 |  | 1.83 | m/s |  | 4.07 | m/s | 5.6956 | 0.010005 | 6.598 |  | -4 | 35.5 | 0.0355 | 185.8581 | 7.0723 | 5.5918 | 0.019038 | 19.2764 | 0.18416
2025-05-19 15:59 | 684 | Remove | 2025-05-19 | 15:59 | ST | GS | - | 37.5 | g | 0 | 111.2 | 12.032 | 1195.6 | 56969 | 5:42 | 30.4 | 2.4 m/s | 21.2 | 31.6 | 3.86 m/s | 18.3 |  | 2.4 | m/s |  | 3.86 | m/s | 5.7039 | 0.0099633 | 6.6079 |  | 2 | 37.5 | 0.0375 | 176.2113 | 6.576 | 6.0551 | 0.023215 | 19.2996 | 0.1943
2025-05-19 15:59 | 685 | Remove | 2025-05-19 | 15:59 | ST | GS | - | 35.5 | g | 0 | 111.1 | 12.03 | 1195.5 | 56979 | 5:43 | 30.4 | 1.83 m/s | 25 | 31.6 | 4.06 m/s | 20 |  | 1.83 | m/s |  | 4.06 | m/s | 5.7122 | 0.0099625 | 6.6179 |  | -2 | 35.5 | 0.0355 | 186.4193 | 7.7547 | 6.6176 | 0.020875 | 19.3205 | 0.18374
2025-05-19 16:00 | 686 | Remove | 2025-05-19 | 16:00 | ST | GS | - | 36 | g | 0 | 111.1 | 12.054 | 1198.5 | 56989 | 5:43 | 30.4 | 1.86 m/s | 20.6 | 31.6 | 3.89 m/s | 17.6 |  | 1.86 | m/s |  | 3.89 | m/s | 5.7206 | 0.0099875 | 6.6279 |  | 0.5 | 36 | 0.036 | 184.1076 | 6.3898 | 5.8235 | 0.017483 | 19.338 | 0.18616
2025-05-19 16:00 | 687 | Remove | 2025-05-19 | 16:00 | ST | GS | - | 36.5 | g | 0 | 111.2 | 12.048 | 1197.9 | 56999 | 5:44 | 30.4 | 1.75 m/s | 21.3 | 31.6 | 3.93 m/s | 19.1 |  | 1.75 | m/s |  | 3.93 | m/s | 5.7289 | 0.0099825 | 6.6379 |  | 0.5 | 36.5 | 0.0365 | 181.8591 | 6.607 | 6.3198 | 0.017008 | 19.355 | 0.18858
2025-05-19 16:01 | 688 | Remove | 2025-05-19 | 16:01 | US | GS | - | 50.5 | g | 0 | 111.3 | 12.008 | 1193.5 | 57009 | 5:44 | 30.4 | 2.12 m/s | 22.7 | 31.6 | 3.96 m/s | 18.7 |  | 2.12 | m/s |  | 3.96 | m/s | 5.7372 | 0.0099458 | 6.6478 |  | 14 | 50.5 | 0.0505 | 131.6397 | 7.0412 | 6.1874 | 0.021958 | 19.3769 | 0.26062
2025-05-19 16:01 | 689 | Remove | 2025-05-19 | 16:01 | US | GS | - | 37.5 | g | 0 | 111.1 | 12.058 | 1198.7 | 57019 | 5:45 | 30.4 | 1.73 m/s | 25.9 | 31.6 | 3.85 m/s | 17.8 |  | 1.73 | m/s |  | 3.85 | m/s | 5.7458 | 0.0099892 | 6.6578 |  | -13 | 37.5 | 0.0375 | 177.5411 | 8.0338 | 5.8896 | 0.020444 | 19.3974 | 0.19333
2025-05-19 16:02 | 690 | Remove | 2025-05-19 | 16:02 | ST | GS | - | 37.5 | g | 0 | 111.2 | 12.054 | 1198.5 | 57029 | 5:45 | 30.4 | 1.91 m/s | 23.4 | 31.6 | 3.85 m/s | 16.9 |  | 1.91 | m/s |  | 3.85 | m/s | 5.7542 | 0.0099875 | 6.6678 |  | 0 | 37.5 | 0.0375 | 177.8074 | 7.2584 | 5.5918 | 0.020393 | 19.4178 | 0.19312
2025-05-19 16:02 | 691 | Keep | 2025-05-19 | 16:02 | ST | GS | - | 39 | g | 0 | 111.2 | 12.057 | 1198.3 | 57039 | 5:46 | 30.4 | 2.05 m/s | 24.6 | 31.6 | 3.9 m/s | 17.4 |  | 2.05 | m/s |  | 3.9 | m/s | 5.7625 | 0.0099858 | 6.6778 |  | 1.5 | 39 | 0.039 | 171.2247 | 7.6306 | 5.7573 | 0.02301 | 19.4408 | 0.20061
2025-05-19 16:03 | 692 | Remove | 2025-05-19 | 16:03 | ST | GS | - | 37.5 | g | 0 | 111.2 | 12.073 | 1200.9 | 57049 | 5:46 | 30.4 | 1.67 m/s | 22.2 | 31.6 | 4.07 m/s | 17.9 |  | 1.67 | m/s |  | 4.07 | m/s | 5.7708 | 0.010008 | 6.6878 |  | -1.5 | 37.5 | 0.0375 | 178.3406 | 6.8861 | 5.9227 | 0.016916 | 19.4577 | 0.19273
2025-05-19 16:03 | 693 | Remove | 2025-05-19 | 16:03 | US | GS | - | 44.5 | g | 0 | 111.1 | 12.067 | 1199.9 | 57059 | 5:47 | 30.4 | 2.25 m/s | 21.6 | 31.6 | 3.76 m/s | 17.5 |  | 2.25 | m/s |  | 3.76 | m/s | 5.7792 | 0.0099992 | 6.6978 |  | 7 | 44.5 | 0.0445 | 150.5117 | 6.7 | 5.7904 | 0.022175 | 19.4799 | 0.22844
2025-05-19 16:04 | 694 | Remove | 2025-05-19 | 16:04 | ST | GS | - | 36.5 | g | 0 | 111.1 | 12.069 | 1200.5 | 57069 | 5:47 | 30.4 | 1.68 m/s | 20.9 | 31.6 | 3.9 m/s | 17.2 |  | 1.68 | m/s |  | 3.9 | m/s | 5.7875 | 0.010004 | 6.7078 |  | -8 | 36.5 | 0.0365 | 183.7747 | 6.4829 | 5.6911 | 0.016021 | 19.4959 | 0.18722
2025-05-19 16:04 | 695 | Remove | 2025-05-19 | 16:04 | ST | GS | - | 37.5 | g | 0 | 111.2 | 12.069 | 1200.7 | 57079 | 5:48 | 30.4 | 1.66 m/s | 21.4 | 31.6 | 4.1 m/s | 17.4 |  | 1.66 | m/s |  | 4.1 | m/s | 5.7958 | 0.010006 | 6.7178 |  | 1 | 37.5 | 0.0375 | 179.1408 | 6.638 | 5.7573 | 0.016209 | 19.5121 | 0.19219
2025-05-19 16:05 | 696 | Remove | 2025-05-19 | 16:05 | ST | GS | - | 37 | g | 0 | 111.2 | 12.058 | 1199.1 | 57089 | 5:48 | 30.4 | 2.26 m/s | 21.1 | 31.6 | 4.2 m/s | 17.1 |  | 2.26 | m/s |  | 4.2 | m/s | 5.8042 | 0.0099925 | 6.7278 |  | -0.5 | 37 | 0.037 | 181.8317 | 6.5449 | 5.658 | 0.021758 | 19.5338 | 0.18941
2025-05-19 16:05 | 697 | Remove | 2025-05-19 | 16:05 | ST | GS | - | 37.5 | g | 0 | 111.2 | 12.054 | 1198.9 | 57099 | 5:49 | 30.4 | 1.86 m/s | 22.1 | 31.6 | 3.89 m/s | 17.4 |  | 1.86 | m/s |  | 3.89 | m/s | 5.8125 | 0.0099908 | 6.7378 |  | 0.5 | 37.5 | 0.0375 | 179.6737 | 6.8551 | 5.7573 | 0.018756 | 19.5526 | 0.19179
2025-05-19 16:06 | 698 | Remove | 2025-05-19 | 16:06 | ST | GS | - | 37 | g | 0 | 111.1 | 12.089 | 1202.4 | 57109 | 5:49 | 30.4 | 2.11 m/s | 21.5 | 31.6 | 3.96 m/s | 15.9 |  | 2.11 | m/s |  | 3.96 | m/s | 5.8208 | 0.01002 | 6.7478 |  | -0.5 | 37 | 0.037 | 182.3726 | 6.669 | 5.261 | 0.020699 | 19.5733 | 0.18903
2025-05-19 16:06 | 699 | Remove | 2025-05-19 | 16:06 | ST | GS | - | 40.5 | g | 0 | 111.3 | 12.073 | 1201.3 | 57119 | 5:50 | 30.4 | 2.09 m/s | 21 | 31.6 | 3.96 m/s | 16.1 |  | 2.09 | m/s |  | 3.96 | m/s | 5.8292 | 0.010011 | 6.7578 |  | 3.5 | 40.5 | 0.0405 | 166.8592 | 6.5139 | 5.3271 | 0.020026 | 19.5933 | 0.2067
2025-05-19 16:07 | 700 | Remove | 2025-05-19 | 16:07 | ST | GS | - | 38.5 | g | 0 | 111.2 | 12.041 | 1197.8 | 57129 | 5:50 | 30.4 | 1.93 m/s | 21.3 | 31.6 | 3.72 m/s | 16.9 |  | 1.93 | m/s |  | 3.72 | m/s | 5.8375 | 0.0099817 | 6.7678 |  | -2 | 38.5 | 0.0385 | 175.7864 | 6.607 | 5.5918 | 0.018757 | 19.6121 | 0.19631
2025-05-19 16:07 | 701 | Remove | 2025-05-19 | 16:07 | US | GS | - | 42 | g | 0 | 111.2 | 12.038 | 1196.4 | 57139 | 5:51 | 30.4 | 2.08 m/s | 22.7 | 31.6 | 3.81 m/s | 16.8 |  | 2.08 | m/s |  | 3.81 | m/s | 5.8458 | 0.00997 | 6.7777 |  | 3.5 | 42 | 0.042 | 161.3749 | 7.0412 | 5.5588 | 0.021543 | 19.6336 | 0.21392
2025-05-19 16:08 | 702 | Remove | 2025-05-19 | 16:08 | ST | GS | - | 38 | g | 0 | 111.2 | 12.06 | 1199.1 | 57149 | 5:51 | 30.3 | 2.04 m/s | 20.7 | 31.6 | 4.56 m/s | 16.1 |  | 2.04 | m/s |  | 4.56 | m/s | 5.8542 | 0.0099925 | 6.7877 |  | -4 | 38 | 0.038 | 178.6247 | 6.3862 | 5.3271 | 0.019164 | 19.6528 | 0.19336
2025-05-19 16:08 | 703 | Remove | 2025-05-19 | 16:08 | ST | GS | - | 41 | g | 0 | 111.3 | 12.049 | 1197.8 | 57159 | 5:52 | 30.4 | 1.97 m/s | 22.8 | 31.6 | 4.12 m/s | 17 |  | 1.97 | m/s |  | 4.12 | m/s | 5.8625 | 0.0099817 | 6.7977 |  | 3 | 41 | 0.041 | 165.7981 | 7.0723 | 5.6249 | 0.020494 | 19.6733 | 0.2084
2025-05-19 16:09 | 704 | Remove | 2025-05-19 | 16:09 | US | GS | - | 39.5 | g | 0 | 111.2 | 12.035 | 1196.5 | 57169 | 5:52 | 30.3 | 1.87 m/s | 21.1 | 31.6 | 3.8 m/s | 16.6 |  | 1.87 | m/s |  | 3.8 | m/s | 5.8708 | 0.0099708 | 6.8077 |  | -1.5 | 39.5 | 0.0395 | 172.3466 | 6.5096 | 5.4926 | 0.017906 | 19.6912 | 0.2006
2025-05-19 16:09 | 705 | Remove | 2025-05-19 | 16:09 | ST | GS | - | 38 | g | 0 | 111.3 | 12.026 | 1195.4 | 57179 | 5:53 | 30.3 | 1.82 m/s | 22.3 | 31.6 | 4.04 m/s | 17 |  | 1.82 | m/s |  | 4.04 | m/s | 5.8792 | 0.0099617 | 6.8177 |  | -1.5 | 38 | 0.038 | 179.412 | 6.8799 | 5.6249 | 0.018418 | 19.7096 | 0.1928
2025-05-19 16:10 | 706 | Remove | 2025-05-19 | 16:10 | ST | GS | - | 39.5 | g | 0 | 111.2 | 12.037 | 1196 | 57189 | 5:53 | 30.4 | 2.04 m/s | 21.4 | 31.5 | 3.93 m/s | 16.3 |  | 2.04 | m/s |  | 3.93 | m/s | 5.8878 | 0.0099667 | 6.8276 |  | 1.5 | 39.5 | 0.0395 | 172.8512 | 6.638 | 5.3645 | 0.019919 | 19.7295 | 0.20021
2025-05-19 16:10 | 707 | Remove | 2025-05-19 | 16:10 | ST | GS | - | 38.5 | g | 0 | 111.3 | 12.026 | 1195.2 | 57199 | 5:54 | 30.4 | 1.87 m/s | 24.7 | 31.5 | 3.97 m/s | 17.4 |  | 1.87 | m/s |  | 3.97 | m/s | 5.8961 | 0.00996 | 6.8376 |  | -1 | 38.5 | 0.0385 | 177.5995 | 7.6616 | 5.7265 | 0.021075 | 19.7506 | 0.19493
2025-05-19 16:11 | 708 | Remove | 2025-05-19 | 16:11 | ST | GS | - | 37.5 | g | 0 | 111.1 | 12.072 | 1200.3 | 57209 | 5:54 | 30.3 | 2.08 m/s | 20.8 | 31.5 | 4.13 m/s | 16.2 |  | 2.08 | m/s |  | 4.13 | m/s | 5.9044 | 0.010002 | 6.8476 |  | -1 | 37.5 | 0.0375 | 182.6022 | 6.4171 | 5.3316 | 0.019634 | 19.7702 | 0.18968
2025-05-19 16:11 | 709 | Remove | 2025-05-19 | 16:11 | ST | GS | - | 39 | g | 0 | 111.2 | 12.046 | 1197.8 | 57219 | 5:55 | 30.3 | 2.35 m/s | 21.7 | 31.6 | 4.16 m/s | 16.4 |  | 2.35 | m/s |  | 4.16 | m/s | 5.9128 | 0.0099817 | 6.8576 |  | 1.5 | 39 | 0.039 | 175.835 | 6.6947 | 5.4264 | 0.023142 | 19.7934 | 0.19704
2025-05-19 16:12 | 710 | Remove | 2025-05-19 | 16:12 | ST | GS | - | 38 | g | 0 | 111.1 | 12.05 | 1197.7 | 57229 | 5:55 | 30.4 | 1.86 m/s | 23.2 | 31.6 | 4.0 m/s | 18.2 |  | 1.86 | m/s |  | 4 | m/s | 5.9211 | 0.0099808 | 6.8675 |  | -1 | 38 | 0.038 | 180.7249 | 7.1963 | 6.022 | 0.019689 | 19.8131 | 0.19179
2025-05-19 16:12 | 711 | Remove | 2025-05-19 | 16:12 | ST | GS | - | 37.5 | g | 0 | 111.1 | 12.071 | 1199.7 | 57239 | 5:56 | 30.4 | 1.86 m/s | 21.9 | 31.6 | 4.09 m/s | 17.7 |  | 1.86 | m/s |  | 4.09 | m/s | 5.9294 | 0.0099975 | 6.8775 |  | -0.5 | 37.5 | 0.0375 | 183.4012 | 6.7931 | 5.8566 | 0.018586 | 19.8316 | 0.18909
2025-05-19 16:13 | 712 | Remove | 2025-05-19 | 16:13 | US | GS | - | 38.5 | g | 0 | 111.1 | 12.074 | 1200.5 | 57249 | 5:56 | 30.4 | 1.91 m/s | 21.4 | 31.6 | 4.1 m/s | 16.5 |  | 1.91 | m/s |  | 4.1 | m/s | 5.9378 | 0.010004 | 6.8875 |  | 1 | 38.5 | 0.0385 | 178.8973 | 6.638 | 5.4595 | 0.01865 | 19.8503 | 0.19395
2025-05-19 16:13 | 713 | Remove | 2025-05-19 | 16:13 | ST | GS | - | 42.5 | g | 0 | 111.1 | 12.073 | 1199.8 | 57259 | 5:57 | 30.4 | 2.19 m/s | 21.3 | 31.6 | 3.8 m/s | 16.3 |  | 2.19 | m/s |  | 3.8 | m/s | 5.9461 | 0.0099983 | 6.8975 |  | 4 | 42.5 | 0.0425 | 162.2952 | 6.607 | 5.3933 | 0.021284 | 19.8716 | 0.21387
2025-05-19 16:14 | 714 | Remove | 2025-05-19 | 16:14 | ST | GS | - | 42 | g | 0 | 111 | 12.061 | 1198.5 | 57269 | 5:57 | 30.4 | 2.5 m/s | 21 | 31.6 | 3.97 m/s | 16.2 |  | 2.5 | m/s |  | 3.97 | m/s | 5.9544 | 0.0099875 | 6.9075 |  | -0.5 | 42 | 0.042 | 164.4651 | 6.5139 | 5.3602 | 0.023954 | 19.8955 | 0.2111
2025-05-19 16:14 | 715 | Remove | 2025-05-19 | 16:14 | ST | GS | - | 41 | g | 0 | 111.2 | 12.04 | 1197.2 | 57279 | 5:58 | 30.4 | 2.6 m/s | 20.9 | 31.6 | 4.12 m/s | 15.6 |  | 2.6 | m/s |  | 4.12 | m/s | 5.9628 | 0.0099767 | 6.9175 |  | -1 | 41 | 0.041 | 168.7198 | 6.4829 | 5.1617 | 0.024794 | 19.9203 | 0.20582
2025-05-19 16:15 | 716 | Remove | 2025-05-19 | 16:15 | US | GS | - | 44 | g | 0 | 111.1 | 12.06 | 1199 | 57289 | 5:58 | 30.4 | 2.37 m/s | 20.8 | 31.6 | 3.84 m/s | 16.1 |  | 2.37 | m/s |  | 3.84 | m/s | 5.9711 | 0.0099917 | 6.9275 |  | 3 | 44 | 0.044 | 157.4432 | 6.4519 | 5.3271 | 0.022492 | 19.9428 | 0.22063
2025-05-19 16:15 | 717 | Remove | 2025-05-19 | 16:15 | US | GS | - | 44 | g | 0 | 110.9 | 12.072 | 1200.3 | 57299 | 5:59 | 30.4 | 2.02 m/s | 20 | 31.6 | 3.86 m/s | 16.3 |  | 2.02 | m/s |  | 3.86 | m/s | 5.9794 | 0.010002 | 6.9375 |  | 0 | 44 | 0.044 | 157.6705 | 6.2037 | 5.3933 | 0.018433 | 19.9613 | 0.22043
2025-05-19 16:16 | 718 | Remove | 2025-05-19 | 16:16 | ST | GS | - | 39 | g | 0 | 111.1 | 12.054 | 1198.8 | 57309 | 5:59 | 30.4 | 2.04 m/s | 21 | 31.6 | 4.16 m/s | 16.8 |  | 2.04 | m/s |  | 4.16 | m/s | 5.9878 | 0.00999 | 6.9475 |  | -5 | 39 | 0.039 | 178.1409 | 6.5139 | 5.5588 | 0.019547 | 19.9808 | 0.19519
2025-05-19 16:16 | 719 | Remove | 2025-05-19 | 16:16 | ST | GS | - | 39 | g | 0 | 111.2 | 12.085 | 1202.5 | 57319 | 6:00 | 30.4 | 2.48 m/s | 20.5 | 31.6 | 4.23 m/s | 15.8 |  | 2.48 | m/s |  | 4.23 | m/s | 5.9961 | 0.010021 | 6.9575 |  | 0 | 39 | 0.039 | 178.3978 | 6.3588 | 5.2279 | 0.023197 | 20.004 | 0.19496
2025-05-19 16:17 | 720 | Remove | 2025-05-19 | 16:17 | ST | GS | - | 40.5 | g | 0 | 111 | 12.086 | 1202 | 57330 | 6:00 | 30.4 | 2.16 m/s | 20.9 | 31.6 | 4.41 m/s | 16 |  | 2.16 | m/s |  | 4.41 | m/s | 6.0044 | 0.010017 | 6.9675 |  | 1.5 | 40.5 | 0.0405 | 172.0378 | 6.4829 | 5.2941 | 0.020598 | 20.0246 | 0.20225
2025-05-19 16:17 | 721 | Keep | 2025-05-19 | 16:17 | ST | GS | - | 39 | g | 0 | 111 | 12.121 | 1205.6 | 57340 | 6:01 | 30.4 | 2.02 m/s | 20.9 | 31.6 | 3.98 m/s | 15.6 |  | 2.02 | m/s |  | 3.98 | m/s | 6.0128 | 0.010047 | 6.9776 |  | -1.5 | 39 | 0.039 | 178.9123 | 6.4829 | 5.1617 | 0.019263 | 20.0439 | 0.19457
2025-05-19 16:18 | 722 | Remove | 2025-05-19 | 16:18 | US | GS | - | 47 | g | 0 | 111.1 | 12.091 | 1202.3 | 57350 | 6:01 | 30.4 | 1.98 m/s | 20.9 | 31.6 | 4.1 m/s | 16 |  | 1.98 | m/s |  | 4.1 | m/s | 6.0211 | 0.010019 | 6.9876 |  | 8 | 47 | 0.047 | 148.6723 | 6.4829 | 5.2941 | 0.018882 | 20.0627 | 0.23427
2025-05-19 16:18 | 723 | Remove | 2025-05-19 | 16:18 | US | GS | - | 40.5 | g | 0 | 111.1 | 12.036 | 1196.3 | 57360 | 6:02 | 30.4 | 2.04 m/s | 21.8 | 31.6 | 4.35 m/s | 17.5 |  | 2.04 | m/s |  | 4.35 | m/s | 6.0297 | 0.0099692 | 6.9976 |  | -6.5 | 40.5 | 0.0405 | 172.7794 | 6.7621 | 5.7904 | 0.020291 | 20.083 | 0.20166
2025-05-19 16:19 | 724 | Remove | 2025-05-19 | 16:19 | ST | GS | - | 42.5 | g | 0 | 111.1 | 12.045 | 1197.3 | 57370 | 6:02 | 30.4 | 2.8 m/s | 20.9 | 31.6 | 3.96 m/s | 16.8 |  | 2.8 | m/s |  | 3.96 | m/s | 6.0381 | 0.0099775 | 7.0075 |  | 2 | 42.5 | 0.0425 | 164.8834 | 6.4829 | 5.5588 | 0.026701 | 20.1097 | 0.21134
2025-05-19 16:19 | 725 | Remove | 2025-05-19 | 16:19 | ST | GS | - | 40 | g | 0 | 111.2 | 12.066 | 1199.5 | 57380 | 6:03 | 30.4 | 2.01 m/s | 21 | 31.6 | 3.86 m/s | 16.2 |  | 2.01 | m/s |  | 3.86 | m/s | 6.0464 | 0.0099958 | 7.0175 |  | -2.5 | 40 | 0.04 | 175.4385 | 6.5139 | 5.3602 | 0.019259 | 20.129 | 0.19872
2025-05-19 16:20 | 726 | Remove | 2025-05-19 | 16:20 | ST | GS | - | 39 | g | 0 | 111.2 | 12.052 | 1199.4 | 57390 | 6:03 | 30.4 | 2.18 m/s | 22.7 | 31.6 | 4.09 m/s | 16.3 |  | 2.18 | m/s |  | 4.09 | m/s | 6.0547 | 0.009995 | 7.0275 |  | -1 | 39 | 0.039 | 180.1932 | 7.0412 | 5.3933 | 0.022579 | 20.1516 | 0.19353
2025-05-19 16:20 | 727 | Remove | 2025-05-19 | 16:20 | US | GS | - | 43 | g | 0 | 111 | 12.081 | 1200.6 | 57400 | 6:04 | 30.4 | 2.47 m/s | 20.7 | 31.6 | 3.92 m/s | 16.2 |  | 2.47 | m/s |  | 3.92 | m/s | 6.0631 | 0.010005 | 7.0375 |  | 4 | 43 | 0.043 | 163.6637 | 6.4209 | 5.3602 | 0.023329 | 20.1749 | 0.21314
2025-05-19 16:21 | 728 | Remove | 2025-05-19 | 16:21 | ST | GS | - | 41.5 | g | 0 | 111.2 | 12.063 | 1200.3 | 57410 | 6:04 | 30.4 | 1.82 m/s | 21.3 | 31.6 | 4.6 m/s | 16.8 |  | 1.82 | m/s |  | 4.6 | m/s | 6.0714 | 0.010002 | 7.0475 |  | -1.5 | 41.5 | 0.0415 | 169.8203 | 6.607 | 5.5588 | 0.017688 | 20.1926 | 0.20552
2025-05-19 16:21 | 729 | Remove | 2025-05-19 | 16:21 | ST | GS | - | 40 | g | 0 | 111.1 | 12.085 | 1201 | 57420 | 6:05 | 30.4 | 1.95 m/s | 21.4 | 31.6 | 4.12 m/s | 16.6 |  | 1.95 | m/s |  | 4.12 | m/s | 6.0797 | 0.010008 | 7.0576 |  | -1.5 | 40 | 0.04 | 176.4388 | 6.638 | 5.4926 | 0.01904 | 20.2116 | 0.19791
2025-05-19 16:22 | 730 | Remove | 2025-05-19 | 16:22 | ST | GS | - | 44 | g | 0 | 111.1 | 12.05 | 1197.4 | 57430 | 6:05 | 30.4 | 1.89 m/s | 20.8 | 31.6 | 4.12 m/s | 16.8 |  | 1.89 | m/s |  | 4.12 | m/s | 6.0881 | 0.0099783 | 7.0675 |  | 4 | 44 | 0.044 | 160.6257 | 6.4519 | 5.5588 | 0.017937 | 20.2296 | 0.2175
2025-05-19 16:22 | 731 | Remove | 2025-05-19 | 16:22 | ST | GS | - | 40.5 | g | 0 | 111.2 | 12.057 | 1199.4 | 57440 | 6:06 | 30.4 | 1.86 m/s | 21.7 | 31.6 | 4.15 m/s | 17 |  | 1.86 | m/s |  | 4.15 | m/s | 6.0964 | 0.009995 | 7.0775 |  | -3.5 | 40.5 | 0.0405 | 174.7537 | 6.7311 | 5.6249 | 0.018416 | 20.248 | 0.20002
2025-05-19 16:23 | 732 | Remove | 2025-05-19 | 16:23 | ST | GS | - | 40 | g | 0 | 111.2 | 12.057 | 1198.8 | 57450 | 6:06 | 30.4 | 1.97 m/s | 21.1 | 31.6 | 4.23 m/s | 16.5 |  | 1.97 | m/s |  | 4.23 | m/s | 6.1047 | 0.00999 | 7.0875 |  | -0.5 | 40 | 0.04 | 177.1879 | 6.5449 | 5.4595 | 0.018966 | 20.267 | 0.19737
2025-05-19 16:23 | 733 | Remove | 2025-05-19 | 16:23 | ST | GS | - | 39 | g | 0 | 111.2 | 12.068 | 1199.9 | 57460 | 6:07 | 30.4 | 1.87 m/s | 23.3 | 31.6 | 4.26 m/s | 17.6 |  | 1.87 | m/s |  | 4.26 | m/s | 6.1131 | 0.0099992 | 7.0975 |  | -1 | 39 | 0.039 | 181.9875 | 7.2273 | 5.8235 | 0.01988 | 20.2868 | 0.19224
2025-05-19 16:24 | 734 | Remove | 2025-05-19 | 16:24 | ST | GS | - | 42 | g | 0 | 111.1 | 12.072 | 1200.8 | 57470 | 6:07 | 30.4 | 1.97 m/s | 21.9 | 31.6 | 3.94 m/s | 16.5 |  | 1.97 | m/s |  | 3.94 | m/s | 6.1214 | 0.010007 | 7.1075 |  | 3 | 42 | 0.042 | 169.2267 | 6.7931 | 5.4595 | 0.019685 | 20.3065 | 0.20683
2025-05-19 16:24 | 735 | Remove | 2025-05-19 | 16:24 | ST | GS | - | 42 | g | 0 | 111.1 | 12.117 | 1206 | 57480 | 6:08 | 30.4 | 1.83 m/s | 20.3 | 31.6 | 4.1 m/s | 16 |  | 1.83 | m/s |  | 4.1 | m/s | 6.1297 | 0.01005 | 7.1176 |  | 0 | 42 | 0.042 | 169.466 | 6.2968 | 5.2941 | 0.01695 | 20.3235 | 0.20666
2025-05-19 16:25 | 736 | Remove | 2025-05-19 | 16:25 | US | GS | - | 41.5 | g | 0 | 111 | 12.108 | 1204 | 57490 | 6:08 | 30.5 | 1.93 m/s | 21.5 | 31.6 | 3.77 m/s | 18.9 |  | 1.93 | m/s |  | 3.77 | m/s | 6.1381 | 0.010033 | 7.1276 |  | -0.5 | 41.5 | 0.0415 | 171.7495 | 6.7051 | 6.2536 | 0.019036 | 20.3425 | 0.20401
2025-05-19 16:25 | 737 | Remove | 2025-05-19 | 16:25 | ST | GS | - | 40 | g | 0 | 111.1 | 12.098 | 1204.1 | 57500 | 6:09 | 30.5 | 1.74 m/s | 23.7 | 31.6 | 3.94 m/s | 18 |  | 1.74 | m/s |  | 3.94 | m/s | 6.1464 | 0.010034 | 7.1376 |  | -1.5 | 40 | 0.04 | 178.4409 | 7.3913 | 5.9558 | 0.018918 | 20.3614 | 0.19645
2025-05-19 16:26 | 738 | Remove | 2025-05-19 | 16:26 | US | GS | - | 54 | g | 0 | 111.1 | 12.106 | 1204.6 | 57510 | 6:09 | 30.5 | 2.04 m/s | 21.8 | 31.5 | 4.04 m/s | 15.7 |  | 2.04 | m/s |  | 4.04 | m/s | 6.1547 | 0.010038 | 7.1477 |  | 14 | 54 | 0.054 | 132.3644 | 6.7987 | 5.167 | 0.020401 | 20.3818 | 0.26494
2025-05-19 16:26 | 739 | Remove | 2025-05-19 | 16:26 | ST | GS | - | 42.5 | g | 0 | 111 | 12.069 | 1199.4 | 57520 | 6:10 | 30.5 | 1.82 m/s | 21.8 | 31.5 | 3.86 m/s | 17.7 |  | 1.82 | m/s |  | 3.86 | m/s | 6.1631 | 0.009995 | 7.1577 |  | -11.5 | 42.5 | 0.0425 | 168.4158 | 6.7987 | 5.8252 | 0.018201 | 20.4 | 0.20833
2025-05-19 16:27 | 740 | Remove | 2025-05-19 | 16:27 | US | GS | - | 40.5 | g | 0 | 111.1 | 12.108 | 1204.4 | 57530 | 6:10 | 30.5 | 2.08 m/s | 20.8 | 31.6 | 3.8 m/s | 15.8 |  | 2.08 | m/s |  | 3.8 | m/s | 6.1717 | 0.010037 | 7.1677 |  | -2 | 40.5 | 0.0405 | 176.9804 | 6.4868 | 5.2279 | 0.019847 | 20.4199 | 0.19834
2025-05-19 16:28 | 741 | Remove | 2025-05-19 | 16:27 | US | GS | - | 38 | g | 0 | 111 | 12.069 | 1199.7 | 57540 | 6:11 | 30.4 | 2.0 m/s | 20.3 | 31.6 | 3.94 m/s | 16.3 |  | 2 | m/s |  | 3.94 | m/s | 6.18 | 0.0099975 | 7.1777 |  | -2.5 | 38 | 0.038 | 188.887 | 6.2968 | 5.3933 | 0.018525 | 20.4384 | 0.18592
2025-05-19 16:28 | 742 | Remove | 2025-05-19 | 16:28 | ST | GS | - | 40 | g | 0 | 111.1 | 12.092 | 1202.2 | 57550 | 6:11 | 30.4 | 1.83 m/s | 20 | 31.6 | 3.97 m/s | 16.3 |  | 1.83 | m/s |  | 3.97 | m/s | 6.1883 | 0.010018 | 7.1877 |  | 2 | 40 | 0.04 | 179.6931 | 6.2037 | 5.3933 | 0.0167 | 20.4551 | 0.19555
2025-05-19 16:28 | 743 | Remove | 2025-05-19 | 16:28 | ST | GS | - | 42 | g | 0 | 111 | 12.09 | 1203 | 57560 | 6:12 | 30.4 | 2.08 m/s | 20.9 | 31.6 | 3.93 m/s | 16.4 |  | 2.08 | m/s |  | 3.93 | m/s | 6.1967 | 0.010025 | 7.1977 |  | 2 | 42 | 0.042 | 171.375 | 6.4829 | 5.4264 | 0.019835 | 20.4749 | 0.20513
2025-05-19 16:29 | 744 | Remove | 2025-05-19 | 16:29 | ST | GS | - | 41.5 | g | 0 | 111 | 12.086 | 1201.7 | 57570 | 6:12 | 30.5 | 2.11 m/s | 19.5 | 31.6 | 4.04 m/s | 16.4 |  | 2.11 | m/s |  | 4.04 | m/s | 6.205 | 0.010014 | 7.2078 |  | -0.5 | 41.5 | 0.0415 | 173.681 | 6.0814 | 5.4264 | 0.018875 | 20.4938 | 0.2025
2025-05-19 16:30 | 745 | Remove | 2025-05-19 | 16:29 | US | GS | - | 49.5 | g | 0 | 111 | 12.097 | 1203.1 | 57581 | 6:13 | 30.5 | 2.19 m/s | 19.4 | 31.6 | 3.79 m/s | 15.2 |  | 2.19 | m/s |  | 3.79 | m/s | 6.2133 | 0.010026 | 7.2178 |  | 8 | 49.5 | 0.0495 | 145.8139 | 6.0502 | 5.0294 | 0.01949 | 20.5133 | 0.24131
2025-05-19 16:30 | 746 | Remove | 2025-05-19 | 16:30 | ST | GS | - | 41 | g | 0 | 111 | 12.069 | 1199.5 | 57591 | 6:13 | 30.5 | 2.04 m/s | 20 | 31.6 | 4.0 m/s | 16.7 |  | 2.04 | m/s |  | 4 | m/s | 6.2217 | 0.0099958 | 7.2278 |  | -8.5 | 41 | 0.041 | 176.2874 | 6.2373 | 5.5257 | 0.018717 | 20.532 | 0.19969
2025-05-19 16:30 | 747 | Remove | 2025-05-19 | 16:31 | US | GS | - | 46.5 | g | 0 | 111 | 12.099 | 1202.5 | 57601 | 6:14 | 30.4 | 1.85 m/s | 20.4 | 31.6 | 3.86 m/s | 16.3 |  | 1.85 | m/s |  | 3.86 | m/s | 6.23 | 0.010021 | 7.2378 |  | 5.5 | 46.5 | 0.0465 | 155.6517 | 6.3278 | 5.3933 | 0.01722 | 20.5492 | 0.22629
2025-05-19 16:31 | 748 | Remove | 2025-05-19 | 16:31 | ST | GS | - | 41.5 | g | 0 | 111 | 12.085 | 1201.3 | 57611 | 6:14 | 30.4 | 1.95 m/s | 20.1 | 31.5 | 3.77 m/s | 15.2 |  | 1.95 | m/s |  | 3.77 | m/s | 6.2383 | 0.010011 | 7.2478 |  | -5 | 41.5 | 0.0415 | 174.6462 | 6.2348 | 5.0025 | 0.017884 | 20.5671 | 0.20178
2025-05-19 16:32 | 749 | Remove | 2025-05-19 | 16:32 | US | GS | - | 42 | g | 0 | 111 | 12.06 | 1198.7 | 57621 | 6:15 | 30.4 | 1.97 m/s | 19.6 | 31.5 | 3.76 m/s | 17.6 |  | 1.97 | m/s |  | 3.76 | m/s | 6.2467 | 0.0099892 | 7.2578 |  | 0.5 | 42 | 0.042 | 172.8049 | 6.0797 | 5.7923 | 0.017618 | 20.5847 | 0.20403
2025-05-19 16:32 | 750 | Remove | 2025-05-19 | 16:32 | ST | GS | - | 42 | g | 0 | 111 | 12.084 | 1201.4 | 57631 | 6:15 | 30.4 | 1.75 m/s | 20.4 | 31.5 | 4.75 m/s | 15.8 |  | 1.75 | m/s |  | 4.75 | m/s | 6.255 | 0.010012 | 7.2678 |  | 0 | 42 | 0.042 | 173.0433 | 6.3278 | 5.1999 | 0.016289 | 20.601 | 0.20387
2025-05-19 16:32 | 751 | Keep | 2025-05-19 | 16:33 | US | GS | - | 43.5 | g | 0 | 111 | 12.088 | 1201.9 | 57641 | 6:16 | 30.4 | 1.89 m/s | 20.7 | 31.5 | 4.13 m/s | 16 |  | 1.89 | m/s |  | 4.13 | m/s | 6.2633 | 0.010016 | 7.2778 |  | 1.5 | 43.5 | 0.0435 | 167.3065 | 6.4209 | 5.2658 | 0.017851 | 20.6189 | 0.21097
2025-05-19 16:33 | 752 | Remove | 2025-05-19 | 16:33 | ST | GS | - | 41.5 | g | 0 | 111 | 12.105 | 1204.6 | 57651 | 6:16 | 30.4 | 1.79 m/s | 20.7 | 31.6 | 4.18 m/s | 16 |  | 1.79 | m/s |  | 4.18 | m/s | 6.2717 | 0.010038 | 7.2879 |  | -2 | 41.5 | 0.0415 | 175.6113 | 6.4209 | 5.2941 | 0.016906 | 20.6358 | 0.20111
2025-05-19 16:34 | 753 | Remove | 2025-05-19 | 16:34 | ST | GS | - | 44 | g | 0 | 111 | 12.087 | 1201.4 | 57661 | 6:17 | 30.5 | 1.79 m/s | 21.3 | 31.6 | 3.81 m/s | 16.5 |  | 1.79 | m/s |  | 3.81 | m/s | 6.28 | 0.010012 | 7.2979 |  | 2.5 | 44 | 0.044 | 165.861 | 6.6428 | 5.4595 | 0.017491 | 20.6533 | 0.21304
2025-05-19 16:34 | 754 | Remove | 2025-05-19 | 16:34 | US | GS | - | 44 | g | 0 | 111.1 | 12.013 | 1193.7 | 57671 | 6:17 | 30.5 | 2.35 m/s | 21.4 | 31.6 | 3.72 m/s | 17.2 |  | 2.35 | m/s |  | 3.72 | m/s | 6.2883 | 0.0099475 | 7.3078 |  | 0 | 44 | 0.044 | 166.087 | 6.674 | 5.6911 | 0.02307 | 20.6763 | 0.2128
2025-05-19 16:35 | 755 | Remove | 2025-05-19 | 16:35 | ST | GS | - | 42 | g | 0 | 111 | 12.077 | 1200.6 | 57681 | 6:18 | 30.4 | 1.97 m/s | 20 | 31.5 | 4.15 m/s | 16.5 |  | 1.97 | m/s |  | 4.15 | m/s | 6.2967 | 0.010005 | 7.3178 |  | -2 | 42 | 0.042 | 174.2342 | 6.2037 | 5.4303 | 0.017977 | 20.6943 | 0.20295
2025-05-19 16:35 | 756 | Remove | 2025-05-19 | 16:35 | ST | GS | - | 41.5 | g | 0 | 111 | 12.066 | 1198.8 | 57691 | 6:18 | 30.4 | 1.77 m/s | 22.1 | 31.5 | 4.16 m/s | 17 |  | 1.77 | m/s |  | 4.16 | m/s | 6.305 | 0.00999 | 7.3278 |  | -0.5 | 41.5 | 0.0415 | 176.5741 | 6.8551 | 5.5949 | 0.017848 | 20.7122 | 0.20037
2025-05-19 16:36 | 757 | Remove | 2025-05-19 | 16:36 | US | GS | - | 43 | g | 0 | 111 | 12.067 | 1199 | 57701 | 6:19 | 30.4 | 2.0 m/s | 21.4 | 31.5 | 3.9 m/s | 16.5 |  | 2 | m/s |  | 3.9 | m/s | 6.3136 | 0.0099917 | 7.3378 |  | 1.5 | 43 | 0.043 | 170.6469 | 6.638 | 5.4303 | 0.019529 | 20.7317 | 0.20741
2025-05-19 16:36 | 758 | Remove | 2025-05-19 | 16:36 | US | GS | - | 46 | g | 0 | 111 | 12.092 | 1202.6 | 57711 | 6:19 | 30.4 | 1.83 m/s | 20.1 | 31.5 | 4.06 m/s | 16.3 |  | 1.83 | m/s |  | 4.06 | m/s | 6.3219 | 0.010022 | 7.3478 |  | 3 | 46 | 0.046 | 159.7356 | 6.2348 | 5.3645 | 0.016783 | 20.7485 | 0.2217
2025-05-19 16:37 | 759 | Remove | 2025-05-19 | 16:37 | ST | GS | - | 42 | g | 0 | 110.9 | 12.091 | 1201.9 | 57721 | 6:20 | 30.4 | 1.93 m/s | 21 | 31.5 | 4.16 m/s | 16.6 |  | 1.93 | m/s |  | 4.16 | m/s | 6.3303 | 0.010016 | 7.3579 |  | -4 | 42 | 0.042 | 175.187 | 6.5139 | 5.4632 | 0.018493 | 20.767 | 0.20224
2025-05-19 16:37 | 760 | Remove | 2025-05-19 | 16:37 | ST | GS | - | 46 | g | 0 | 111 | 12.018 | 1193.9 | 57731 | 6:20 | 30.4 | 1.98 m/s | 23.8 | 31.5 | 3.84 m/s | 18.4 |  | 1.98 | m/s |  | 3.84 | m/s | 6.3386 | 0.0099492 | 7.3678 |  | 4 | 46 | 0.046 | 160.1696 | 7.3824 | 6.0556 | 0.021501 | 20.7885 | 0.22128
2025-05-19 16:38 | 761 | Remove | 2025-05-19 | 16:38 | ST | GS | - | 42.5 | g | 0 | 111 | 12.048 | 1196.4 | 57741 | 6:21 | 30.4 | 1.77 m/s | 22 | 31.5 | 3.75 m/s | 17.9 |  | 1.77 | m/s |  | 3.75 | m/s | 6.3469 | 0.00997 | 7.3778 |  | -3.5 | 42.5 | 0.0425 | 173.5947 | 6.8241 | 5.8911 | 0.017767 | 20.8062 | 0.20427
2025-05-19 16:38 | 762 | Remove | 2025-05-19 | 16:38 | ST | GS | - | 42 | g | 0 | 111 | 12.035 | 1195.3 | 57751 | 6:21 | 30.4 | 1.77 m/s | 21.4 | 31.5 | 4.18 m/s | 17.4 |  | 1.77 | m/s |  | 4.18 | m/s | 6.3553 | 0.0099608 | 7.3877 |  | -0.5 | 42 | 0.042 | 175.8984 | 6.638 | 5.7265 | 0.017283 | 20.8235 | 0.2017
2025-05-19 16:39 | 763 | Remove | 2025-05-19 | 16:39 | US | GS | - | 42 | g | 0 | 110.9 | 12.086 | 1200.7 | 57761 | 6:22 | 30.4 | 1.98 m/s | 23.5 | 31.5 | 3.85 m/s | 16.9 |  | 1.98 | m/s |  | 3.85 | m/s | 6.3636 | 0.010006 | 7.3977 |  | 0 | 42 | 0.042 | 176.1367 | 7.2894 | 5.562 | 0.02123 | 20.8448 | 0.20149
2025-05-19 16:39 | 764 | Remove | 2025-05-19 | 16:39 | ST | GS | - | 42 | g | 0 | 110.9 | 12.09 | 1201.9 | 57771 | 6:22 | 30.4 | 1.59 m/s | 22.2 | 31.5 | 4.15 m/s | 16.6 |  | 1.59 | m/s |  | 4.15 | m/s | 6.3719 | 0.010016 | 7.4078 |  | 0 | 42 | 0.042 | 176.3751 | 6.8861 | 5.4632 | 0.016106 | 20.8609 | 0.20133
2025-05-19 16:40 | 765 | Remove | 2025-05-19 | 16:40 | ST | GS | - | 43 | g | 0 | 111 | 12.077 | 1200.3 | 57781 | 6:23 | 30.4 | 1.68 m/s | 21.9 | 31.5 | 4.16 m/s | 17.6 |  | 1.68 | m/s |  | 4.16 | m/s | 6.3803 | 0.010002 | 7.4178 |  | 1 | 43 | 0.043 | 172.506 | 6.7931 | 5.7923 | 0.016787 | 20.8776 | 0.20596
2025-05-19 16:40 | 766 | Remove | 2025-05-19 | 16:40 | ST | GS | - | 41 | g | 0 | 111 | 12.049 | 1197.1 | 57791 | 6:23 | 30.4 | 1.67 m/s | 22.9 | 31.5 | 3.92 m/s | 18.2 |  | 1.67 | m/s |  | 3.92 | m/s | 6.3886 | 0.0099758 | 7.4277 |  | -2 | 41 | 0.041 | 181.1642 | 7.1033 | 5.9898 | 0.017449 | 20.8951 | 0.19622
2025-05-19 16:41 | 767 | Remove | 2025-05-19 | 16:41 | ST | GS | - | 43.5 | g | 0 | 111 | 12.04 | 1196 | 57801 | 6:24 | 30.4 | 1.66 m/s | 25.7 | 31.5 | 4.03 m/s | 20.1 |  | 1.66 | m/s |  | 4.03 | m/s | 6.3969 | 0.0099667 | 7.4377 |  | 2.5 | 43.5 | 0.0435 | 170.9816 | 7.9718 | 6.6151 | 0.019466 | 20.9146 | 0.20799
2025-05-19 16:41 | 768 | Remove | 2025-05-19 | 16:41 | ST | GS | - | 45 | g | 0 | 110.9 | 12.079 | 1200.4 | 57811 | 6:24 | 30.4 | 1.75 m/s | 24.3 | 31.5 | 3.97 m/s | 16.9 |  | 1.75 | m/s |  | 3.97 | m/s | 6.4053 | 0.010003 | 7.4477 |  | 1.5 | 45 | 0.045 | 165.5045 | 7.5375 | 5.562 | 0.019403 | 20.934 | 0.21496
2025-05-19 16:42 | 769 | Remove | 2025-05-19 | 16:42 | ST | GS | - | 43 | g | 0 | 110.9 | 12.095 | 1202.2 | 57821 | 6:25 | 30.4 | 1.64 m/s | 21.8 | 31.5 | 4.09 m/s | 17.3 |  | 1.64 | m/s |  | 4.09 | m/s | 6.4136 | 0.010018 | 7.4577 |  | -2 | 43 | 0.043 | 173.4354 | 6.7621 | 5.6936 | 0.016313 | 20.9503 | 0.20525
2025-05-19 16:42 | 770 | Remove | 2025-05-19 | 16:42 | ST | GS | - | 45 | g | 0 | 111.1 | 12.045 | 1196.9 | 57831 | 6:25 | 30.4 | 1.93 m/s | 20.7 | 31.5 | 3.86 m/s | 16.4 |  | 1.93 | m/s |  | 3.86 | m/s | 6.4219 | 0.0099742 | 7.4677 |  | 2 | 45 | 0.045 | 165.9488 | 6.4209 | 5.3974 | 0.018229 | 20.9685 | 0.21461
2025-05-19 16:43 | 771 | Remove | 2025-05-19 | 16:43 | US | GS | - | 45.5 | g | 0 | 111.2 | 12.041 | 1196.9 | 57841 | 6:26 | 30.4 | 1.68 m/s | 20.7 | 31.5 | 3.86 m/s | 16.4 |  | 1.68 | m/s |  | 3.86 | m/s | 6.4303 | 0.0099742 | 7.4777 |  | 0.5 | 45.5 | 0.0455 | 164.3444 | 6.4209 | 5.3974 | 0.015867 | 20.9844 | 0.21683
2025-05-19 16:43 | 772 | Remove | 2025-05-19 | 16:43 | US | GS | - | 43.5 | g | 0 | 111.1 | 12.071 | 1200.3 | 57851 | 6:26 | 30.4 | 1.81 m/s | 21 | 31.5 | 3.77 m/s | 17.2 |  | 1.81 | m/s |  | 3.77 | m/s | 6.4386 | 0.010002 | 7.4877 |  | -2 | 43.5 | 0.0435 | 172.1304 | 6.5139 | 5.6607 | 0.017343 | 21.0017 | 0.20713
2025-05-19 16:44 | 773 | Remove | 2025-05-19 | 16:44 | US | GS | - | 52.5 | g | 0 | 111.1 | 12.019 | 1193.8 | 57861 | 6:27 | 30.4 | 2.02 m/s | 21 | 31.4 | 3.79 m/s | 16.5 |  | 2.02 | m/s |  | 3.79 | m/s | 6.4469 | 0.0099483 | 7.4976 |  | 9 | 52.5 | 0.0525 | 142.8118 | 6.5139 | 5.4013 | 0.019355 | 21.0211 | 0.24975
2025-05-19 16:44 | 774 | Remove | 2025-05-19 | 16:44 | US | GS | - | 43.5 | g | 0 | 111.1 | 12.072 | 1200.4 | 57871 | 6:27 | 30.4 | 1.75 m/s | 20.9 | 31.4 | 3.85 m/s | 17.4 |  | 1.75 | m/s |  | 3.85 | m/s | 6.4556 | 0.010003 | 7.5076 |  | -9 | 43.5 | 0.0435 | 172.5891 | 6.4829 | 5.6959 | 0.016688 | 21.0378 | 0.20677
2025-05-19 16:45 | 775 | Remove | 2025-05-19 | 16:45 | ST | GS | - | 44.5 | g | 0 | 111.2 | 12.033 | 1196.4 | 57881 | 6:28 | 30.4 | 1.85 m/s | 23 | 31.4 | 4.06 m/s | 18 |  | 1.85 | m/s |  | 4.06 | m/s | 6.4639 | 0.00997 | 7.5176 |  | 1 | 44.5 | 0.0445 | 168.9347 | 7.1343 | 5.8923 | 0.019414 | 21.0572 | 0.21133
2025-05-19 16:45 | 776 | Remove | 2025-05-19 | 16:45 | US | GS | - | 46 | g | 0 | 111.1 | 12.046 | 1197.7 | 57891 | 6:28 | 30.4 | 1.75 m/s | 21.3 | 31.4 | 4.15 m/s | 16.6 |  | 1.75 | m/s |  | 4.15 | m/s | 6.4722 | 0.0099808 | 7.5276 |  | 1.5 | 46 | 0.046 | 163.643 | 6.607 | 5.434 | 0.017008 | 21.0742 | 0.21828
2025-05-19 16:46 | 777 | Remove | 2025-05-19 | 16:46 | ST | GS | - | 44.5 | g | 0 | 111.2 | 12.019 | 1194.3 | 57901 | 6:29 | 30.4 | 2.08 m/s | 20.5 | 31.4 | 4.06 m/s | 16.1 |  | 2.08 | m/s |  | 4.06 | m/s | 6.4806 | 0.0099525 | 7.5375 |  | -1.5 | 44.5 | 0.0445 | 169.3827 | 6.3588 | 5.2703 | 0.019456 | 21.0936 | 0.21096
2025-05-19 16:46 | 778 | Remove | 2025-05-19 | 16:46 | ST | GS | - | 44.5 | g | 0 | 111.2 | 12.026 | 1195.2 | 57911 | 6:29 | 30.4 | 1.94 m/s | 23.6 | 31.4 | 4.06 m/s | 16.1 |  | 1.94 | m/s |  | 4.06 | m/s | 6.4889 | 0.00996 | 7.5475 |  | 0 | 44.5 | 0.0445 | 169.6065 | 7.3204 | 5.2703 | 0.02089 | 21.1145 | 0.21076
2025-05-19 16:47 | 779 | Remove | 2025-05-19 | 16:47 | ST | GS | - | 45 | g | 0 | 111 | 12.036 | 1196.6 | 57921 | 6:30 | 30.4 | 1.7 m/s | 21.7 | 31.4 | 3.8 m/s | 17.7 |  | 1.7 | m/s |  | 3.8 | m/s | 6.4972 | 0.0099717 | 7.5575 |  | 0.5 | 45 | 0.045 | 167.9436 | 6.7311 | 5.7941 | 0.016832 | 21.1314 | 0.21295
2025-05-19 16:47 | 780 | Remove | 2025-05-19 | 16:47 | ST | GS | - | 48 | g | 0 | 111 | 12.058 | 1198.4 | 57931 | 6:30 | 30.4 | 2.2 m/s | 20.4 | 31.4 | 3.98 m/s | 16.8 |  | 2.2 | m/s |  | 3.98 | m/s | 6.5056 | 0.0099867 | 7.5674 |  | 3 | 48 | 0.048 | 157.6551 | 6.3278 | 5.4995 | 0.020478 | 21.1518 | 0.22693
2025-05-19 16:48 | 781 | Keep | 2025-05-19 | 16:48 | US | GS | - | 45 | g | 0 | 111.1 | 12.05 | 1197.9 | 57941 | 6:31 | 30.4 | 1.74 m/s | 22.1 | 31.4 | 4.13 m/s | 16.2 |  | 1.74 | m/s |  | 4.13 | m/s | 6.5139 | 0.0099825 | 7.5774 |  | -3 | 45 | 0.045 | 168.3873 | 6.8551 | 5.3031 | 0.017546 | 21.1694 | 0.21257
2025-05-19 16:48 | 782 | Remove | 2025-05-19 | 16:48 | ST | GS | - | 44.5 | g | 0 | 111 | 12.067 | 1199.9 | 57951 | 6:31 | 30.4 | 1.79 m/s | 21.3 | 31.4 | 3.98 m/s | 17.2 |  | 1.79 | m/s |  | 3.98 | m/s | 6.5222 | 0.0099992 | 7.5874 |  | -0.5 | 44.5 | 0.0445 | 170.504 | 6.607 | 5.6304 | 0.017396 | 21.1868 | 0.21004
2025-05-19 16:49 | 783 | Remove | 2025-05-19 | 16:49 | ST | GS | - | 48.5 | g | 0 | 110.9 | 12.078 | 1199.9 | 57961 | 6:32 | 30.4 | 2.06 m/s | 20.8 | 31.4 | 4.24 m/s | 17.3 |  | 2.06 | m/s |  | 4.24 | m/s | 6.5306 | 0.0099992 | 7.5974 |  | 4 | 48.5 | 0.0485 | 156.648 | 6.4519 | 5.6631 | 0.01955 | 21.2063 | 0.22871
2025-05-19 16:49 | 784 | Remove | 2025-05-19 | 16:49 | ST | GS | - | 49 | g | 0 | 111 | 12.064 | 1198.5 | 57971 | 6:32 | 30.4 | 1.94 m/s | 20.5 | 31.4 | 4.16 m/s | 16.1 |  | 1.94 | m/s |  | 4.16 | m/s | 6.5389 | 0.0099875 | 7.6074 |  | 0.5 | 49 | 0.049 | 155.2534 | 6.3588 | 5.2703 | 0.018146 | 21.2245 | 0.23087
2025-05-19 16:50 | 785 | Remove | 2025-05-19 | 16:50 | ST | GS | - | 44 | g | 0 | 111 | 12.054 | 1197.8 | 57981 | 6:33 | 30.4 | 1.71 m/s | 20.3 | 31.4 | 4.16 m/s | 16 |  | 1.71 | m/s |  | 4.16 | m/s | 6.5472 | 0.0099817 | 7.6174 |  | -5 | 44 | 0.044 | 173.1227 | 6.2968 | 5.2376 | 0.015839 | 21.2403 | 0.20715
2025-05-19 16:50 | 786 | Remove | 2025-05-19 | 16:50 | US | GS | - | 44.5 | g | 0 | 111 | 12.06 | 1198.5 | 57991 | 6:33 | 30.4 | 1.98 m/s | 21.1 | 31.4 | 3.9 m/s | 17.5 |  | 1.98 | m/s |  | 3.9 | m/s | 6.5556 | 0.0099875 | 7.6274 |  | 0.5 | 44.5 | 0.0445 | 171.4019 | 6.5449 | 5.7286 | 0.019062 | 21.2594 | 0.20932
2025-05-19 16:51 | 787 | Remove | 2025-05-19 | 16:51 | ST | GS | - | 46 | g | 0 | 111 | 12.047 | 1196.7 | 58001 | 6:34 | 30.4 | 1.78 m/s | 21.1 | 31.4 | 4.1 m/s | 16.8 |  | 1.78 | m/s |  | 4.1 | m/s | 6.5639 | 0.0099725 | 7.6374 |  | 1.5 | 46 | 0.046 | 166.0295 | 6.5449 | 5.4995 | 0.017137 | 21.2765 | 0.2162
2025-05-19 16:51 | 788 | Remove | 2025-05-19 | 16:51 | ST | GS | - | 46 | g | 0 | 111 | 12.042 | 1197 | 58011 | 6:34 | 30.4 | 2.08 m/s | 21.3 | 31.4 | 4.29 m/s | 17.7 |  | 2.08 | m/s |  | 4.29 | m/s | 6.5722 | 0.009975 | 7.6473 |  | 0 | 46 | 0.046 | 166.2463 | 6.607 | 5.7941 | 0.020215 | 21.2967 | 0.216
2025-05-19 16:52 | 789 | Remove | 2025-05-19 | 16:52 | ST | GS | - | 44.5 | g | 0 | 111 | 12.048 | 1197.2 | 58021 | 6:35 | 30.4 | 1.74 m/s | 20.8 | 31.4 | 3.84 m/s | 16.5 |  | 1.74 | m/s |  | 3.84 | m/s | 6.5806 | 0.0099767 | 7.6573 |  | -1.5 | 44.5 | 0.0445 | 172.0743 | 6.4519 | 5.4013 | 0.016513 | 21.3132 | 0.20879
2025-05-19 16:52 | 790 | Remove | 2025-05-19 | 16:52 | ST | GS | - | 46.5 | g | 0 | 111 | 12.039 | 1195.8 | 58031 | 6:35 | 30.4 | 1.86 m/s | 20.4 | 31.4 | 4.04 m/s | 16.6 |  | 1.86 | m/s |  | 4.04 | m/s | 6.5889 | 0.009965 | 7.6673 |  | 2 | 46.5 | 0.0465 | 164.8876 | 6.3278 | 5.434 | 0.017313 | 21.3306 | 0.218
2025-05-19 16:53 | 791 | Remove | 2025-05-19 | 16:53 | US | GS | - | 47.5 | g | 0 | 111 | 12.058 | 1198.8 | 58041 | 6:36 | 30.4 | 2.05 m/s | 20 | 31.4 | 4.15 m/s | 16.9 |  | 2.05 | m/s |  | 4.15 | m/s | 6.5975 | 0.00999 | 7.6773 |  | 1 | 47.5 | 0.0475 | 161.6266 | 6.2037 | 5.5322 | 0.018707 | 21.3493 | 0.22249
2025-05-19 16:53 | 792 | Remove | 2025-05-19 | 16:53 | ST | GS | - | 45 | g | 0 | 111.1 | 12.056 | 1199 | 58051 | 6:36 | 30.4 | 1.66 m/s | 20.1 | 31.4 | 3.77 m/s | 15.8 |  | 1.66 | m/s |  | 3.77 | m/s | 6.6058 | 0.0099917 | 7.6873 |  | -2.5 | 45 | 0.045 | 170.8279 | 6.2348 | 5.1721 | 0.015224 | 21.3645 | 0.21063
2025-05-19 16:54 | 793 | Remove | 2025-05-19 | 16:54 | US | GS | - | 48 | g | 0 | 111 | 12.079 | 1200.9 | 58061 | 6:37 | 30.4 | 1.78 m/s | 20.8 | 31.4 | 4.23 m/s | 16.2 |  | 1.78 | m/s |  | 4.23 | m/s | 6.6142 | 0.010008 | 7.6973 |  | 3 | 48 | 0.048 | 160.3596 | 6.4519 | 5.3031 | 0.016893 | 21.3814 | 0.22449
2025-05-19 16:54 | 794 | Remove | 2025-05-19 | 16:54 | US | GS | - | 46 | g | 0 | 111.1 | 12.027 | 1194.7 | 58072 | 6:37 | 30.4 | 1.94 m/s | 20.1 | 31.4 | 3.84 m/s | 15.7 |  | 1.94 | m/s |  | 3.84 | m/s | 6.6225 | 0.0099558 | 7.7072 |  | -2 | 46 | 0.046 | 167.5482 | 6.2348 | 5.1394 | 0.017792 | 21.3992 | 0.21496
2025-05-19 16:55 | 795 | Remove | 2025-05-19 | 16:55 | US | GS | - | 47.5 | g | 0 | 111.1 | 12.028 | 1195 | 58081 | 6:38 | 30.4 | 2.52 m/s | 20.2 | 31.4 | 4.07 m/s | 16.6 |  | 2.52 | m/s |  | 4.07 | m/s | 6.6308 | 0.0099583 | 7.7172 |  | 1.5 | 47.5 | 0.0475 | 162.4669 | 6.2658 | 5.434 | 0.023226 | 21.4224 | 0.22173
2025-05-19 16:55 | 796 | Remove | 2025-05-19 | 16:55 | ST | GS | - | 45 | g | 0 | 110.9 | 12.028 | 1194.3 | 58091 | 6:38 | 30.4 | 2.09 m/s | 20.6 | 31.4 | 4.01 m/s | 16.4 |  | 2.09 | m/s |  | 4.01 | m/s | 6.6392 | 0.0099525 | 7.7271 |  | -2.5 | 45 | 0.045 | 171.714 | 6.3898 | 5.3685 | 0.019644 | 21.442 | 0.20987
2025-05-19 16:56 | 797 | Remove | 2025-05-19 | 16:56 | US | GS | - | 44 | g | 0 | 111 | 12.019 | 1193.8 | 58101 | 6:39 | 30.4 | 1.85 m/s | 21.4 | 31.4 | 4.27 m/s | 16.1 |  | 1.85 | m/s |  | 4.27 | m/s | 6.6475 | 0.0099483 | 7.7371 |  | -1 | 44 | 0.044 | 175.8427 | 6.638 | 5.2703 | 0.018064 | 21.4601 | 0.20503
2025-05-19 16:56 | 798 | Remove | 2025-05-19 | 16:56 | ST | GS | - | 46 | g | 0 | 110.9 | 12.034 | 1195.5 | 58111 | 6:39 | 30.3 | 2.67 m/s | 20.4 | 31.4 | 3.92 m/s | 16.5 |  | 2.67 | m/s |  | 3.92 | m/s | 6.6558 | 0.0099625 | 7.747 |  | 2 | 46 | 0.046 | 168.4139 | 6.2937 | 5.4013 | 0.024718 | 21.4848 | 0.2141
2025-05-19 16:57 | 799 | Remove | 2025-05-19 | 16:57 | US | GS | - | 50.5 | g | 0 | 111.1 | 12.012 | 1193.9 | 58121 | 6:40 | 30.3 | 2.04 m/s | 19.8 | 31.4 | 3.86 m/s | 16.3 |  | 2.04 | m/s |  | 3.86 | m/s | 6.6644 | 0.0099492 | 7.757 |  | 4.5 | 50.5 | 0.0505 | 153.6037 | 6.1086 | 5.3358 | 0.01833 | 21.5031 | 0.23485
2025-05-19 16:57 | 800 | Remove | 2025-05-19 | 16:57 | US | GS | - | 46.5 | g | 0 | 111.1 | 11.988 | 1190.4 | 58131 | 6:40 | 30.2 | 2.18 m/s | 21.4 | 31.3 | 3.55 m/s | 15.9 |  | 2.18 | m/s |  | 3.55 | m/s | 6.6728 | 0.00992 | 7.7669 |  | -4 | 46.5 | 0.0465 | 167.0303 | 6.5666 | 5.177 | 0.021057 | 21.5242 | 0.21604
2025-05-19 16:58 | 801 | Remove | 2025-05-19 | 16:58 | ST | GS | - | 49 | g | 0 | 111.2 | 11.988 | 1190.9 | 58141 | 6:41 | 30.1 | 2.48 m/s | 20.2 | 31.3 | 3.88 m/s | 16.8 |  | 2.48 | m/s |  | 3.88 | m/s | 6.6811 | 0.0099242 | 7.7768 |  | 2.5 | 49 | 0.049 | 158.7109 | 6.1649 | 5.47 | 0.022489 | 21.5467 | 0.22741
2025-05-19 16:58 | 802 | Remove | 2025-05-19 | 16:58 | US | GS | - | 45.5 | g | 0 | 111.1 | 11.96 | 1188 | 58151 | 6:41 | 30 | 2.81 m/s | 21.3 | 31.3 | 4.15 m/s | 16.3 |  | 2.81 | m/s |  | 4.15 | m/s | 6.6894 | 0.0099 | 7.7867 |  | -3.5 | 45.5 | 0.0455 | 171.137 | 6.4654 | 5.3072 | 0.026724 | 21.5734 | 0.21091
2025-05-19 16:59 | 803 | Remove | 2025-05-19 | 16:59 | US | GS | - | 45.5 | g | 0 | 111.2 | 11.998 | 1192.2 | 58161 | 6:42 | 29.9 | 2.27 m/s | 21.8 | 31.3 | 3.97 m/s | 16.7 |  | 2.27 | m/s |  | 3.97 | m/s | 6.6978 | 0.009935 | 7.7967 |  | 0 | 45.5 | 0.0455 | 171.3553 | 6.5814 | 5.4375 | 0.021976 | 21.5954 | 0.21069
2025-05-19 16:59 | 804 | Remove | 2025-05-19 | 16:59 | ST | GS | - | 45.5 | g | 0 | 111.1 | 11.996 | 1192.1 | 58171 | 6:42 | 29.9 | 2.05 m/s | 23.4 | 31.2 | 4.21 m/s | 16.7 |  | 2.05 | m/s |  | 4.21 | m/s | 6.7061 | 0.0099342 | 7.8066 |  | 0 | 45.5 | 0.0455 | 171.5737 | 7.0644 | 5.4083 | 0.021303 | 21.6167 | 0.21049
2025-05-19 17:00 | 805 | Remove | 2025-05-19 | 17:00 | US | GS | - | 46.5 | g | 0 | 111 | 11.983 | 1189.9 | 58181 | 6:43 | 29.9 | 2.02 m/s | 22.7 | 31.2 | 4.13 m/s | 17.4 |  | 2.02 | m/s |  | 4.13 | m/s | 6.7144 | 0.0099158 | 7.8165 |  | 1 | 46.5 | 0.0465 | 168.0972 | 6.8531 | 5.635 | 0.020363 | 21.6371 | 0.21491
2025-05-19 17:00 | 806 | Remove | 2025-05-19 | 17:00 | ST | GS | - | 47.5 | g | 0 | 111.1 | 11.961 | 1187.9 | 58191 | 6:43 | 29.8 | 2.58 m/s | 22.6 | 31.2 | 4.04 m/s | 17.4 |  | 2.58 | m/s |  | 4.04 | m/s | 6.7228 | 0.0098992 | 7.8264 |  | 1 | 47.5 | 0.0475 | 164.7667 | 6.786 | 5.635 | 0.025753 | 21.6628 | 0.21927
2025-05-19 17:01 | 807 | Remove | 2025-05-19 | 17:01 | ST | GS | - | 46.5 | g | 0 | 111.1 | 11.983 | 1190.9 | 58201 | 6:44 | 29.8 | 2.06 m/s | 22 | 31.2 | 4.06 m/s | 16.4 |  | 2.06 | m/s |  | 4.06 | m/s | 6.7311 | 0.0099242 | 7.8363 |  | -1 | 46.5 | 0.0465 | 168.5235 | 6.6058 | 5.3112 | 0.020017 | 21.6828 | 0.21446
2025-05-19 17:01 | 808 | Remove | 2025-05-19 | 17:01 | US | GS | - | 47.5 | g | 0 | 111.1 | 11.966 | 1188.3 | 58211 | 6:44 | 29.8 | 1.97 m/s | 21.7 | 31.2 | 3.98 m/s | 17 |  | 1.97 | m/s |  | 3.98 | m/s | 6.7394 | 0.0099025 | 7.8462 |  | 1 | 47.5 | 0.0475 | 165.1841 | 6.5158 | 5.5055 | 0.018881 | 21.7017 | 0.21888
2025-05-19 17:02 | 809 | Remove | 2025-05-19 | 17:02 | ST | GS | - | 48.5 | g | 0 | 111.2 | 11.978 | 1189.4 | 58221 | 6:45 | 29.7 | 2.2 m/s | 22 | 31.1 | 4.24 m/s | 17.3 |  | 2.2 | m/s |  | 4.24 | m/s | 6.7481 | 0.0099117 | 7.8562 |  | 1 | 48.5 | 0.0485 | 161.9826 | 6.57 | 5.5726 | 0.021261 | 21.723 | 0.22327
2025-05-19 17:02 | 810 | Remove | 2025-05-19 | 17:02 | ST | GS | - | 46.5 | g | 0 | 111.2 | 11.963 | 1188.2 | 58231 | 6:45 | 29.7 | 2.16 m/s | 20.7 | 31.1 | 4.0 m/s | 16.6 |  | 2.16 | m/s |  | 4 | m/s | 6.7564 | 0.0099017 | 7.8661 |  | -2 | 46.5 | 0.0465 | 169.1625 | 6.1818 | 5.3471 | 0.019641 | 21.7426 | 0.21387
2025-05-19 17:03 | 811 | Keep | 2025-05-19 | 17:03 | ST | GS | - | 47.5 | g | 0 | 111.3 | 11.931 | 1185 | 58241 | 6:46 | 29.7 | 2.09 m/s | 21.5 | 31.1 | 4.03 m/s | 17.2 |  | 2.09 | m/s |  | 4.03 | m/s | 6.7647 | 0.009875 | 7.8759 |  | 1 | 47.5 | 0.0475 | 165.8091 | 6.4207 | 5.5404 | 0.019739 | 21.7624 | 0.21827
2025-05-19 17:03 | 812 | Remove | 2025-05-19 | 17:03 | ST | GS | - | 47 | g | 0 | 111.3 | 11.947 | 1186.8 | 58251 | 6:46 | 29.6 | 2.83 m/s | 20.3 | 31.1 | 4.1 m/s | 16.6 |  | 2.83 | m/s |  | 4.1 | m/s | 6.7731 | 0.00989 | 7.8858 |  | -0.5 | 47 | 0.047 | 167.7835 | 6.0295 | 5.3471 | 0.0251 | 21.7875 | 0.21572
2025-05-19 17:04 | 813 | Remove | 2025-05-19 | 17:04 | ST | GS | - | 47.5 | g | 0 | 111.3 | 11.938 | 1185.8 | 58261 | 6:47 | 29.6 | 2.02 m/s | 20.9 | 31.1 | 4.01 m/s | 16.1 |  | 2.02 | m/s |  | 4.01 | m/s | 6.7814 | 0.0098817 | 7.8957 |  | 0.5 | 47.5 | 0.0475 | 166.2254 | 6.2077 | 5.1861 | 0.018445 | 21.8059 | 0.21783
2025-05-19 17:04 | 814 | Remove | 2025-05-19 | 17:04 | ST | GS | - | 50.5 | g | 0 | 111.2 | 11.936 | 1186 | 58270 | 6:47 | 29.6 | 2.12 m/s | 20 | 31 | 4.03 m/s | 16.5 |  | 2.12 | m/s |  | 4.03 | m/s | 6.7897 | 0.0098833 | 7.9056 |  | 3 | 50.5 | 0.0505 | 156.5463 | 5.9404 | 5.2864 | 0.018525 | 21.8244 | 0.23139
2025-05-19 17:05 | 815 | Remove | 2025-05-19 | 17:05 | ST | GS | - | 49 | g | 0 | 111.3 | 11.936 | 1184.9 | 58280 | 6:48 | 29.6 | 2.08 m/s | 21.1 | 31 | 4.07 m/s | 16 |  | 2.08 | m/s |  | 4.07 | m/s | 6.7981 | 0.0098742 | 7.9155 |  | -1.5 | 49 | 0.049 | 161.54 | 6.2671 | 5.1262 | 0.019175 | 21.8436 | 0.22432
2025-05-19 17:05 | 816 | Remove | 2025-05-19 | 17:05 | US | GS | - | 45 | g | 0 | 111.3 | 11.919 | 1183.6 | 58290 | 6:48 | 29.6 | 2.42 m/s | 21.3 | 31 | 4.2 m/s | 16.1 |  | 2.42 | m/s |  | 4.2 | m/s | 6.8064 | 0.0098633 | 7.9253 |  | -4 | 45 | 0.045 | 176.1183 | 6.3265 | 5.1583 | 0.022521 | 21.8661 | 0.2058
2025-05-19 17:06 | 817 | Remove | 2025-05-19 | 17:06 | US | GS | - | 47.5 | g | 0 | 111.3 | 11.921 | 1183.5 | 58300 | 6:49 | 29.6 | 2.09 m/s | 22.7 | 31 | 4.13 m/s | 16.7 |  | 2.09 | m/s |  | 4.13 | m/s | 6.8147 | 0.0098625 | 7.9352 |  | 2.5 | 47.5 | 0.0475 | 167.0566 | 6.7423 | 5.3505 | 0.020728 | 21.8868 | 0.21703
2025-05-19 17:06 | 818 | Remove | 2025-05-19 | 17:06 | ST | GS | - | 50.5 | g | 0 | 111.2 | 11.958 | 1187.3 | 58310 | 6:49 | 29.6 | 2.23 m/s | 21.3 | 31 | 4.27 m/s | 17 |  | 2.23 | m/s |  | 4.27 | m/s | 6.8231 | 0.0098942 | 7.9451 |  | 3 | 50.5 | 0.0505 | 157.3283 | 6.3265 | 5.4466 | 0.020753 | 21.9076 | 0.23051
2025-05-19 17:07 | 819 | Remove | 2025-05-19 | 17:07 | ST | GS | - | 52.5 | g | 0 | 111.3 | 11.924 | 1184.1 | 58320 | 6:50 | 29.6 | 2.44 m/s | 23.4 | 31 | 3.97 m/s | 16.1 |  | 2.44 | m/s |  | 3.97 | m/s | 6.8314 | 0.0098675 | 7.9549 |  | 2 | 52.5 | 0.0525 | 151.5228 | 6.9502 | 5.1583 | 0.024946 | 21.9325 | 0.23937
2025-05-19 17:07 | 820 | Remove | 2025-05-19 | 17:07 | ST | GS | - | 47.5 | g | 0 | 111.3 | 11.894 | 1180.7 | 58330 | 6:50 | 29.6 | 1.97 m/s | 22.7 | 30.9 | 3.92 m/s | 17.8 |  | 1.97 | m/s |  | 3.92 | m/s | 6.8397 | 0.0098392 | 7.9648 |  | -5 | 47.5 | 0.0475 | 167.6798 | 6.7423 | 5.6723 | 0.019538 | 21.9521 | 0.21638
2025-05-19 17:08 | 821 | Remove | 2025-05-19 | 17:08 | US | GS | - | 47.5 | g | 0 | 111.3 | 11.91 | 1181.8 | 58340 | 6:51 | 29.6 | 2.09 m/s | 24.1 | 30.9 | 4.07 m/s | 18.2 |  | 2.09 | m/s |  | 4.07 | m/s | 6.8481 | 0.0098483 | 7.9746 |  | 0 | 47.5 | 0.0475 | 167.8871 | 7.1582 | 5.7998 | 0.022006 | 21.9741 | 0.21616
2025-05-19 17:08 | 822 | Remove | 2025-05-19 | 17:08 | ST | GS | - | 49.5 | g | 0 | 111.2 | 11.905 | 1181.6 | 58350 | 6:51 | 29.6 | 2.4 m/s | 23 | 30.9 | 4.04 m/s | 17.7 |  | 2.4 | m/s |  | 4.04 | m/s | 6.8564 | 0.0098467 | 7.9845 |  | 2 | 49.5 | 0.0495 | 161.3027 | 6.8314 | 5.6404 | 0.024117 | 21.9982 | 0.22502
2025-05-19 17:09 | 823 | Remove | 2025-05-19 | 17:09 | ST | GS | - | 48.5 | g | 0 | 111.3 | 11.919 | 1183.5 | 58359 | 6:52 | 29.6 | 2.13 m/s | 21.5 | 30.9 | 3.97 m/s | 16.7 |  | 2.13 | m/s |  | 3.97 | m/s | 6.8647 | 0.0098625 | 7.9943 |  | -1 | 48.5 | 0.0485 | 164.8319 | 6.3859 | 5.3218 | 0.020008 | 22.0182 | 0.22027
2025-05-19 17:09 | 824 | Remove | 2025-05-19 | 17:09 | ST | GS | - | 54.5 | g | 0 | 111.2 | 11.933 | 1184.4 | 58369 | 6:52 | 29.6 | 2.55 m/s | 22.5 | 30.9 | 4.0 m/s | 16.8 |  | 2.55 | m/s |  | 4 | m/s | 6.8731 | 0.00987 | 8.0042 |  | 6 | 54.5 | 0.0545 | 146.8663 | 6.6829 | 5.3536 | 0.025067 | 22.0433 | 0.24724
2025-05-19 17:10 | 825 | Remove | 2025-05-19 | 17:10 | ST | GS | - | 47.5 | g | 0 | 111.3 | 11.9 | 1181.3 | 58379 | 6:53 | 29.6 | 2.25 m/s | 21.9 | 30.9 | 3.92 m/s | 16.2 |  | 2.25 | m/s |  | 3.92 | m/s | 6.8814 | 0.0098442 | 8.0141 |  | -7 | 47.5 | 0.0475 | 168.7171 | 6.5047 | 5.1624 | 0.021528 | 22.0648 | 0.21527
2025-05-19 17:10 | 826 | Remove | 2025-05-19 | 17:10 | ST | GS | - | 49 | g | 0 | 111.2 | 11.903 | 1181.4 | 58389 | 6:53 | 29.6 | 2.33 m/s | 23.3 | 30.9 | 4.0 m/s | 18 |  | 2.33 | m/s |  | 4 | m/s | 6.89 | 0.009845 | 8.0239 |  | 1.5 | 49 | 0.049 | 163.7532 | 6.9205 | 5.736 | 0.023719 | 22.0885 | 0.22183
2025-05-19 17:11 | 827 | Remove | 2025-05-19 | 17:11 | ST | GS | - | 48.5 | g | 0 | 111.2 | 11.902 | 1180.9 | 58399 | 6:54 | 29.6 | 2.12 m/s | 22.2 | 30.9 | 3.75 m/s | 16.9 |  | 2.12 | m/s |  | 3.75 | m/s | 6.8983 | 0.0098408 | 8.0337 |  | -0.5 | 48.5 | 0.0485 | 165.6442 | 6.5938 | 5.3855 | 0.020562 | 22.1091 | 0.21937
2025-05-19 17:11 | 828 | Remove | 2025-05-19 | 17:11 | ST | GS | - | 48 | g | 0 | 111.1 | 11.9 | 1180.6 | 58409 | 6:54 | 29.6 | 2.2 m/s | 21.7 | 30.9 | 3.88 m/s | 17.2 |  | 2.2 | m/s |  | 3.88 | m/s | 6.9067 | 0.0098383 | 8.0436 |  | -0.5 | 48 | 0.048 | 167.5747 | 6.4453 | 5.4811 | 0.020858 | 22.13 | 0.2169
2025-05-19 17:12 | 829 | Remove | 2025-05-19 | 17:12 | ST | GS | - | 48.5 | g | 0 | 111.2 | 11.896 | 1180.3 | 58419 | 6:55 | 29.5 | 1.98 m/s | 23.5 | 30.9 | 4.13 m/s | 19 |  | 1.98 | m/s |  | 4.13 | m/s | 6.915 | 0.0098358 | 8.0534 |  | 0.5 | 48.5 | 0.0485 | 166.0499 | 6.9421 | 6.0547 | 0.020219 | 22.1502 | 0.21896
2025-05-19 17:12 | 830 | Remove | 2025-05-19 | 17:12 | US | GS | - | 48 | g | 0 | 111.1 | 11.896 | 1179.8 | 58429 | 6:55 | 29.5 | 2.05 m/s | 22.7 | 30.9 | 4.12 m/s | 16.8 |  | 2.05 | m/s |  | 4.12 | m/s | 6.9233 | 0.0098317 | 8.0633 |  | -0.5 | 48 | 0.048 | 167.9844 | 6.7058 | 5.3536 | 0.020221 | 22.1704 | 0.2165
2025-05-19 17:13 | 831 | Remove | 2025-05-19 | 17:13 | ST | GS | - | 51 | g | 0 | 111.3 | 11.925 | 1184.1 | 58439 | 6:56 | 29.6 | 2.3 m/s | 21.6 | 30.9 | 3.88 m/s | 18.5 |  | 2.3 | m/s |  | 3.88 | m/s | 6.9317 | 0.0098675 | 8.0731 |  | 3 | 51 | 0.051 | 158.2965 | 6.4156 | 5.8954 | 0.021705 | 22.1921 | 0.22981
2025-05-19 17:13 | 832 | Remove | 2025-05-19 | 17:13 | ST | GS | - | 52.5 | g | 0 | 111.1 | 11.891 | 1179.1 | 58449 | 6:56 | 29.6 | 2.11 m/s | 27.3 | 30.9 | 3.81 m/s | 19.7 |  | 2.11 | m/s |  | 3.81 | m/s | 6.94 | 0.0098258 | 8.0829 |  | 1.5 | 52.5 | 0.0525 | 153.9609 | 8.1086 | 6.2778 | 0.025167 | 22.2173 | 0.2363
2025-05-19 17:14 | 833 | Remove | 2025-05-19 | 17:14 | ST | GS | - | 48.5 | g | 0 | 111.2 | 11.899 | 1180.8 | 58458 | 6:57 | 29.6 | 2.23 m/s | 22.6 | 30.8 | 3.88 m/s | 18.9 |  | 2.23 | m/s |  | 3.88 | m/s | 6.9483 | 0.00984 | 8.0928 |  | -4 | 48.5 | 0.0485 | 166.8615 | 6.7126 | 5.9905 | 0.022019 | 22.2393 | 0.21808
2025-05-19 17:14 | 834 | Remove | 2025-05-19 | 17:14 | ST | GS | - | 48 | g | 0 | 111.1 | 11.942 | 1185.1 | 58468 | 6:57 | 29.6 | 2.09 m/s | 21.8 | 30.8 | 3.67 m/s | 18.3 |  | 2.09 | m/s |  | 3.67 | m/s | 6.9567 | 0.0098758 | 8.1027 |  | -0.5 | 48 | 0.048 | 168.8054 | 6.475 | 5.8003 | 0.019906 | 22.2592 | 0.21564
2025-05-19 17:15 | 835 | Remove | 2025-05-19 | 17:15 | ST | GS | - | 48.5 | g | 0 | 111.1 | 11.876 | 1177.8 | 58478 | 6:58 | 29.6 | 2.02 m/s | 23.9 | 30.8 | 4.2 m/s | 16.3 |  | 2.02 | m/s |  | 4.2 | m/s | 6.965 | 0.009815 | 8.1125 |  | 0.5 | 48.5 | 0.0485 | 167.2675 | 7.0988 | 5.1664 | 0.021093 | 22.2803 | 0.21768
2025-05-19 17:15 | 836 | Remove | 2025-05-19 | 17:15 | US | GS | - | 49.5 | g | 0 | 111.2 | 11.908 | 1181.3 | 58488 | 6:58 | 29.5 | 2.25 m/s | 24.8 | 30.9 | 4.06 m/s | 20.4 |  | 2.25 | m/s |  | 4.06 | m/s | 6.9733 | 0.0098442 | 8.1223 |  | 1 | 49.5 | 0.0495 | 164.0873 | 7.3261 | 6.5008 | 0.024247 | 22.3045 | 0.22193
2025-05-19 17:16 | 837 | Remove | 2025-05-19 | 17:16 | US | GS | - | 56.5 | g | 0 | 111.2 | 11.916 | 1182.5 | 58498 | 6:59 | 29.5 | 2.18 m/s | 21.6 | 30.8 | 3.96 m/s | 18.5 |  | 2.18 | m/s |  | 3.96 | m/s | 6.9817 | 0.0098542 | 8.1322 |  | 7 | 56.5 | 0.0565 | 143.9323 | 6.3808 | 5.8637 | 0.020461 | 22.325 | 0.25308
2025-05-19 17:16 | 838 | Remove | 2025-05-19 | 17:16 | US | GS | - | 53.5 | g | 0 | 111.2 | 11.899 | 1180.8 | 58508 | 6:59 | 29.5 | 2.09 m/s | 23.5 | 30.8 | 3.89 m/s | 17.8 |  | 2.09 | m/s |  | 3.89 | m/s | 6.99 | 0.00984 | 8.142 |  | -3 | 53.5 | 0.0535 | 152.1872 | 6.9421 | 5.6418 | 0.021342 | 22.3463 | 0.23941
2025-05-19 17:17 | 839 | Remove | 2025-05-19 | 17:17 | ST | GS | - | 51.5 | g | 0 | 111.1 | 11.911 | 1181.5 | 58517 | 7:00 | 29.5 | 2.38 m/s | 22.5 | 30.8 | 4.1 m/s | 17.1 |  | 2.38 | m/s |  | 4.1 | m/s | 6.9983 | 0.0098458 | 8.1519 |  | -2 | 51.5 | 0.0515 | 158.2885 | 6.6467 | 5.42 | 0.023269 | 22.3696 | 0.23022
2025-05-19 17:17 | 840 | Remove | 2025-05-19 | 17:17 | US | GS | - | 53.5 | g | 0 | 111.2 | 11.914 | 1182.4 | 58527 | 7:00 | 29.6 | 2.38 m/s | 21.3 | 30.8 | 3.84 m/s | 18.1 |  | 2.38 | m/s |  | 3.84 | m/s | 7.0067 | 0.0098533 | 8.1617 |  | 2 | 53.5 | 0.0535 | 152.5554 | 6.3265 | 5.7369 | 0.022148 | 22.3918 | 0.23893
2025-05-19 17:18 | 841 | Keep | 2025-05-19 | 17:18 | ST | GS | - | 51 | g | 0 | 111.3 | 11.884 | 1179.2 | 58537 | 7:01 | 29.6 | 2.16 m/s | 22.1 | 30.8 | 3.81 m/s | 17 |  | 2.16 | m/s |  | 3.81 | m/s | 7.015 | 0.0098267 | 8.1715 |  | -2.5 | 51 | 0.051 | 160.2263 | 6.5641 | 5.3883 | 0.020856 | 22.4126 | 0.22755
2025-05-19 17:18 | 842 | Remove | 2025-05-19 | 17:18 | US | GS | - | 50 | g | 0 | 111.2 | 11.919 | 1182.6 | 58547 | 7:01 | 29.5 | 2.44 m/s | 24 | 30.8 | 3.96 m/s | 18.4 |  | 2.44 | m/s |  | 3.96 | m/s | 7.0233 | 0.009855 | 8.1814 |  | -1 | 50 | 0.05 | 163.6279 | 7.0898 | 5.832 | 0.025446 | 22.4381 | 0.22284
2025-05-19 17:19 | 843 | Remove | 2025-05-19 | 17:19 | ST | GS | - | 52 | g | 0 | 111.1 | 11.93 | 1183.6 | 58557 | 7:02 | 29.5 | 2.27 m/s | 22.7 | 30.8 | 3.88 m/s | 17.1 |  | 2.27 | m/s |  | 3.88 | m/s | 7.0317 | 0.0098633 | 8.1913 |  | 2 | 52 | 0.052 | 157.5242 | 6.7058 | 5.42 | 0.022391 | 22.4604 | 0.23152
2025-05-19 17:19 | 844 | Remove | 2025-05-19 | 17:19 | US | GS | - | 57 | g | 0 | 111.2 | 11.904 | 1180.7 | 58567 | 7:02 | 29.5 | 2.2 m/s | 21.5 | 30.8 | 3.89 m/s | 17.4 |  | 2.2 | m/s |  | 3.89 | m/s | 7.0403 | 0.0098392 | 8.2011 |  | 5 | 57 | 0.057 | 143.8789 | 6.3513 | 5.515 | 0.020553 | 22.481 | 0.25355
2025-05-19 17:20 | 845 | Remove | 2025-05-19 | 17:20 | US | GS | - | 48.5 | g | 0 | 111.3 | 11.863 | 1176.5 | 58577 | 7:03 | 29.5 | 2.33 m/s | 21.7 | 30.7 | 3.92 m/s | 16.8 |  | 2.33 | m/s |  | 3.92 | m/s | 7.0486 | 0.0098042 | 8.2109 |  | -8.5 | 48.5 | 0.0485 | 169.2969 | 6.4103 | 5.2962 | 0.02197 | 22.503 | 0.21553
2025-05-19 17:20 | 846 | Remove | 2025-05-19 | 17:20 | US | GS | - | 58.5 | g | 0 | 111.2 | 11.875 | 1177.5 | 58587 | 7:03 | 29.5 | 2.34 m/s | 23.3 | 30.7 | 3.84 m/s | 18 |  | 2.34 | m/s |  | 3.84 | m/s | 7.0569 | 0.0098125 | 8.2207 |  | 10 | 58.5 | 0.0585 | 140.525 | 6.883 | 5.6745 | 0.023692 | 22.5267 | 0.25969
2025-05-19 17:21 | 847 | Remove | 2025-05-19 | 17:21 | US | GS | - | 67.5 | g | 0 | 111.3 | 11.897 | 1180.4 | 58596 | 7:04 | 29.5 | 2.91 m/s | 23 | 30.7 | 3.97 m/s | 18.6 |  | 2.91 | m/s |  | 3.97 | m/s | 7.0653 | 0.0098367 | 8.2306 |  | 9 | 67.5 | 0.0675 | 121.9341 | 6.7944 | 5.8637 | 0.029083 | 22.5557 | 0.29926
2025-05-19 17:21 | 848 | Remove | 2025-05-19 | 17:21 | US | GS | - | 67.5 | g | 0 | 111.2 | 11.899 | 1180.5 | 58606 | 7:04 | 29.5 | 2.83 m/s | 22.5 | 30.7 | 4.06 m/s | 18.2 |  | 2.83 | m/s |  | 4.06 | m/s | 7.0736 | 0.0098375 | 8.2404 |  | 0 | 67.5 | 0.0675 | 122.0798 | 6.6467 | 5.7376 | 0.027669 | 22.5834 | 0.29889
2025-05-19 17:22 | 849 | Remove | 2025-05-19 | 17:22 | US | GS | - | 54.5 | g | 0 | 111.4 | 11.891 | 1180 | 58616 | 7:05 | 29.5 | 2.81 m/s | 21.3 | 30.6 | 3.76 m/s | 17 |  | 2.81 | m/s |  | 3.76 | m/s | 7.0819 | 0.0098333 | 8.2502 |  | -13 | 54.5 | 0.0545 | 151.3802 | 6.2922 | 5.3305 | 0.026008 | 22.6094 | 0.24105
2025-05-19 17:22 | 850 | Remove | 2025-05-19 | 17:22 | ST | GS | - | 53 | g | 0 | 111.3 | 11.904 | 1181.4 | 58626 | 7:05 | 29.5 | 2.31 m/s | 21 | 30.6 | 3.67 m/s | 16.8 |  | 2.31 | m/s |  | 3.67 | m/s | 7.0903 | 0.009845 | 8.2601 |  | -1.5 | 53 | 0.053 | 155.8503 | 6.2036 | 5.2677 | 0.021079 | 22.6305 | 0.2342
2025-05-19 17:23 | 851 | Remove | 2025-05-19 | 17:23 | US | GS | - | 51.5 | g | 0 | 111.2 | 11.89 | 1179.2 | 58636 | 7:06 | 29.5 | 2.15 m/s | 23.1 | 30.6 | 3.86 m/s | 17.9 |  | 2.15 | m/s |  | 3.86 | m/s | 7.0986 | 0.0098267 | 8.2699 |  | -1.5 | 51.5 | 0.0515 | 160.5805 | 6.8239 | 5.6127 | 0.021581 | 22.6521 | 0.22735
2025-05-19 17:23 | 852 | Remove | 2025-05-19 | 17:23 | ST | GS | - | 53 | g | 0 | 111.2 | 11.868 | 1176.7 | 58646 | 7:06 | 29.5 | 2.3 m/s | 26.2 | 30.6 | 3.86 m/s | 17.6 |  | 2.3 | m/s |  | 3.86 | m/s | 7.1069 | 0.0098058 | 8.2797 |  | 1.5 | 53 | 0.053 | 156.2207 | 7.7397 | 5.5186 | 0.026185 | 22.6783 | 0.2337
2025-05-19 17:24 | 853 | Remove | 2025-05-19 | 17:24 | ST | GS | - | 50.5 | g | 0 | 111.3 | 11.829 | 1172.3 | 58656 | 7:07 | 29.5 | 2.2 m/s | 26.6 | 30.7 | 4.04 m/s | 20.9 |  | 2.2 | m/s |  | 4.04 | m/s | 7.1153 | 0.0097692 | 8.2895 |  | -2.5 | 50.5 | 0.0505 | 164.1479 | 7.8578 | 6.5888 | 0.025429 | 22.7037 | 0.22243
2025-05-19 17:24 | 854 | Remove | 2025-05-19 | 17:24 | ST | GS | - | 50.5 | g | 0 | 111.3 | 11.863 | 1175.9 | 58665 | 7:07 | 29.5 | 2.13 m/s | 24.8 | 30.7 | 3.94 m/s | 21.2 |  | 2.13 | m/s |  | 3.94 | m/s | 7.1236 | 0.0097992 | 8.2993 |  | 0 | 50.5 | 0.0505 | 164.3419 | 7.3261 | 6.6833 | 0.022954 | 22.7266 | 0.22221
2025-05-19 17:25 | 855 | Remove | 2025-05-19 | 17:25 | ST | GS | - | 51 | g | 0 | 111.2 | 11.865 | 1175.5 | 58675 | 7:08 | 29.5 | 2.09 m/s | 25.7 | 30.7 | 4.21 m/s | 19.2 |  | 2.09 | m/s |  | 4.21 | m/s | 7.1319 | 0.0097958 | 8.3091 |  | 0.5 | 51 | 0.051 | 162.9228 | 7.592 | 6.0528 | 0.02334 | 22.75 | 0.22418
2025-05-19 17:25 | 856 | Remove | 2025-05-19 | 17:25 | US | GS | - | 52.5 | g | 0 | 111.2 | 11.925 | 1183.1 | 58685 | 7:08 | 29.5 | 2.13 m/s | 24.2 | 30.7 | 4.07 m/s | 20.6 |  | 2.13 | m/s |  | 4.07 | m/s | 7.1403 | 0.0098592 | 8.3189 |  | 1.5 | 52.5 | 0.0525 | 158.4557 | 7.1489 | 6.4942 | 0.022399 | 22.7724 | 0.23054
2025-05-19 17:26 | 857 | Remove | 2025-05-19 | 17:26 | US | GS | - | 54.5 | g | 0 | 111.2 | 11.909 | 1181.4 | 58695 | 7:09 | 29.5 | 2.34 m/s | 22.7 | 30.7 | 4.0 m/s | 17.3 |  | 2.34 | m/s |  | 4 | m/s | 7.1486 | 0.009845 | 8.3288 |  | 2 | 54.5 | 0.0545 | 152.8214 | 6.7058 | 5.4539 | 0.023082 | 22.7955 | 0.23908
2025-05-19 17:26 | 858 | Remove | 2025-05-19 | 17:26 | US | GS | - | 54 | g | 0 | 111.2 | 11.905 | 1180.9 | 58705 | 7:09 | 29.5 | 2.13 m/s | 21.8 | 30.7 | 4.07 m/s | 17 |  | 2.13 | m/s |  | 4.07 | m/s | 7.1569 | 0.0098408 | 8.3386 |  | -0.5 | 54 | 0.054 | 154.4187 | 6.4399 | 5.3593 | 0.020177 | 22.8156 | 0.23668
2025-05-19 17:27 | 859 | Remove | 2025-05-19 | 17:27 | US | GS | - | 50 | g | 0 | 111.2 | 11.877 | 1177.7 | 58715 | 7:10 | 29.5 | 2.09 m/s | 24 | 30.8 | 3.94 m/s | 17.2 |  | 2.09 | m/s |  | 3.94 | m/s | 7.1653 | 0.0098142 | 8.3484 |  | -4 | 50 | 0.05 | 166.9685 | 7.0898 | 5.4517 | 0.021796 | 22.8374 | 0.21894
2025-05-19 17:27 | 860 | Remove | 2025-05-19 | 17:27 | US | GS | - | 50.5 | g | 0 | 111.3 | 11.842 | 1174 | 58724 | 7:10 | 29.5 | 2.27 m/s | 25.2 | 30.8 | 3.94 m/s | 19.1 |  | 2.27 | m/s |  | 3.94 | m/s | 7.1736 | 0.0097833 | 8.3582 |  | 0.5 | 50.5 | 0.0505 | 165.509 | 7.4443 | 6.0539 | 0.024857 | 22.8623 | 0.22089
2025-05-19 17:28 | 861 | Remove | 2025-05-19 | 17:28 | ST | GS | - | 52 | g | 0 | 111.2 | 11.934 | 1184.6 | 58735 | 7:11 | 29.5 | 2.09 m/s | 22.9 | 30.8 | 4.09 m/s | 20.2 |  | 2.09 | m/s |  | 4.09 | m/s | 7.1822 | 0.0098717 | 8.3681 |  | 1.5 | 52 | 0.052 | 160.9246 | 6.7648 | 6.4025 | 0.020797 | 22.8831 | 0.22724
2025-05-19 17:28 | 862 | Remove | 2025-05-19 | 17:28 | ST | GS | - | 52 | g | 0 | 111.2 | 11.907 | 1181.5 | 58744 | 7:11 | 29.6 | 2.05 m/s | 23.1 | 30.8 | 3.71 m/s | 17.5 |  | 2.05 | m/s |  | 3.71 | m/s | 7.1906 | 0.0098458 | 8.3779 |  | 0 | 52 | 0.052 | 161.1139 | 6.8611 | 5.5467 | 0.02069 | 22.9038 | 0.22704
2025-05-19 17:29 | 863 | Remove | 2025-05-19 | 17:29 | ST | GS | - | 51 | g | 0 | 111.3 | 11.886 | 1179.6 | 58754 | 7:12 | 29.6 | 2.31 m/s | 22.1 | 30.8 | 4.07 m/s | 17 |  | 2.31 | m/s |  | 4.07 | m/s | 7.1989 | 0.00983 | 8.3878 |  | -1 | 51 | 0.051 | 164.4658 | 6.5641 | 5.3883 | 0.022304 | 22.9261 | 0.22245
2025-05-19 17:29 | 864 | Remove | 2025-05-19 | 17:29 | ST | GS | - | 51.5 | g | 0 | 111.3 | 11.881 | 1179.2 | 58764 | 7:12 | 29.6 | 2.27 m/s | 21.7 | 30.8 | 3.73 m/s | 17.8 |  | 2.27 | m/s |  | 3.73 | m/s | 7.2072 | 0.0098267 | 8.3976 |  | 0.5 | 51.5 | 0.0515 | 163.0598 | 6.4453 | 5.6418 | 0.021521 | 22.9476 | 0.22442
2025-05-19 17:30 | 865 | Remove | 2025-05-19 | 17:30 | US | GS | - | 53 | g | 0 | 111.3 | 11.862 | 1176.6 | 58774 | 7:13 | 29.6 | 2.2 m/s | 22.8 | 30.8 | 3.85 m/s | 18 |  | 2.2 | m/s |  | 3.85 | m/s | 7.2156 | 0.009805 | 8.4074 |  | 1.5 | 53 | 0.053 | 158.6299 | 6.772 | 5.7052 | 0.021915 | 22.9695 | 0.23074
2025-05-19 17:30 | 866 | Remove | 2025-05-19 | 17:30 | ST | GS | - | 51 | g | 0 | 111.3 | 11.874 | 1177.8 | 58784 | 7:13 | 29.6 | 1.98 m/s | 23.4 | 30.8 | 4.29 m/s | 17.9 |  | 1.98 | m/s |  | 4.29 | m/s | 7.2239 | 0.009815 | 8.4172 |  | -2 | 51 | 0.051 | 165.0431 | 6.9502 | 5.6735 | 0.020243 | 22.9898 | 0.22184
2025-05-19 17:31 | 867 | Remove | 2025-05-19 | 17:31 | US | GS | - | 60 | g | 0 | 111.4 | 11.908 | 1182.8 | 58794 | 7:14 | 29.6 | 2.62 m/s | 23.3 | 30.8 | 3.93 m/s | 17.5 |  | 2.62 | m/s |  | 3.93 | m/s | 7.2322 | 0.0098567 | 8.4271 |  | 9 | 60 | 0.06 | 140.4509 | 6.9205 | 5.5467 | 0.026671 | 23.0164 | 0.26068
2025-05-19 17:31 | 868 | Remove | 2025-05-19 | 17:31 | ST | GS | - | 55 | g | 0 | 111.1 | 11.916 | 1182.5 | 58804 | 7:14 | 29.6 | 2.02 m/s | 22 | 30.8 | 4.01 m/s | 17.6 |  | 2.02 | m/s |  | 4.01 | m/s | 7.2406 | 0.0098542 | 8.4369 |  | -5 | 55 | 0.055 | 153.3984 | 6.5344 | 5.5784 | 0.019416 | 23.0359 | 0.23876
2025-05-19 17:32 | 869 | Remove | 2025-05-19 | 17:32 | ST | GS | - | 52 | g | 0 | 111.3 | 11.9 | 1181.3 | 58813 | 7:15 | 29.6 | 2.16 m/s | 24 | 30.8 | 4.44 m/s | 18.8 |  | 2.16 | m/s |  | 4.44 | m/s | 7.2489 | 0.0098442 | 8.4468 |  | -3 | 52 | 0.052 | 162.4376 | 7.1285 | 5.9588 | 0.022649 | 23.0585 | 0.22551
2025-05-19 17:32 | 870 | Remove | 2025-05-19 | 17:32 | US | GS | - | 54 | g | 0 | 111.3 | 11.87 | 1178.4 | 58823 | 7:15 | 29.6 | 1.94 m/s | 22.1 | 30.8 | 4.0 m/s | 17.9 |  | 1.94 | m/s |  | 4 | m/s | 7.2572 | 0.00982 | 8.4566 |  | 2 | 54 | 0.054 | 156.6032 | 6.5641 | 5.6735 | 0.018732 | 23.0772 | 0.234
2025-05-19 17:33 | 871 | Keep | 2025-05-19 | 17:33 | ST | GS | - | 52 | g | 0 | 111.3 | 11.888 | 1180.1 | 58833 | 7:16 | 29.5 | 2.38 m/s | 22.8 | 30.8 | 4.06 m/s | 18.2 |  | 2.38 | m/s |  | 4.06 | m/s | 7.2656 | 0.0098342 | 8.4664 |  | -2 | 52 | 0.052 | 162.8156 | 6.7353 | 5.7686 | 0.02358 | 23.1008 | 0.2251
2025-05-19 17:33 | 872 | Remove | 2025-05-19 | 17:33 | ST | GS | - | 51 | g | 0 | 111.3 | 11.893 | 1180.6 | 58843 | 7:16 | 29.6 | 2.12 m/s | 21.6 | 30.8 | 4.29 m/s | 16.4 |  | 2.12 | m/s |  | 4.29 | m/s | 7.2739 | 0.0098383 | 8.4762 |  | -1 | 51 | 0.051 | 166.2009 | 6.4156 | 5.1981 | 0.020007 | 23.1208 | 0.22058
2025-05-19 17:34 | 873 | Remove | 2025-05-19 | 17:34 | US | GS | - | 57.5 | g | 0 | 111.3 | 11.868 | 1177.5 | 58853 | 7:17 | 29.5 | 2.91 m/s | 22.3 | 30.9 | 4.1 m/s | 17.6 |  | 2.91 | m/s |  | 4.1 | m/s | 7.2822 | 0.0098125 | 8.4861 |  | 6.5 | 57.5 | 0.0575 | 147.5837 | 6.5876 | 5.6086 | 0.028198 | 23.149 | 0.24839
2025-05-19 17:34 | 874 | Remove | 2025-05-19 | 17:34 | ST | GS | - | 51 | g | 0 | 111.2 | 11.904 | 1181.2 | 58863 | 7:17 | 29.5 | 2.11 m/s | 22.8 | 30.9 | 4.06 m/s | 16.7 |  | 2.11 | m/s |  | 4.06 | m/s | 7.2906 | 0.0098433 | 8.4959 |  | -6.5 | 51 | 0.051 | 166.5863 | 6.7353 | 5.3218 | 0.020905 | 23.1699 | 0.22011
2025-05-19 17:35 | 875 | Remove | 2025-05-19 | 17:35 | US | GS | - | 57.5 | g | 0 | 111.2 | 11.879 | 1178.2 | 58872 | 7:18 | 29.5 | 2.27 m/s | 22.7 | 30.9 | 4.13 m/s | 17.2 |  | 2.27 | m/s |  | 4.13 | m/s | 7.2989 | 0.0098183 | 8.5057 |  | 6.5 | 57.5 | 0.0575 | 147.9256 | 6.7058 | 5.4811 | 0.022391 | 23.1923 | 0.24793
2025-05-19 17:35 | 876 | Remove | 2025-05-19 | 17:35 | ST | GS | - | 53 | g | 0 | 111.2 | 11.875 | 1177.8 | 58882 | 7:18 | 29.5 | 2.02 m/s | 23 | 30.9 | 3.81 m/s | 17 |  | 2.02 | m/s |  | 3.81 | m/s | 7.3072 | 0.009815 | 8.5155 |  | -4.5 | 53 | 0.053 | 160.6705 | 6.7944 | 5.4174 | 0.020188 | 23.2125 | 0.22833
2025-05-19 17:36 | 877 | Remove | 2025-05-19 | 17:36 | US | GS | - | 55 | g | 0 | 111.3 | 11.846 | 1174.8 | 58892 | 7:19 | 29.5 | 2.45 m/s | 22.9 | 30.9 | 4.01 m/s | 18.4 |  | 2.45 | m/s |  | 4.01 | m/s | 7.3156 | 0.00979 | 8.5253 |  | 2 | 55 | 0.055 | 155.0059 | 6.7648 | 5.8635 | 0.02438 | 23.2369 | 0.23669
2025-05-19 17:36 | 878 | Remove | 2025-05-19 | 17:36 | ST | GS | - | 55 | g | 0 | 111.3 | 11.846 | 1175.2 | 58902 | 7:19 | 29.5 | 2.31 m/s | 22.6 | 30.9 | 4.15 m/s | 17.8 |  | 2.31 | m/s |  | 4.15 | m/s | 7.3239 | 0.0097933 | 8.5351 |  | 0 | 55 | 0.055 | 155.184 | 6.6762 | 5.6723 | 0.022685 | 23.2596 | 0.23646
2025-05-19 17:37 | 879 | Remove | 2025-05-19 | 17:37 | ST | GS | - | 51.5 | g | 0 | 111.3 | 11.859 | 1176.7 | 58912 | 7:20 | 29.5 | 2.45 m/s | 21.6 | 30.8 | 3.96 m/s | 17.3 |  | 2.45 | m/s |  | 3.96 | m/s | 7.3325 | 0.0098058 | 8.5449 |  | -3.5 | 51.5 | 0.0515 | 165.9209 | 6.3808 | 5.4833 | 0.022996 | 23.2826 | 0.2212
2025-05-19 17:37 | 880 | Remove | 2025-05-19 | 17:37 | US | GS | - | 55.5 | g | 0 | 111.2 | 11.867 | 1177 | 58922 | 7:20 | 29.5 | 2.25 m/s | 22.5 | 30.8 | 4.13 m/s | 17.3 |  | 2.25 | m/s |  | 4.13 | m/s | 7.3408 | 0.0098083 | 8.5547 |  | 4 | 55.5 | 0.0555 | 154.1394 | 6.6467 | 5.4833 | 0.021998 | 23.3046 | 0.23815
2025-05-19 17:38 | 881 | Remove | 2025-05-19 | 17:38 | ST | GS | - | 52.5 | g | 0 | 111.2 | 11.869 | 1176.5 | 58932 | 7:21 | 29.5 | 2.25 m/s | 22.6 | 30.8 | 3.92 m/s | 17.5 |  | 2.25 | m/s |  | 3.92 | m/s | 7.3492 | 0.0098042 | 8.5645 |  | -3 | 52.5 | 0.0525 | 163.1341 | 6.6762 | 5.5467 | 0.022096 | 23.3267 | 0.22506
2025-05-19 17:38 | 882 | Remove | 2025-05-19 | 17:38 | US | GS | - | 56 | g | 0 | 111.3 | 11.866 | 1176.8 | 58941 | 7:21 | 29.5 | 2.47 m/s | 21.9 | 30.8 | 4.09 m/s | 17.1 |  | 2.47 | m/s |  | 4.09 | m/s | 7.3575 | 0.0098067 | 8.5743 |  | 3.5 | 56 | 0.056 | 153.1133 | 6.4694 | 5.42 | 0.023505 | 23.3502 | 0.23983
2025-05-19 17:39 | 883 | Remove | 2025-05-19 | 17:39 | US | GS | - | 53.5 | g | 0 | 111.2 | 11.861 | 1176.1 | 58951 | 7:22 | 29.5 | 2.18 m/s | 22.5 | 30.8 | 3.93 m/s | 16.7 |  | 2.18 | m/s |  | 3.93 | m/s | 7.3658 | 0.0098008 | 8.5841 |  | -2.5 | 53.5 | 0.0535 | 160.4513 | 6.6467 | 5.2932 | 0.021314 | 23.3715 | 0.22891
2025-05-19 17:39 | 884 | Remove | 2025-05-19 | 17:39 | US | GS | - | 53 | g | 0 | 111.3 | 11.855 | 1175.8 | 58961 | 7:22 | 29.5 | 2.48 m/s | 21.8 | 30.8 | 3.79 m/s | 16.9 |  | 2.48 | m/s |  | 3.79 | m/s | 7.3742 | 0.0097983 | 8.5939 |  | -0.5 | 53 | 0.053 | 162.1499 | 6.4399 | 5.3566 | 0.023493 | 23.395 | 0.22654
2025-05-19 17:40 | 885 | Remove | 2025-05-19 | 17:40 | US | GS | - | 54.5 | g | 0 | 111.2 | 11.866 | 1176.7 | 58971 | 7:23 | 29.5 | 2.65 m/s | 23 | 30.8 | 4.11 m/s | 16.4 |  | 2.65 | m/s |  | 4.11 | m/s | 7.3825 | 0.0098058 | 8.6038 |  | 1.5 | 54.5 | 0.0545 | 157.867 | 6.7944 | 5.1981 | 0.026485 | 23.4215 | 0.23269
2025-05-19 17:40 | 886 | Remove | 2025-05-19 | 17:40 | ST | GS | - | 55 | g | 0 | 111.1 | 11.851 | 1174.5 | 58981 | 7:23 | 29.5 | 2.37 m/s | 21.7 | 30.8 | 3.6 m/s | 17.4 |  | 2.37 | m/s |  | 3.6 | m/s | 7.3908 | 0.0097875 | 8.6135 |  | 0.5 | 55 | 0.055 | 156.6098 | 6.4103 | 5.515 | 0.022348 | 23.4438 | 0.2346
2025-05-19 17:41 | 887 | Remove | 2025-05-19 | 17:41 | ST | GS | - | 54 | g | 0 | 111.2 | 11.889 | 1179.7 | 58991 | 7:24 | 29.5 | 2.48 m/s | 22 | 30.8 | 4.01 m/s | 18.3 |  | 2.48 | m/s |  | 4.01 | m/s | 7.3992 | 0.0098308 | 8.6234 |  | -1 | 54 | 0.054 | 159.692 | 6.499 | 5.8003 | 0.023708 | 23.4675 | 0.23011
2025-05-19 17:41 | 888 | Remove | 2025-05-19 | 17:41 | ST | GS | - | 53 | g | 0 | 111.2 | 11.894 | 1179.8 | 59000 | 7:24 | 29.5 | 2.06 m/s | 21.7 | 30.8 | 3.96 m/s | 18 |  | 2.06 | m/s |  | 3.96 | m/s | 7.4075 | 0.0098317 | 8.6332 |  | -1 | 53 | 0.053 | 162.8906 | 6.4103 | 5.7052 | 0.019425 | 23.4869 | 0.22566
2025-05-19 17:42 | 889 | Remove | 2025-05-19 | 17:42 | US | GS | - | 56.5 | g | 0 | 111.2 | 11.858 | 1175.6 | 59010 | 7:25 | 29.5 | 2.68 m/s | 22 | 30.8 | 4.09 m/s | 18.6 |  | 2.68 | m/s |  | 4.09 | m/s | 7.4158 | 0.0097967 | 8.643 |  | 3.5 | 56.5 | 0.0565 | 152.9734 | 6.499 | 5.8954 | 0.02562 | 23.5126 | 0.2403
2025-05-19 17:42 | 890 | Remove | 2025-05-19 | 17:42 | ST | GS | - | 55.5 | g | 0 | 111.3 | 11.895 | 1180.6 | 59020 | 7:25 | 29.5 | 2.22 m/s | 22.5 | 30.8 | 4.01 m/s | 17.3 |  | 2.22 | m/s |  | 4.01 | m/s | 7.4242 | 0.0098383 | 8.6528 |  | -1 | 55.5 | 0.0555 | 155.9069 | 6.6467 | 5.4833 | 0.021705 | 23.5343 | 0.23583
2025-05-19 17:43 | 891 | Remove | 2025-05-19 | 17:43 | ST | GS | - | 54 | g | 0 | 111.2 | 11.888 | 1179.8 | 59030 | 7:26 | 29.5 | 2.34 m/s | 20.8 | 30.8 | 3.86 m/s | 17.1 |  | 2.34 | m/s |  | 3.86 | m/s | 7.4325 | 0.0098317 | 8.6627 |  | -1.5 | 54 | 0.054 | 160.4198 | 6.1445 | 5.42 | 0.02115 | 23.5554 | 0.22925
2025-05-19 17:43 | 892 | Remove | 2025-05-19 | 17:43 | ST | GS | - | 52.5 | g | 0 | 111.3 | 11.865 | 1177.2 | 59040 | 7:26 | 29.5 | 2.06 m/s | 23.1 | 30.7 | 3.85 m/s | 17.7 |  | 2.06 | m/s |  | 3.85 | m/s | 7.4408 | 0.00981 | 8.6725 |  | -1.5 | 52.5 | 0.0525 | 165.19 | 6.8239 | 5.58 | 0.020678 | 23.5761 | 0.22268
2025-05-19 17:44 | 893 | Remove | 2025-05-19 | 17:44 | US | GS | - | 61 | g | 0 | 111.3 | 11.901 | 1181.4 | 59050 | 7:27 | 29.5 | 2.65 m/s | 21.7 | 30.7 | 3.75 m/s | 19.7 |  | 2.65 | m/s |  | 3.75 | m/s | 7.4492 | 0.009845 | 8.6823 |  | 8.5 | 61 | 0.061 | 142.3331 | 6.4103 | 6.2105 | 0.024988 | 23.6011 | 0.25846
2025-05-19 17:44 | 894 | Remove | 2025-05-19 | 17:44 | US | GS | - | 53 | g | 0 | 111.2 | 11.858 | 1175.7 | 59059 | 7:27 | 29.5 | 2.23 m/s | 23.9 | 30.7 | 3.94 m/s | 16.5 |  | 2.23 | m/s |  | 3.94 | m/s | 7.4575 | 0.0097975 | 8.6921 |  | -8 | 53 | 0.053 | 164.0022 | 7.0602 | 5.2017 | 0.023159 | 23.6242 | 0.22435
2025-05-19 17:45 | 895 | Remove | 2025-05-19 | 17:45 | US | GS | - | 58 | g | 0 | 111.1 | 11.899 | 1180.2 | 59069 | 7:28 | 29.5 | 2.62 m/s | 24.1 | 30.7 | 3.92 m/s | 18 |  | 2.62 | m/s |  | 3.92 | m/s | 7.4661 | 0.009835 | 8.702 |  | 5 | 58 | 0.058 | 150.0337 | 7.1193 | 5.6745 | 0.027437 | 23.6517 | 0.24523
2025-05-19 17:45 | 896 | Remove | 2025-05-19 | 17:45 | US | GS | - | 54.5 | g | 0 | 111.1 | 11.905 | 1180.5 | 59079 | 7:28 | 29.5 | 2.43 m/s | 21.8 | 30.7 | 3.8 m/s | 17.3 |  | 2.43 | m/s |  | 3.8 | m/s | 7.4744 | 0.0098375 | 8.7118 |  | -3.5 | 54.5 | 0.0545 | 159.8494 | 6.4399 | 5.4539 | 0.023019 | 23.6747 | 0.2302
2025-05-19 17:46 | 897 | Remove | 2025-05-19 | 17:46 | US | GS | - | 69 | g | 0 | 111.1 | 11.9 | 1180.6 | 59089 | 7:29 | 29.5 | 2.72 m/s | 22.2 | 30.7 | 4.03 m/s | 18.5 |  | 2.72 | m/s |  | 4.03 | m/s | 7.4828 | 0.0098383 | 8.7216 |  | 14.5 | 69 | 0.069 | 126.4004 | 6.558 | 5.8322 | 0.026239 | 23.7009 | 0.29113
2025-05-19 17:46 | 898 | Remove | 2025-05-19 | 17:46 | ST | GS | - | 52.5 | g | 0 | 111.1 | 11.874 | 1177 | 59099 | 7:29 | 29.5 | 2.09 m/s | 22.1 | 30.7 | 3.81 m/s | 17 |  | 2.09 | m/s |  | 3.81 | m/s | 7.4911 | 0.0098083 | 8.7314 |  | -16.5 | 52.5 | 0.0525 | 166.3131 | 6.5285 | 5.3593 | 0.020071 | 23.721 | 0.22132
2025-05-19 17:47 | 899 | Remove | 2025-05-19 | 17:47 | US | GS | - | 61 | g | 0 | 111.2 | 11.896 | 1180 | 59109 | 7:30 | 29.5 | 2.91 m/s | 20.3 | 30.7 | 3.81 m/s | 16.4 |  | 2.91 | m/s |  | 3.81 | m/s | 7.4994 | 0.0098333 | 8.7413 |  | 8.5 | 61 | 0.061 | 143.2995 | 5.9968 | 5.1701 | 0.025669 | 23.7467 | 0.25688
2025-05-19 17:47 | 900 | Remove | 2025-05-19 | 17:47 | ST | GS | - | 56 | g | 0 | 111.2 | 11.886 | 1178.3 | 59119 | 7:30 | 29.5 | 2.47 m/s | 21.3 | 30.7 | 3.9 m/s | 16.9 |  | 2.47 | m/s |  | 3.9 | m/s | 7.5078 | 0.0098192 | 8.7511 |  | -5 | 56 | 0.056 | 156.2695 | 6.2922 | 5.3278 | 0.022861 | 23.7695 | 0.2356
2025-05-19 17:48 | 901 | Keep | 2025-05-19 | 17:48 | ST | GS | - | 54.5 | g | 0 | 111.2 | 11.855 | 1175.1 | 59129 | 7:31 | 29.5 | 1.98 m/s | 22.8 | 30.7 | 4.04 m/s | 17.9 |  | 1.98 | m/s |  | 4.04 | m/s | 7.5161 | 0.0097925 | 8.7609 |  | -1.5 | 54.5 | 0.0545 | 160.7502 | 6.7353 | 5.643 | 0.019617 | 23.7892 | 0.2291
2025-05-19 17:48 | 902 | Remove | 2025-05-19 | 17:48 | ST | GS | - | 54.5 | g | 0 | 111.1 | 11.884 | 1178.1 | 59138 | 7:31 | 29.5 | 2.22 m/s | 21.7 | 30.7 | 4.07 m/s | 17.7 |  | 2.22 | m/s |  | 4.07 | m/s | 7.5244 | 0.0098175 | 8.7707 |  | 0 | 54.5 | 0.0545 | 160.9303 | 6.4103 | 5.58 | 0.020933 | 23.8101 | 0.22889
2025-05-19 17:49 | 903 | Remove | 2025-05-19 | 17:49 | US | GS | - | 54.5 | g | 0 | 111.1 | 11.886 | 1178.4 | 59148 | 7:32 | 29.5 | 2.18 m/s | 21.3 | 30.7 | 3.89 m/s | 16.6 |  | 2.18 | m/s |  | 3.89 | m/s | 7.5328 | 0.00982 | 8.7805 |  | 0 | 54.5 | 0.0545 | 161.1105 | 6.2922 | 5.2332 | 0.020177 | 23.8303 | 0.2287
2025-05-19 17:49 | 904 | Remove | 2025-05-19 | 17:49 | ST | GS | - | 56 | g | 0 | 111.2 | 11.883 | 1178.1 | 59158 | 7:32 | 29.5 | 2.13 m/s | 20.9 | 30.8 | 4.0 m/s | 16.4 |  | 2.13 | m/s |  | 4 | m/s | 7.5411 | 0.0098175 | 8.7903 |  | 1.5 | 56 | 0.056 | 156.9703 | 6.174 | 5.1981 | 0.019344 | 23.8496 | 0.2348
2025-05-19 17:50 | 905 | Remove | 2025-05-19 | 17:50 | ST | GS | - | 56 | g | 0 | 111.3 | 11.842 | 1173.7 | 59168 | 7:33 | 29.5 | 1.98 m/s | 22.6 | 30.8 | 4.15 m/s | 16.2 |  | 1.98 | m/s |  | 4.15 | m/s | 7.5494 | 0.0097808 | 8.8001 |  | 0 | 56 | 0.056 | 157.145 | 6.6762 | 5.1347 | 0.019445 | 23.8691 | 0.23461
2025-05-19 17:50 | 906 | Remove | 2025-05-19 | 17:50 | ST | GS | - | 54 | g | 0 | 111.3 | 11.873 | 1177.9 | 59178 | 7:33 | 29.5 | 2.01 m/s | 21.8 | 30.8 | 4.55 m/s | 17.9 |  | 2.01 | m/s |  | 4.55 | m/s | 7.5578 | 0.0098158 | 8.8099 |  | -2 | 54 | 0.054 | 163.1469 | 6.4399 | 5.6735 | 0.01904 | 23.8881 | 0.22605
2025-05-19 17:51 | 907 | Remove | 2025-05-19 | 17:51 | ST | GS | - | 54 | g | 0 | 111.4 | 11.852 | 1176 | 59188 | 7:34 | 29.5 | 2.02 m/s | 21.8 | 30.8 | 4.13 m/s | 16.6 |  | 2.02 | m/s |  | 4.13 | m/s | 7.5661 | 0.0098 | 8.8197 |  | 0 | 54 | 0.054 | 163.3284 | 6.4399 | 5.2615 | 0.019135 | 23.9072 | 0.22587
2025-05-19 17:51 | 908 | Remove | 2025-05-19 | 17:51 | ST | GS | - | 55 | g | 0 | 111.4 | 11.832 | 1173 | 59197 | 7:34 | 29.5 | 2.42 m/s | 23.1 | 30.8 | 4.32 m/s | 17.3 |  | 2.42 | m/s |  | 4.32 | m/s | 7.5744 | 0.009775 | 8.8295 |  | 1 | 55 | 0.055 | 160.5365 | 6.8239 | 5.4833 | 0.024291 | 23.9315 | 0.22982
2025-05-19 17:52 | 909 | Remove | 2025-05-19 | 17:52 | ST | GS | - | 61 | g | 0 | 111.3 | 11.878 | 1178.6 | 59207 | 7:35 | 29.5 | 2.52 m/s | 22.1 | 30.8 | 3.92 m/s | 17.1 |  | 2.52 | m/s |  | 3.92 | m/s | 7.5828 | 0.0098217 | 8.8393 |  | 6 | 61 | 0.061 | 144.9071 | 6.5285 | 5.42 | 0.0242 | 23.9557 | 0.25464
2025-05-19 17:52 | 910 | Remove | 2025-05-19 | 17:52 | ST | GS | - | 55 | g | 0 | 111.3 | 11.861 | 1176.2 | 59217 | 7:35 | 29.5 | 2.23 m/s | 21.5 | 30.8 | 3.96 m/s | 17 |  | 2.23 | m/s |  | 3.96 | m/s | 7.5911 | 0.0098017 | 8.8491 |  | -6 | 55 | 0.055 | 160.8933 | 6.3513 | 5.3883 | 0.020834 | 23.9766 | 0.22939
2025-05-19 17:53 | 911 | Remove | 2025-05-19 | 17:53 | US | GS | - | 58 | g | 0 | 111.3 | 11.84 | 1174 | 59227 | 7:36 | 29.5 | 2.31 m/s | 22.5 | 30.8 | 4.07 m/s | 17.7 |  | 2.31 | m/s |  | 4.07 | m/s | 7.5994 | 0.0097833 | 8.8589 |  | 3 | 58 | 0.058 | 152.7399 | 6.6467 | 5.6101 | 0.022585 | 23.9991 | 0.24168
2025-05-19 17:53 | 912 | Remove | 2025-05-19 | 17:53 | ST | GS | - | 56.5 | g | 0 | 111.4 | 11.842 | 1174 | 59237 | 7:36 | 29.5 | 2.18 m/s | 22.6 | 30.8 | 3.96 m/s | 17.2 |  | 2.18 | m/s |  | 3.96 | m/s | 7.6078 | 0.0097833 | 8.8687 |  | -1.5 | 56.5 | 0.0565 | 156.9681 | 6.6762 | 5.4517 | 0.021409 | 24.0205 | 0.23522
2025-05-19 17:54 | 913 | Remove | 2025-05-19 | 17:54 | US | GS | - | 55 | g | 0 | 111.3 | 11.838 | 1173.7 | 59246 | 7:37 | 29.5 | 1.95 m/s | 23.6 | 30.8 | 4.5 m/s | 17.7 |  | 1.95 | m/s |  | 4.5 | m/s | 7.6164 | 0.0097808 | 8.8785 |  | -1.5 | 55 | 0.055 | 161.4269 | 6.9716 | 5.6101 | 0.019997 | 24.0405 | 0.22878
2025-05-19 17:54 | 914 | Remove | 2025-05-19 | 17:54 | US | GS | - | 63 | g | 0 | 111.3 | 11.873 | 1178.2 | 59256 | 7:37 | 29.5 | 2.44 m/s | 20.9 | 30.8 | 3.76 m/s | 16.8 |  | 2.44 | m/s |  | 3.76 | m/s | 7.6247 | 0.0098183 | 8.8883 |  | 8 | 63 | 0.063 | 141.0841 | 6.174 | 5.3249 | 0.02216 | 24.0627 | 0.26182
2025-05-19 17:55 | 915 | Remove | 2025-05-19 | 17:55 | US | GS | - | 56 | g | 0 | 111.4 | 11.84 | 1173.9 | 59266 | 7:38 | 29.5 | 2.18 m/s | 23.7 | 30.8 | 3.76 m/s | 17 |  | 2.18 | m/s |  | 3.76 | m/s | 7.6331 | 0.0097825 | 8.8981 |  | -7 | 56 | 0.056 | 158.8943 | 7.0012 | 5.3883 | 0.022451 | 24.0852 | 0.23251
2025-05-19 17:55 | 916 | Remove | 2025-05-19 | 17:55 | US | GS | - | 65 | g | 0 | 111.2 | 11.888 | 1179.2 | 59276 | 7:38 | 29.5 | 2.5 m/s | 21.2 | 30.8 | 4.03 m/s | 16.6 |  | 2.5 | m/s |  | 4.03 | m/s | 7.6414 | 0.0098267 | 8.9079 |  | 9 | 65 | 0.065 | 137.0447 | 6.2626 | 5.2615 | 0.02303 | 24.1082 | 0.26962
2025-05-19 17:56 | 917 | Remove | 2025-05-19 | 17:56 | ST | GS | - | 54.5 | g | 0 | 111.4 | 11.857 | 1176.2 | 59286 | 7:39 | 29.5 | 2.23 m/s | 21.9 | 30.8 | 3.85 m/s | 16.5 |  | 2.23 | m/s |  | 3.85 | m/s | 7.6497 | 0.0098017 | 8.9177 |  | -10.5 | 54.5 | 0.0545 | 163.6277 | 6.4694 | 5.2298 | 0.021221 | 24.1294 | 0.22587
2025-05-19 17:56 | 918 | Remove | 2025-05-19 | 17:56 | ST | GS | - | 55 | g | 0 | 111.4 | 11.806 | 1170.3 | 59296 | 7:39 | 29.5 | 2.2 m/s | 27.6 | 30.8 | 4.06 m/s | 16.6 |  | 2.2 | m/s |  | 4.06 | m/s | 7.6581 | 0.0097525 | 8.9275 |  | 0.5 | 55 | 0.055 | 162.3175 | 8.1533 | 5.2615 | 0.026385 | 24.1558 | 0.22769
2025-05-19 17:57 | 919 | Remove | 2025-05-19 | 17:57 | ST | GS | - | 54.5 | g | 0 | 111.3 | 11.86 | 1175.9 | 59305 | 7:40 | 29.5 | 2.44 m/s | 23.5 | 30.8 | 4.09 m/s | 19.5 |  | 2.44 | m/s |  | 4.09 | m/s | 7.6664 | 0.0097992 | 8.9373 |  | -0.5 | 54.5 | 0.0545 | 163.9865 | 6.9421 | 6.1807 | 0.024916 | 24.1807 | 0.22539
2025-05-19 17:57 | 920 | Remove | 2025-05-19 | 17:57 | ST | GS | - | 58.5 | g | 0 | 111.4 | 11.845 | 1174.3 | 59315 | 7:40 | 29.5 | 2.08 m/s | 22.1 | 30.7 | 4.01 m/s | 17.3 |  | 2.08 | m/s |  | 4.01 | m/s | 7.6747 | 0.0097858 | 8.947 |  | 4 | 58.5 | 0.0585 | 152.941 | 6.5285 | 5.4539 | 0.019975 | 24.2007 | 0.24173
2025-05-19 17:58 | 921 | Remove | 2025-05-19 | 17:58 | ST | GS | - | 58.5 | g | 0 | 111.5 | 11.842 | 1174.9 | 59325 | 7:41 | 29.5 | 2.3 m/s | 22.5 | 30.7 | 3.96 m/s | 17.7 |  | 2.3 | m/s |  | 3.96 | m/s | 7.6831 | 0.0097908 | 8.9568 |  | 0 | 58.5 | 0.0585 | 153.1083 | 6.6467 | 5.58 | 0.022487 | 24.2232 | 0.2415
2025-05-19 17:58 | 922 | Remove | 2025-05-19 | 17:58 | US | GS | - | 55.5 | g | 0 | 111.3 | 11.836 | 1173.3 | 59335 | 7:41 | 29.5 | 1.77 m/s | 22 | 30.7 | 4.16 m/s | 17.9 |  | 1.77 | m/s |  | 4.16 | m/s | 7.6914 | 0.0097775 | 8.9666 |  | -3 | 55.5 | 0.0555 | 161.5606 | 6.499 | 5.643 | 0.016921 | 24.2401 | 0.22896
2025-05-19 17:59 | 923 | Remove | 2025-05-19 | 17:59 | ST | GS | - | 58.5 | g | 0 | 111.5 | 11.84 | 1174.9 | 59345 | 7:42 | 29.5 | 2.2 m/s | 22 | 30.8 | 3.92 m/s | 17.3 |  | 2.2 | m/s |  | 3.92 | m/s | 7.6997 | 0.0097908 | 8.9764 |  | 3 | 58.5 | 0.0585 | 153.4428 | 6.499 | 5.4833 | 0.021031 | 24.2611 | 0.24113
2025-05-19 17:59 | 924 | Remove | 2025-05-19 | 17:59 | ST | GS | - | 57 | g | 0 | 111.5 | 11.816 | 1171.7 | 59355 | 7:42 | 29.5 | 2.04 m/s | 24.4 | 30.8 | 4.09 m/s | 18.7 |  | 2.04 | m/s |  | 4.09 | m/s | 7.7081 | 0.0097642 | 8.9862 |  | -1.5 | 57 | 0.057 | 157.6521 | 7.2079 | 5.9271 | 0.021629 | 24.2827 | 0.23473
2025-05-19 18:00 | 925 | Remove | 2025-05-19 | 18:00 | ST | GS | - | 57.5 | g | 0 | 111.4 | 11.862 | 1177.2 | 59364 | 7:43 | 29.5 | 2.34 m/s | 21.3 | 30.7 | 3.86 m/s | 18.7 |  | 2.34 | m/s |  | 3.86 | m/s | 7.7164 | 0.00981 | 8.996 |  | 0.5 | 57.5 | 0.0575 | 156.4518 | 6.2922 | 5.8952 | 0.021658 | 24.3044 | 0.23658
2025-05-19 18:00 | 926 | Remove | 2025-05-19 | 18:00 | ST | GS | - | 57 | g | 0 | 111.5 | 11.864 | 1177.9 | 59374 | 7:43 | 29.5 | 2.41 m/s | 23.1 | 30.7 | 4.24 m/s | 20 |  | 2.41 | m/s |  | 4.24 | m/s | 7.7247 | 0.0098158 | 9.0058 |  | -0.5 | 57 | 0.057 | 157.9964 | 6.8239 | 6.305 | 0.024191 | 24.3286 | 0.23429
2025-05-19 18:01 | 927 | Remove | 2025-05-19 | 18:01 | ST | GS | - | 57.5 | g | 0 | 111.6 | 11.853 | 1177.2 | 59384 | 7:44 | 29.5 | 2.22 m/s | 22.3 | 30.7 | 4.07 m/s | 16.5 |  | 2.22 | m/s |  | 4.07 | m/s | 7.7331 | 0.00981 | 9.0156 |  | 0.5 | 57.5 | 0.0575 | 156.7932 | 6.5876 | 5.2017 | 0.021512 | 24.3501 | 0.23614
2025-05-19 18:01 | 928 | Remove | 2025-05-19 | 18:01 | ST | GS | - | 56.5 | g | 0 | 111.6 | 11.824 | 1173.9 | 59394 | 7:44 | 29.5 | 2.57 m/s | 23.5 | 30.7 | 4.16 m/s | 16.3 |  | 2.57 | m/s |  | 4.16 | m/s | 7.7414 | 0.0097825 | 9.0254 |  | -1 | 56.5 | 0.0565 | 159.7414 | 6.9421 | 5.1386 | 0.026244 | 24.3764 | 0.23178
2025-05-19 18:02 | 929 | Remove | 2025-05-19 | 18:02 | ST | GS | - | 57 | g | 0 | 111.5 | 11.851 | 1176.1 | 59404 | 7:45 | 29.5 | 2.05 m/s | 22.6 | 30.8 | 3.88 m/s | 16.7 |  | 2.05 | m/s |  | 3.88 | m/s | 7.7497 | 0.0098008 | 9.0352 |  | 0.5 | 57 | 0.057 | 158.5121 | 6.6762 | 5.2932 | 0.020132 | 24.3965 | 0.23364
2025-05-19 18:02 | 930 | Remove | 2025-05-19 | 18:02 | US | GS | - | 62.5 | g | 0 | 111.6 | 11.855 | 1177.5 | 59414 | 7:46 | 29.5 | 2.7 m/s | 21.8 | 30.8 | 3.77 m/s | 17.5 |  | 2.7 | m/s |  | 3.77 | m/s | 7.7583 | 0.0098125 | 9.045 |  | 5.5 | 62.5 | 0.0625 | 144.72 | 6.4399 | 5.5467 | 0.025577 | 24.4221 | 0.25592
2025-05-19 18:03 | 931 | Keep | 2025-05-19 | 18:03 | ST | GS | - | 59.5 | g | 0 | 111.6 | 11.85 | 1176.8 | 59423 | 7:46 | 29.5 | 2.23 m/s | 22.3 | 30.7 | 3.96 m/s | 17.8 |  | 2.23 | m/s |  | 3.96 | m/s | 7.7667 | 0.0098067 | 9.0548 |  | -3 | 59.5 | 0.0595 | 152.1817 | 6.5876 | 5.6115 | 0.021609 | 24.4437 | 0.24342
2025-05-19 18:03 | 932 | Remove | 2025-05-19 | 18:03 | ST | GS | - | 55.5 | g | 0 | 111.6 | 11.812 | 1172.5 | 59433 | 7:46 | 29.5 | 2.16 m/s | 24.6 | 30.7 | 4.24 m/s | 17.1 |  | 2.16 | m/s |  | 4.24 | m/s | 7.775 | 0.0097708 | 9.0646 |  | -4 | 55.5 | 0.0555 | 163.3258 | 7.267 | 5.3908 | 0.023089 | 24.4668 | 0.22684
2025-05-19 18:04 | 933 | Remove | 2025-05-19 | 18:04 | ST | GS | - | 59 | g | 0 | 111.7 | 11.813 | 1172.3 | 59443 | 7:47 | 29.5 | 2.06 m/s | 26 | 30.7 | 3.76 m/s | 17.2 |  | 2.06 | m/s |  | 3.76 | m/s | 7.7833 | 0.0097692 | 9.0743 |  | 3.5 | 59 | 0.059 | 153.8025 | 7.6806 | 5.4223 | 0.023274 | 24.49 | 0.24091
2025-05-19 18:04 | 934 | Remove | 2025-05-19 | 18:04 | US | GS | - | 60 | g | 0 | 111.6 | 11.87 | 1179.3 | 59453 | 7:48 | 29.5 | 2.34 m/s | 22.5 | 30.7 | 3.79 m/s | 18.8 |  | 2.34 | m/s |  | 3.79 | m/s | 7.7917 | 0.0098275 | 9.0842 |  | 1 | 60 | 0.06 | 151.4029 | 6.6467 | 5.9267 | 0.022878 | 24.5129 | 0.24477
2025-05-19 18:05 | 935 | Remove | 2025-05-19 | 18:05 | ST | GS | - | 57 | g | 0 | 111.7 | 11.813 | 1172.7 | 59463 | 7:48 | 29.5 | 1.98 m/s | 22.9 | 30.7 | 4.15 m/s | 18.9 |  | 1.98 | m/s |  | 4.15 | m/s | 7.8 | 0.0097725 | 9.0939 |  | -3 | 57 | 0.057 | 159.543 | 6.7648 | 5.9583 | 0.019703 | 24.5326 | 0.23234
2025-05-19 18:05 | 936 | Remove | 2025-05-19 | 18:05 | ST | GS | - | 56 | g | 0 | 111.7 | 11.831 | 1174.5 | 59472 | 7:48 | 29.5 | 2.09 m/s | 21.7 | 30.7 | 4.13 m/s | 17.1 |  | 2.09 | m/s |  | 4.13 | m/s | 7.8083 | 0.0097875 | 9.1037 |  | -1 | 56 | 0.056 | 162.5667 | 6.4103 | 5.3908 | 0.019707 | 24.5523 | 0.22808
2025-05-19 18:06 | 937 | Remove | 2025-05-19 | 18:06 | ST | GS | - | 57 | g | 0 | 111.5 | 11.833 | 1174.2 | 59482 | 7:49 | 29.5 | 2.08 m/s | 22.1 | 30.7 | 3.88 m/s | 17 |  | 2.08 | m/s |  | 3.88 | m/s | 7.8167 | 0.009785 | 9.1135 |  | 1 | 57 | 0.057 | 159.8863 | 6.5285 | 5.3593 | 0.019975 | 24.5723 | 0.23197
2025-05-19 18:06 | 938 | Remove | 2025-05-19 | 18:06 | ST | GS | - | 59 | g | 0 | 111.7 | 11.839 | 1174.9 | 59492 | 7:50 | 29.5 | 2.55 m/s | 22.3 | 30.7 | 4.27 m/s | 17.8 |  | 2.55 | m/s |  | 4.27 | m/s | 7.825 | 0.0097908 | 9.1233 |  | 2 | 59 | 0.059 | 154.6324 | 6.5876 | 5.6115 | 0.02471 | 24.597 | 0.23987
2025-05-19 18:07 | 939 | Remove | 2025-05-19 | 18:07 | US | GS | - | 62 | g | 0 | 111.8 | 11.849 | 1176.7 | 59502 | 7:50 | 29.5 | 2.16 m/s | 22.9 | 30.8 | 4.01 m/s | 17.7 |  | 2.16 | m/s |  | 4.01 | m/s | 7.8333 | 0.0098058 | 9.1331 |  | 3 | 62 | 0.062 | 147.3084 | 6.7648 | 5.6101 | 0.021494 | 24.6185 | 0.25184
2025-05-19 18:07 | 940 | Remove | 2025-05-19 | 18:07 | ST | GS | - | 59 | g | 0 | 111.7 | 11.826 | 1174 | 59512 | 7:50 | 29.5 | 2.19 m/s | 25 | 30.8 | 3.92 m/s | 18.7 |  | 2.19 | m/s |  | 3.92 | m/s | 7.8417 | 0.0097833 | 9.1429 |  | -3 | 59 | 0.059 | 154.9644 | 7.3852 | 5.9271 | 0.023791 | 24.6423 | 0.23943
2025-05-19 18:08 | 941 | Remove | 2025-05-19 | 18:08 | ST | GS | - | 57.5 | g | 0 | 111.7 | 11.819 | 1173.1 | 59522 | 7:51 | 29.5 | 2.09 m/s | 22.7 | 30.7 | 4.2 m/s | 18.2 |  | 2.09 | m/s |  | 4.2 | m/s | 7.85 | 0.0097758 | 9.1527 |  | -1.5 | 57.5 | 0.0575 | 159.177 | 6.7058 | 5.7376 | 0.020616 | 24.6629 | 0.23314
2025-05-19 18:08 | 942 | Remove | 2025-05-19 | 18:08 | ST | GS | - | 57.5 | g | 0 | 111.8 | 11.822 | 1173.4 | 59531 | 7:52 | 29.5 | 2.13 m/s | 25.8 | 30.7 | 3.94 m/s | 19.1 |  | 2.13 | m/s |  | 3.94 | m/s | 7.8583 | 0.0097783 | 9.1625 |  | 0 | 57.5 | 0.0575 | 159.3471 | 7.6215 | 6.0213 | 0.023879 | 24.6868 | 0.23292
2025-05-19 18:09 | 943 | Remove | 2025-05-19 | 18:09 | ST | GS | - | 57 | g | 0 | 111.7 | 11.84 | 1175.4 | 59541 | 7:52 | 29.5 | 2.06 m/s | 22.2 | 30.7 | 3.85 m/s | 17.9 |  | 2.06 | m/s |  | 3.85 | m/s | 7.8667 | 0.009795 | 9.1723 |  | -0.5 | 57 | 0.057 | 160.9167 | 6.558 | 5.643 | 0.019872 | 24.7067 | 0.23071
2025-05-19 18:09 | 944 | Remove | 2025-05-19 | 18:09 | US | GS | - | 61.5 | g | 0 | 111.7 | 11.847 | 1176.6 | 59551 | 7:52 | 29.5 | 2.72 m/s | 22.5 | 30.7 | 4.12 m/s | 18 |  | 2.72 | m/s |  | 4.12 | m/s | 7.875 | 0.009805 | 9.1821 |  | 4.5 | 61.5 | 0.0615 | 149.3017 | 6.6467 | 5.6745 | 0.026593 | 24.7333 | 0.24865
2025-05-19 18:10 | 945 | Remove | 2025-05-19 | 18:10 | US | GS | - | 65 | g | 0 | 111.7 | 11.85 | 1176.4 | 59561 | 7:53 | 29.5 | 2.8 m/s | 22 | 30.8 | 4.15 m/s | 17.4 |  | 2.8 | m/s |  | 4.15 | m/s | 7.8833 | 0.0098033 | 9.1919 |  | 3.5 | 65 | 0.065 | 141.4132 | 6.499 | 5.515 | 0.026767 | 24.76 | 0.26252
2025-05-19 18:10 | 946 | Remove | 2025-05-19 | 18:10 | ST | GS | - | 58 | g | 0 | 111.7 | 11.852 | 1176.8 | 59571 | 7:54 | 29.5 | 2.42 m/s | 22.6 | 30.8 | 3.93 m/s | 16.4 |  | 2.42 | m/s |  | 3.93 | m/s | 7.8917 | 0.0098067 | 9.2017 |  | -7 | 58 | 0.058 | 158.6494 | 6.6762 | 5.1981 | 0.023766 | 24.7838 | 0.23402
2025-05-19 18:11 | 947 | Remove | 2025-05-19 | 18:11 | US | GS | - | 56.5 | g | 0 | 111.8 | 11.848 | 1176.9 | 59580 | 7:54 | 29.5 | 2.27 m/s | 22.6 | 30.8 | 3.84 m/s | 17.4 |  | 2.27 | m/s |  | 3.84 | m/s | 7.9003 | 0.0098075 | 9.2115 |  | -1.5 | 56.5 | 0.0565 | 163.0349 | 6.6762 | 5.515 | 0.022292 | 24.8061 | 0.22777
2025-05-19 18:11 | 948 | Remove | 2025-05-19 | 18:11 | ST | GS | - | 61.5 | g | 0 | 111.8 | 11.821 | 1173.7 | 59590 | 7:55 | 29.5 | 2.05 m/s | 21.8 | 30.8 | 4.03 m/s | 18.3 |  | 2.05 | m/s |  | 4.03 | m/s | 7.9086 | 0.0097808 | 9.2213 |  | 5 | 61.5 | 0.0615 | 149.9391 | 6.4399 | 5.8003 | 0.019419 | 24.8255 | 0.24773
2025-05-19 18:12 | 949 | Remove | 2025-05-19 | 18:12 | ST | GS | - | 60.5 | g | 0 | 111.8 | 11.834 | 1175.4 | 59600 | 7:55 | 29.5 | 2.02 m/s | 22.2 | 30.8 | 3.89 m/s | 18 |  | 2.02 | m/s |  | 3.89 | m/s | 7.9169 | 0.009795 | 9.231 |  | -1 | 60.5 | 0.0605 | 152.5793 | 6.558 | 5.7052 | 0.019486 | 24.845 | 0.24351
2025-05-19 18:12 | 950 | Remove | 2025-05-19 | 18:12 | ST | GS | - | 57 | g | 0 | 111.8 | 11.83 | 1174.5 | 59610 | 7:56 | 29.5 | 2.23 m/s | 21.5 | 30.8 | 3.76 m/s | 17.5 |  | 2.23 | m/s |  | 3.76 | m/s | 7.9253 | 0.0097875 | 9.2408 |  | -3.5 | 57 | 0.057 | 162.1199 | 6.3513 | 5.5467 | 0.020834 | 24.8658 | 0.22923
2025-05-19 18:13 | 951 | Remove | 2025-05-19 | 18:13 | US | GS | - | 57 | g | 0 | 111.8 | 11.836 | 1175.4 | 59620 | 7:56 | 29.5 | 2.3 m/s | 21.7 | 30.8 | 4.0 m/s | 17.6 |  | 2.3 | m/s |  | 4 | m/s | 7.9336 | 0.009795 | 9.2506 |  | 0 | 57 | 0.057 | 162.2918 | 6.4103 | 5.5784 | 0.021688 | 24.8875 | 0.22903
2025-05-19 18:13 | 952 | Remove | 2025-05-19 | 18:13 | US | GS | - | 58 | g | 0 | 111.8 | 11.848 | 1176.2 | 59630 | 7:57 | 29.5 | 2.27 m/s | 21.6 | 30.7 | 3.89 m/s | 17 |  | 2.27 | m/s |  | 3.89 | m/s | 7.9419 | 0.0098017 | 9.2604 |  | 1 | 58 | 0.058 | 159.6626 | 6.3808 | 5.3593 | 0.021306 | 24.9088 | 0.23285
2025-05-19 18:14 | 953 | Remove | 2025-05-19 | 18:14 | ST | GS | - | 59 | g | 0 | 111.8 | 11.807 | 1171 | 59639 | 7:57 | 29.5 | 2.13 m/s | 24.4 | 30.7 | 4.09 m/s | 16.8 |  | 2.13 | m/s |  | 4.09 | m/s | 7.9503 | 0.0097583 | 9.2702 |  | 1 | 59 | 0.059 | 157.1219 | 7.2079 | 5.2962 | 0.022584 | 24.9314 | 0.23665
2025-05-19 18:14 | 954 | Remove | 2025-05-19 | 18:14 | ST | GS | - | 59 | g | 0 | 111.7 | 11.808 | 1171.5 | 59649 | 7:58 | 29.5 | 2.04 m/s | 24.2 | 30.7 | 4.2 m/s | 18.7 |  | 2.04 | m/s |  | 4.2 | m/s | 7.9586 | 0.0097625 | 9.28 |  | 0 | 59 | 0.059 | 157.2874 | 7.1489 | 5.8952 | 0.021452 | 24.9528 | 0.23645
2025-05-19 18:15 | 955 | Remove | 2025-05-19 | 18:15 | ST | GS | - | 58.5 | g | 0 | 111.9 | 11.791 | 1169.8 | 59659 | 7:58 | 29.5 | 2.04 m/s | 25 | 30.8 | 4.04 m/s | 18 |  | 2.04 | m/s |  | 4.04 | m/s | 7.9669 | 0.0097483 | 9.2897 |  | -0.5 | 58.5 | 0.0585 | 158.7983 | 7.3852 | 5.7052 | 0.022161 | 24.975 | 0.23423
2025-05-19 18:15 | 956 | Remove | 2025-05-19 | 18:15 | ST | GS | - | 59.5 | g | 0 | 111.8 | 11.843 | 1175.4 | 59669 | 7:59 | 29.5 | 2.34 m/s | 21.7 | 30.7 | 3.72 m/s | 18.2 |  | 2.34 | m/s |  | 3.72 | m/s | 7.9753 | 0.009795 | 9.2995 |  | 1 | 59.5 | 0.0595 | 156.2941 | 6.4103 | 5.7376 | 0.022065 | 24.9971 | 0.23803
2025-05-19 18:16 | 957 | Remove | 2025-05-19 | 18:16 | ST | GS | - | 60 | g | 0 | 111.9 | 11.847 | 1177 | 59679 | 7:59 | 29.5 | 2.26 m/s | 22.2 | 30.7 | 4.1 m/s | 18.7 |  | 2.26 | m/s |  | 4.1 | m/s | 7.9836 | 0.0098083 | 9.3093 |  | 0.5 | 60 | 0.06 | 155.1551 | 6.558 | 5.8952 | 0.021801 | 25.0189 | 0.23982
2025-05-19 18:16 | 958 | Remove | 2025-05-19 | 18:16 | ST | GS | - | 58 | g | 0 | 111.8 | 11.834 | 1175.3 | 59688 | 8:00 | 29.5 | 2.02 m/s | 21.8 | 30.7 | 4.07 m/s | 17.6 |  | 2.02 | m/s |  | 4.07 | m/s | 7.9919 | 0.0097942 | 9.3191 |  | -2 | 58 | 0.058 | 160.6741 | 6.4399 | 5.5484 | 0.019135 | 25.038 | 0.23165
2025-05-19 18:17 | 959 | Remove | 2025-05-19 | 18:17 | ST | GS | - | 58.5 | g | 0 | 111.9 | 11.786 | 1169.5 | 59698 | 8:00 | 29.5 | 2.18 m/s | 25.8 | 30.7 | 4.36 m/s | 19 |  | 2.18 | m/s |  | 4.36 | m/s | 8.0003 | 0.0097458 | 9.3288 |  | 0.5 | 58.5 | 0.0585 | 159.4675 | 7.6215 | 5.9898 | 0.02444 | 25.0624 | 0.23342
2025-05-19 18:17 | 960 | Remove | 2025-05-19 | 18:17 | ST | GS | - | 56.5 | g | 0 | 111.9 | 11.796 | 1170.8 | 59708 | 8:01 | 29.5 | 1.91 m/s | 23.3 | 30.7 | 4.06 m/s | 17.3 |  | 1.91 | m/s |  | 4.06 | m/s | 8.0086 | 0.0097567 | 9.3386 |  | -2 | 56.5 | 0.0565 | 165.285 | 6.883 | 5.4539 | 0.019338 | 25.0818 | 0.22526
2025-05-19 18:18 | 961 | Keep | 2025-05-19 | 18:18 | ST | GS | - | 61.5 | g | 0 | 112 | 11.853 | 1178.1 | 59718 | 8:01 | 29.5 | 2.83 m/s | 20.9 | 30.7 | 3.88 m/s | 17.1 |  | 2.83 | m/s |  | 3.88 | m/s | 8.0169 | 0.0098175 | 9.3484 |  | 5 | 61.5 | 0.0615 | 152.0068 | 6.174 | 5.3908 | 0.025701 | 25.1075 | 0.24495
2025-05-19 18:18 | 962 | Remove | 2025-05-19 | 18:18 | ST | GS | - | 58.5 | g | 0 | 111.9 | 11.833 | 1175.1 | 59728 | 8:02 | 29.5 | 2.41 m/s | 22.3 | 30.7 | 4.44 m/s | 17 |  | 2.41 | m/s |  | 4.44 | m/s | 8.0253 | 0.0097925 | 9.3582 |  | -3 | 58.5 | 0.0585 | 159.9694 | 6.5876 | 5.3593 | 0.023353 | 25.1308 | 0.23278
2025-05-19 18:19 | 963 | Remove | 2025-05-19 | 18:19 | US | GS | - | 59 | g | 0 | 111.9 | 11.834 | 1175.2 | 59738 | 8:02 | 29.5 | 2.51 m/s | 21.5 | 30.7 | 4.03 m/s | 17 |  | 2.51 | m/s |  | 4.03 | m/s | 8.0336 | 0.0097933 | 9.368 |  | 0.5 | 59 | 0.059 | 158.7798 | 6.3513 | 5.3593 | 0.02345 | 25.1543 | 0.23455
2025-05-19 18:19 | 964 | Remove | 2025-05-19 | 18:19 | ST | GS | - | 60.5 | g | 0 | 111.9 | 11.845 | 1176.7 | 59747 | 8:03 | 29.5 | 2.12 m/s | 20.9 | 30.7 | 3.89 m/s | 16.1 |  | 2.12 | m/s |  | 3.89 | m/s | 8.0422 | 0.0098058 | 9.3778 |  | 1.5 | 60.5 | 0.0605 | 155.0052 | 6.174 | 5.0756 | 0.019253 | 25.1735 | 0.24033
2025-05-19 18:20 | 965 | Remove | 2025-05-19 | 18:20 | US | GS | - | 67.5 | g | 0 | 111.9 | 11.828 | 1174.6 | 59757 | 8:03 | 29.5 | 2.34 m/s | 23.8 | 30.7 | 3.98 m/s | 20.5 |  | 2.34 | m/s |  | 3.98 | m/s | 8.0506 | 0.0097883 | 9.3876 |  | 7 | 67.5 | 0.0675 | 139.0756 | 7.0307 | 6.4627 | 0.0242 | 25.1977 | 0.26788
2025-05-19 18:20 | 966 | Remove | 2025-05-19 | 18:20 | ST | GS | - | 57.5 | g | 0 | 111.9 | 11.803 | 1171.6 | 59767 | 8:04 | 29.5 | 2.18 m/s | 23.9 | 30.7 | 3.84 m/s | 17.5 |  | 2.18 | m/s |  | 3.84 | m/s | 8.0589 | 0.0097633 | 9.3974 |  | -10 | 57.5 | 0.0575 | 163.4324 | 7.0602 | 5.5169 | 0.02264 | 25.2204 | 0.22799
2025-05-19 18:21 | 967 | Remove | 2025-05-19 | 18:21 | US | GS | - | 59.5 | g | 0 | 111.9 | 11.832 | 1174.8 | 59777 | 8:04 | 29.5 | 2.15 m/s | 22.3 | 30.7 | 3.88 m/s | 17.9 |  | 2.15 | m/s |  | 3.88 | m/s | 8.0672 | 0.00979 | 9.4072 |  | 2 | 59.5 | 0.0595 | 158.1034 | 6.5876 | 5.643 | 0.020834 | 25.2412 | 0.23573
2025-05-19 18:21 | 968 | Remove | 2025-05-19 | 18:21 | ST | GS | - | 60 | g | 0 | 111.8 | 11.814 | 1172.6 | 59787 | 8:05 | 29.5 | 2.06 m/s | 22.7 | 30.7 | 3.94 m/s | 17.6 |  | 2.06 | m/s |  | 3.94 | m/s | 8.0756 | 0.0097717 | 9.4169 |  | 0.5 | 60 | 0.06 | 156.9488 | 6.7058 | 5.5484 | 0.02032 | 25.2615 | 0.23752
2025-05-19 18:22 | 969 | Remove | 2025-05-19 | 18:22 | ST | GS | - | 62 | g | 0 | 111.9 | 11.814 | 1172.5 | 59796 | 8:05 | 29.5 | 2.42 m/s | 23.5 | 30.7 | 3.9 m/s | 17.6 |  | 2.42 | m/s |  | 3.9 | m/s | 8.0839 | 0.0097708 | 9.4267 |  | 2 | 62 | 0.062 | 152.0435 | 6.9421 | 5.5484 | 0.024712 | 25.2863 | 0.24519
2025-05-19 18:22 | 970 | Remove | 2025-05-19 | 18:22 | ST | GS | - | 61.5 | g | 0 | 111.9 | 11.805 | 1171.9 | 59806 | 8:06 | 29.5 | 2.54 m/s | 23 | 30.7 | 4.29 m/s | 17.9 |  | 2.54 | m/s |  | 4.29 | m/s | 8.0922 | 0.0097658 | 9.4365 |  | -0.5 | 61.5 | 0.0615 | 153.4384 | 6.7944 | 5.643 | 0.025385 | 25.3116 | 0.24297
2025-05-19 18:23 | 971 | Remove | 2025-05-19 | 18:23 | US | GS | - | 59 | g | 0 | 112 | 11.799 | 1171.6 | 59816 | 8:06 | 29.5 | 2.04 m/s | 22.8 | 30.7 | 4.1 m/s | 17.1 |  | 2.04 | m/s |  | 4.1 | m/s | 8.1006 | 0.0097633 | 9.4462 |  | -2.5 | 59 | 0.059 | 160.1055 | 6.7353 | 5.3908 | 0.020211 | 25.3318 | 0.23291
2025-05-19 18:23 | 972 | Remove | 2025-05-19 | 18:23 | ST | GS | - | 58.5 | g | 0 | 112 | 11.809 | 1171.9 | 59826 | 8:07 | 29.4 | 2.15 m/s | 23.2 | 30.7 | 4.04 m/s | 18.7 |  | 2.15 | m/s |  | 4.04 | m/s | 8.1092 | 0.0097658 | 9.456 |  | -0.5 | 58.5 | 0.0585 | 161.6409 | 6.8162 | 5.8952 | 0.021557 | 25.3534 | 0.23074
2025-05-19 18:24 | 973 | Remove | 2025-05-19 | 18:24 | ST | GS | - | 59.5 | g | 0 | 112.1 | 11.775 | 1168.5 | 59836 | 8:07 | 29.4 | 2.19 m/s | 26.6 | 30.7 | 3.81 m/s | 19.6 |  | 2.19 | m/s |  | 3.81 | m/s | 8.1175 | 0.0097375 | 9.4657 |  | 1 | 59.5 | 0.0595 | 159.0879 | 7.8152 | 6.1789 | 0.025176 | 25.3786 | 0.23445
2025-05-19 18:24 | 974 | Remove | 2025-05-19 | 18:24 | US | GS | - | 63 | g | 0 | 112 | 11.752 | 1165 | 59845 | 8:08 | 29.4 | 2.08 m/s | 28.7 | 30.7 | 4.15 m/s | 19.4 |  | 2.08 | m/s |  | 4.15 | m/s | 8.1258 | 0.0097083 | 9.4754 |  | 3.5 | 63 | 0.063 | 150.4038 | 8.4322 | 6.1159 | 0.025799 | 25.4044 | 0.24799
2025-05-19 18:25 | 975 | Remove | 2025-05-19 | 18:25 | ST | GS | - | 60 | g | 0 | 112 | 11.81 | 1172.6 | 59855 | 8:08 | 29.4 | 2.61 m/s | 24.2 | 30.7 | 3.93 m/s | 18.1 |  | 2.61 | m/s |  | 3.93 | m/s | 8.1342 | 0.0097717 | 9.4852 |  | -3 | 60 | 0.06 | 158.0868 | 7.11 | 5.7061 | 0.027297 | 25.4317 | 0.23593
2025-05-19 18:25 | 976 | Remove | 2025-05-19 | 18:25 | ST | GS | - | 59.5 | g | 0 | 112.2 | 11.784 | 1169.9 | 59865 | 8:09 | 29.4 | 2.04 m/s | 23.2 | 30.7 | 4.23 m/s | 17.8 |  | 2.04 | m/s |  | 4.23 | m/s | 8.1425 | 0.0097492 | 9.495 |  | -0.5 | 59.5 | 0.0595 | 159.5791 | 6.8162 | 5.6115 | 0.020454 | 25.4521 | 0.23377
2025-05-19 18:26 | 977 | Remove | 2025-05-19 | 18:26 | ST | GS | - | 61.5 | g | 0 | 112.2 | 11.816 | 1173.8 | 59875 | 8:09 | 29.4 | 2.57 m/s | 22.2 | 30.7 | 3.97 m/s | 17.8 |  | 2.57 | m/s |  | 3.97 | m/s | 8.1508 | 0.0097817 | 9.5047 |  | 2 | 61.5 | 0.0615 | 154.5486 | 6.5224 | 5.6115 | 0.024657 | 25.4768 | 0.2414
2025-05-19 18:26 | 978 | Remove | 2025-05-19 | 18:26 | US | GS | - | 62 | g | 0 | 112.2 | 11.788 | 1171.3 | 59885 | 8:10 | 29.4 | 2.13 m/s | 23.6 | 30.7 | 4.23 m/s | 18.5 |  | 2.13 | m/s |  | 4.23 | m/s | 8.1592 | 0.0097608 | 9.5145 |  | 0.5 | 62 | 0.062 | 153.4597 | 6.9338 | 5.8322 | 0.021725 | 25.4985 | 0.24315
2025-05-19 18:27 | 979 | Remove | 2025-05-19 | 18:27 | US | GS | - | 60 | g | 0 | 112.2 | 11.809 | 1173.3 | 59894 | 8:10 | 29.4 | 2.18 m/s | 22.7 | 30.7 | 4.3 m/s | 17.3 |  | 2.18 | m/s |  | 4.3 | m/s | 8.1675 | 0.0097775 | 9.5243 |  | -2 | 60 | 0.06 | 158.738 | 6.6693 | 5.4539 | 0.021387 | 25.5199 | 0.23511
2025-05-19 18:27 | 980 | Remove | 2025-05-19 | 18:27 | US | GS | - | 64 | g | 0 | 112.2 | 11.819 | 1174.5 | 59904 | 8:11 | 29.4 | 2.48 m/s | 22.5 | 30.7 | 3.85 m/s | 17.1 |  | 2.48 | m/s |  | 3.85 | m/s | 8.1758 | 0.0097875 | 9.5341 |  | 4 | 64 | 0.064 | 148.9698 | 6.6106 | 5.3908 | 0.024115 | 25.544 | 0.25055
2025-05-19 18:28 | 981 | Remove | 2025-05-19 | 18:28 | ST | GS | - | 58.5 | g | 0 | 112.2 | 11.806 | 1172.6 | 59914 | 8:11 | 29.4 | 2.04 m/s | 22.2 | 30.7 | 4.16 m/s | 17 |  | 2.04 | m/s |  | 4.16 | m/s | 8.1844 | 0.0097717 | 9.5438 |  | -5.5 | 58.5 | 0.0585 | 163.1425 | 6.5224 | 5.3593 | 0.019572 | 25.5636 | 0.22884
2025-05-19 18:28 | 982 | Remove | 2025-05-19 | 18:28 | US | GS | - | 61 | g | 0 | 112.3 | 11.783 | 1170.1 | 59924 | 8:12 | 29.4 | 2.08 m/s | 23.4 | 30.7 | 4.06 m/s | 18.5 |  | 2.08 | m/s |  | 4.06 | m/s | 8.1928 | 0.0097508 | 9.5536 |  | 2.5 | 61 | 0.061 | 156.6162 | 6.875 | 5.8322 | 0.021035 | 25.5846 | 0.23842
2025-05-19 18:29 | 983 | Remove | 2025-05-19 | 18:29 | ST | GS | - | 58.5 | g | 0 | 112.2 | 11.816 | 1173.5 | 59933 | 8:12 | 29.4 | 2.38 m/s | 22.5 | 30.7 | 4.16 m/s | 17.2 |  | 2.38 | m/s |  | 4.16 | m/s | 8.2011 | 0.0097792 | 9.5634 |  | -2.5 | 58.5 | 0.0585 | 163.4764 | 6.6106 | 5.4223 | 0.023143 | 25.6078 | 0.22845
2025-05-19 18:29 | 984 | Remove | 2025-05-19 | 18:29 | US | GS | - | 67.5 | g | 0 | 112.3 | 11.818 | 1174.4 | 59943 | 8:13 | 29.4 | 2.16 m/s | 21.7 | 30.7 | 3.88 m/s | 17.6 |  | 2.16 | m/s |  | 3.88 | m/s | 8.2094 | 0.0097867 | 9.5732 |  | 9 | 67.5 | 0.0675 | 141.8245 | 6.3755 | 5.5484 | 0.020257 | 25.628 | 0.26338
2025-05-19 18:30 | 985 | Remove | 2025-05-19 | 18:30 | ST | GS | - | 60 | g | 0 | 112.3 | 11.828 | 1175.3 | 59953 | 8:13 | 29.4 | 2.7 m/s | 22.7 | 30.7 | 3.94 m/s | 17.2 |  | 2.7 | m/s |  | 3.94 | m/s | 8.2178 | 0.0097942 | 9.5829 |  | -7.5 | 60 | 0.06 | 159.7158 | 6.6693 | 5.4223 | 0.026488 | 25.6545 | 0.23388
2025-05-19 18:30 | 986 | Remove | 2025-05-19 | 18:30 | ST | GS | - | 61.5 | g | 0 | 112.3 | 11.836 | 1176.3 | 59963 | 8:14 | 29.5 | 2.12 m/s | 21.3 | 30.7 | 3.76 m/s | 17.2 |  | 2.12 | m/s |  | 3.76 | m/s | 8.2261 | 0.0098025 | 9.5928 |  | 1.5 | 61.5 | 0.0615 | 155.9797 | 6.2922 | 5.4223 | 0.019622 | 25.6741 | 0.23954
2025-05-19 18:31 | 987 | Remove | 2025-05-19 | 18:31 | ST | GS | - | 60 | g | 0 | 112.4 | 11.817 | 1175.1 | 59973 | 8:14 | 29.4 | 2.15 m/s | 22.7 | 30.7 | 3.9 m/s | 17.9 |  | 2.15 | m/s |  | 3.9 | m/s | 8.2344 | 0.0097925 | 9.6025 |  | -1.5 | 60 | 0.06 | 160.0424 | 6.6693 | 5.643 | 0.021092 | 25.6952 | 0.23351
2025-05-19 18:31 | 988 | Remove | 2025-05-19 | 18:31 | ST | GS | - | 60.5 | g | 0 | 112.2 | 11.809 | 1172.6 | 59983 | 8:15 | 29.5 | 2.11 m/s | 21.5 | 30.7 | 4.41 m/s | 16.9 |  | 2.11 | m/s |  | 4.41 | m/s | 8.2428 | 0.0097717 | 9.6123 |  | 0.5 | 60.5 | 0.0605 | 158.8812 | 6.3513 | 5.3278 | 0.019713 | 25.7149 | 0.23527
2025-05-19 18:32 | 989 | Remove | 2025-05-19 | 18:32 | US | GS | - | 61 | g | 0 | 112.4 | 11.788 | 1171.1 | 59992 | 8:15 | 29.4 | 2.23 m/s | 22.5 | 30.7 | 3.94 m/s | 17.6 |  | 2.23 | m/s |  | 3.94 | m/s | 8.2511 | 0.0097592 | 9.6221 |  | 0.5 | 61 | 0.061 | 157.7389 | 6.6106 | 5.5484 | 0.021684 | 25.7366 | 0.23702
2025-05-19 18:32 | 990 | Remove | 2025-05-19 | 18:32 | ST | GS | - | 61 | g | 0 | 112.4 | 11.807 | 1173.5 | 60002 | 8:16 | 29.4 | 2.51 m/s | 21.6 | 30.7 | 4.12 m/s | 17.2 |  | 2.51 | m/s |  | 4.12 | m/s | 8.2594 | 0.0097792 | 9.6319 |  | 0 | 61 | 0.061 | 157.8992 | 6.3462 | 5.4223 | 0.023431 | 25.7601 | 0.2368
2025-05-19 18:33 | 991 | Keep | 2025-05-19 | 18:33 | US | GS | - | 62.5 | g | 0 | 112.4 | 11.824 | 1175.4 | 60012 | 8:16 | 29.5 | 2.68 m/s | 21.5 | 30.7 | 3.94 m/s | 17.8 |  | 2.68 | m/s |  | 3.94 | m/s | 8.2678 | 0.009795 | 9.6416 |  | 1.5 | 62.5 | 0.0625 | 154.2664 | 6.3513 | 5.6115 | 0.025038 | 25.7851 | 0.24239
2025-05-19 18:33 | 992 | Remove | 2025-05-19 | 18:33 | ST | GS | - | 61 | g | 0 | 112.4 | 11.81 | 1173.9 | 60022 | 8:17 | 29.5 | 2.31 m/s | 21.9 | 30.7 | 4.09 m/s | 17.5 |  | 2.31 | m/s |  | 4.09 | m/s | 8.2761 | 0.0097825 | 9.6514 |  | -1.5 | 61 | 0.061 | 158.2202 | 6.4694 | 5.5169 | 0.021983 | 25.8071 | 0.23637
2025-05-19 18:34 | 993 | Remove | 2025-05-19 | 18:34 | ST | GS | - | 61 | g | 0 | 112.4 | 11.814 | 1174.1 | 60032 | 8:17 | 29.5 | 2.74 m/s | 21.1 | 30.7 | 4.4 m/s | 17 |  | 2.74 | m/s |  | 4.4 | m/s | 8.2844 | 0.0097842 | 9.6612 |  | 0 | 61 | 0.061 | 158.3806 | 6.2331 | 5.3593 | 0.025122 | 25.8322 | 0.23614
2025-05-19 18:34 | 994 | Remove | 2025-05-19 | 18:34 | US | GS | - | 60.5 | g | 0 | 112.4 | 11.797 | 1172.5 | 60041 | 8:18 | 29.5 | 2.74 m/s | 21.1 | 30.7 | 4.26 m/s | 18.1 |  | 2.74 | m/s |  | 4.26 | m/s | 8.2928 | 0.0097708 | 9.671 |  | -0.5 | 60.5 | 0.0605 | 159.851 | 6.2331 | 5.7061 | 0.025122 | 25.8573 | 0.23398
2025-05-19 18:35 | 995 | Remove | 2025-05-19 | 18:35 | ST | GS | - | 59.5 | g | 0 | 112.4 | 11.793 | 1171.7 | 60051 | 8:18 | 29.4 | 2.2 m/s | 21.8 | 30.7 | 4.09 m/s | 17.8 |  | 2.2 | m/s |  | 4.09 | m/s | 8.3011 | 0.0097642 | 9.6807 |  | -1 | 59.5 | 0.0595 | 162.7017 | 6.4049 | 5.6115 | 0.020727 | 25.878 | 0.22992
2025-05-19 18:35 | 996 | Remove | 2025-05-19 | 18:35 | ST | GS | - | 63.5 | g | 0 | 112.4 | 11.78 | 1170.2 | 60061 | 8:19 | 29.4 | 2.37 m/s | 24.7 | 30.7 | 3.92 m/s | 17.4 |  | 2.37 | m/s |  | 3.92 | m/s | 8.3094 | 0.0097517 | 9.6905 |  | 4 | 63.5 | 0.0635 | 152.6063 | 7.2569 | 5.4854 | 0.025299 | 25.9033 | 0.24514
2025-05-19 18:36 | 997 | Remove | 2025-05-19 | 18:36 | ST | GS | - | 64 | g | 0 | 112.5 | 11.772 | 1169.7 | 60071 | 8:19 | 29.4 | 2.16 m/s | 24 | 30.7 | 4.04 m/s | 20.1 |  | 2.16 | m/s |  | 4.04 | m/s | 8.3178 | 0.0097475 | 9.7002 |  | 0.5 | 64 | 0.064 | 151.5664 | 7.0513 | 6.3366 | 0.022404 | 25.9257 | 0.24686
2025-05-19 18:36 | 998 | Remove | 2025-05-19 | 18:36 | ST | GS | - | 61.5 | g | 0 | 112.4 | 11.761 | 1167.7 | 60081 | 8:20 | 29.4 | 2.18 m/s | 23.7 | 30.7 | 4.13 m/s | 18.7 |  | 2.18 | m/s |  | 4.13 | m/s | 8.3264 | 0.0097308 | 9.71 |  | -2.5 | 61.5 | 0.0615 | 157.8858 | 6.9631 | 5.8952 | 0.022329 | 25.9481 | 0.23701
2025-05-19 18:37 | 999 | Remove | 2025-05-19 | 18:37 | US | GS | - | 62 | g | 0 | 112.6 | 11.752 | 1167.7 | 60090 | 8:20 | 29.4 | 2.11 m/s | 22.7 | 30.7 | 4.46 m/s | 18.5 |  | 2.11 | m/s |  | 4.46 | m/s | 8.3347 | 0.0097308 | 9.7197 |  | 0.5 | 62 | 0.062 | 156.7695 | 6.6693 | 5.8322 | 0.0207 | 25.9688 | 0.23875
2025-05-19 18:37 | 1000 | Remove | 2025-05-19 | 18:37 | US | GS | - | 68.5 | g | 0 | 112.5 | 11.77 | 1169.5 | 60100 | 8:21 | 29.4 | 2.34 m/s | 23 | 30.7 | 4.06 m/s | 18.7 |  | 2.34 | m/s |  | 4.06 | m/s | 8.3431 | 0.0097458 | 9.7295 |  | 6.5 | 68.5 | 0.0685 | 142.0359 | 6.7575 | 5.8952 | 0.02326 | 25.992 | 0.26354
2025-05-19 18:38 | 1001 | Remove | 2025-05-19 | 18:38 | US | GS | - | 61.5 | g | 0 | 112.4 | 11.811 | 1174.3 | 60110 | 8:21 | 29.4 | 2.34 m/s | 23 | 30.7 | 3.85 m/s | 17.2 |  | 2.34 | m/s |  | 3.85 | m/s | 8.3514 | 0.0097858 | 9.7392 |  | -7 | 61.5 | 0.0615 | 158.3617 | 6.7575 | 5.4223 | 0.02326 | 26.0153 | 0.2364
2025-05-19 18:38 | 1002 | Remove | 2025-05-19 | 18:38 | US | GS | - | 70 | g | 0 | 112.5 | 11.807 | 1173.9 | 60120 | 8:22 | 29.4 | 2.2 m/s | 22.5 | 30.7 | 3.93 m/s | 18.4 |  | 2.2 | m/s |  | 3.93 | m/s | 8.3597 | 0.0097825 | 9.749 |  | 8.5 | 70 | 0.07 | 139.2718 | 6.6106 | 5.8006 | 0.021393 | 26.0367 | 0.26885
2025-05-19 18:39 | 1003 | Remove | 2025-05-19 | 18:39 | US | GS | - | 62 | g | 0 | 112.5 | 11.764 | 1168.8 | 60129 | 8:22 | 29.4 | 2.11 m/s | 21.9 | 30.7 | 4.09 m/s | 17.6 |  | 2.11 | m/s |  | 4.09 | m/s | 8.3681 | 0.00974 | 9.7588 |  | -8 | 62 | 0.062 | 157.3994 | 6.4343 | 5.5484 | 0.01997 | 26.0567 | 0.23794
2025-05-19 18:39 | 1004 | Remove | 2025-05-19 | 18:39 | ST | GS | - | 64 | g | 0 | 112.5 | 11.774 | 1170.4 | 60139 | 8:23 | 29.4 | 2.16 m/s | 22.9 | 30.7 | 3.93 m/s | 18.4 |  | 2.16 | m/s |  | 3.93 | m/s | 8.3764 | 0.0097533 | 9.7685 |  | 2 | 64 | 0.064 | 152.6331 | 6.7281 | 5.8006 | 0.021377 | 26.078 | 0.24542
2025-05-19 18:40 | 1005 | Remove | 2025-05-19 | 18:40 | US | GS | - | 66.5 | g | 0 | 112.4 | 11.802 | 1172.8 | 60149 | 8:23 | 29.4 | 2.01 m/s | 22.3 | 30.7 | 3.98 m/s | 18.4 |  | 2.01 | m/s |  | 3.98 | m/s | 8.3847 | 0.0097733 | 9.7783 |  | 2.5 | 66.5 | 0.0665 | 147.042 | 6.5518 | 5.8006 | 0.019371 | 26.0974 | 0.25481
2025-05-19 18:40 | 1006 | Remove | 2025-05-19 | 18:40 | US | GS | - | 67.5 | g | 0 | 112.6 | 11.781 | 1171.4 | 60159 | 8:24 | 29.4 | 2.33 m/s | 22 | 30.7 | 4.09 m/s | 17 |  | 2.33 | m/s |  | 4.09 | m/s | 8.3931 | 0.0097617 | 9.7881 |  | 1 | 67.5 | 0.0675 | 145.0082 | 6.4637 | 5.3593 | 0.022153 | 26.1196 | 0.25843
2025-05-19 18:41 | 1007 | Remove | 2025-05-19 | 18:41 | ST | GS | - | 63 | g | 0 | 112.5 | 11.772 | 1169.7 | 60169 | 8:24 | 29.4 | 2.48 m/s | 22.3 | 30.7 | 4.04 m/s | 17.6 |  | 2.48 | m/s |  | 4.04 | m/s | 8.4014 | 0.0097475 | 9.7978 |  | -4.5 | 63 | 0.063 | 155.5206 | 6.5518 | 5.5484 | 0.023901 | 26.1435 | 0.24098
2025-05-19 18:41 | 1008 | Remove | 2025-05-19 | 18:41 | ST | GS | - | 62.5 | g | 0 | 112.6 | 11.792 | 1172.7 | 60178 | 8:25 | 29.4 | 2.5 m/s | 22.7 | 30.7 | 3.98 m/s | 16.4 |  | 2.5 | m/s |  | 3.98 | m/s | 8.4097 | 0.0097725 | 9.8076 |  | -0.5 | 62.5 | 0.0625 | 156.9212 | 6.6693 | 5.1701 | 0.024526 | 26.168 | 0.23884
2025-05-19 18:42 | 1009 | Remove | 2025-05-19 | 18:42 | ST | GS | - | 61 | g | 0 | 112.5 | 11.776 | 1170 | 60188 | 8:25 | 29.4 | 2.12 m/s | 21.9 | 30.7 | 4.09 m/s | 16.3 |  | 2.12 | m/s |  | 4.09 | m/s | 8.4181 | 0.00975 | 9.8173 |  | -1.5 | 61 | 0.061 | 160.9397 | 6.4343 | 5.1386 | 0.020065 | 26.188 | 0.23293
2025-05-19 18:42 | 1010 | Remove | 2025-05-19 | 18:42 | ST | GS | - | 63 | g | 0 | 112.5 | 11.765 | 1169.5 | 60198 | 8:26 | 29.4 | 2.06 m/s | 21.3 | 30.7 | 4.09 m/s | 17.6 |  | 2.06 | m/s |  | 4.09 | m/s | 8.4264 | 0.0097458 | 9.8271 |  | 2 | 63 | 0.063 | 155.9852 | 6.258 | 5.5484 | 0.018963 | 26.207 | 0.24039
2025-05-19 18:43 | 1011 | Remove | 2025-05-19 | 18:43 | ST | GS | - | 64.5 | g | 0 | 112.7 | 11.761 | 1168.8 | 60208 | 8:26 | 29.4 | 2.11 m/s | 22.1 | 30.7 | 4.21 m/s | 18.6 |  | 2.11 | m/s |  | 4.21 | m/s | 8.4347 | 0.00974 | 9.8368 |  | 1.5 | 64.5 | 0.0645 | 152.5087 | 6.4931 | 5.8637 | 0.020153 | 26.2272 | 0.24593
2025-05-19 18:43 | 1012 | Remove | 2025-05-19 | 18:43 | ST | GS | - | 64 | g | 0 | 112.6 | 11.763 | 1168.8 | 60218 | 8:27 | 29.4 | 2.04 m/s | 23.5 | 30.7 | 4.06 m/s | 17.6 |  | 2.04 | m/s |  | 4.06 | m/s | 8.4431 | 0.00974 | 9.8465 |  | -0.5 | 64 | 0.064 | 153.8523 | 6.9044 | 5.5484 | 0.020718 | 26.2479 | 0.24383
2025-05-19 18:44 | 1013 | Remove | 2025-05-19 | 18:44 | ST | GS | - | 65 | g | 0 | 112.6 | 11.774 | 1171 | 60227 | 8:27 | 29.4 | 1.98 m/s | 22.7 | 30.6 | 3.97 m/s | 18.2 |  | 1.98 | m/s |  | 3.97 | m/s | 8.4514 | 0.0097583 | 9.8563 |  | 1 | 65 | 0.065 | 151.6355 | 6.6693 | 5.7067 | 0.019425 | 26.2673 | 0.24746
2025-05-19 18:44 | 1014 | Remove | 2025-05-19 | 18:44 | ST | GS | - | 64 | g | 0 | 112.6 | 11.736 | 1165.7 | 60237 | 8:28 | 29.4 | 2.42 m/s | 23.1 | 30.6 | 3.96 m/s | 20 |  | 2.42 | m/s |  | 3.96 | m/s | 8.4597 | 0.0097142 | 9.866 |  | -1 | 64 | 0.064 | 154.1566 | 6.7869 | 6.2711 | 0.024159 | 26.2915 | 0.24342
2025-05-19 18:45 | 1015 | Remove | 2025-05-19 | 18:45 | ST | GS | - | 65.5 | g | 0 | 112.6 | 11.79 | 1172.8 | 60247 | 8:28 | 29.4 | 2.0 m/s | 24 | 30.6 | 4.01 m/s | 19.3 |  | 2 | m/s |  | 4.01 | m/s | 8.4683 | 0.0097733 | 9.8758 |  | 1.5 | 65.5 | 0.0655 | 150.7755 | 7.0513 | 6.0516 | 0.020744 | 26.3122 | 0.24893
2025-05-19 18:45 | 1016 | Remove | 2025-05-19 | 18:45 | ST | GS | - | 64 | g | 0 | 112.5 | 11.743 | 1166 | 60256 | 8:29 | 29.4 | 2.08 m/s | 21.5 | 30.6 | 4.06 m/s | 19.1 |  | 2.08 | m/s |  | 4.06 | m/s | 8.4767 | 0.0097167 | 9.8855 |  | -1.5 | 64 | 0.064 | 154.4611 | 6.3168 | 5.9889 | 0.019327 | 26.3315 | 0.24305
2025-05-19 18:46 | 1017 | Remove | 2025-05-19 | 18:46 | ST | GS | - | 64 | g | 0 | 112.6 | 11.771 | 1169.8 | 60266 | 8:29 | 29.4 | 2.02 m/s | 25.4 | 30.6 | 4.06 m/s | 17.4 |  | 2.02 | m/s |  | 4.06 | m/s | 8.485 | 0.0097483 | 9.8953 |  | 0 | 64 | 0.064 | 154.6134 | 7.4626 | 5.4559 | 0.022174 | 26.3537 | 0.24285
2025-05-19 18:46 | 1018 | Remove | 2025-05-19 | 18:46 | ST | GS | - | 64.5 | g | 0 | 112.5 | 11.775 | 1170.2 | 60276 | 8:30 | 29.4 | 2.04 m/s | 24 | 30.6 | 4.26 m/s | 17.7 |  | 2.04 | m/s |  | 4.26 | m/s | 8.4933 | 0.0097517 | 9.905 |  | 0.5 | 64.5 | 0.0645 | 153.5661 | 7.0513 | 5.5499 | 0.021159 | 26.3749 | 0.24455
2025-05-19 18:47 | 1019 | Remove | 2025-05-19 | 18:47 | ST | GS | - | 65.5 | g | 0 | 112.7 | 11.751 | 1167.9 | 60286 | 8:30 | 29.4 | 2.23 m/s | 22.2 | 30.6 | 3.96 m/s | 17.6 |  | 2.23 | m/s |  | 3.96 | m/s | 8.5017 | 0.0097325 | 9.9147 |  | 1 | 65.5 | 0.0655 | 151.3701 | 6.5224 | 5.5186 | 0.021395 | 26.3963 | 0.24814
2025-05-19 18:47 | 1020 | Remove | 2025-05-19 | 18:47 | ST | GS | - | 64 | g | 0 | 112.6 | 11.744 | 1166.6 | 60296 | 8:31 | 29.4 | 2.0 m/s | 23.8 | 30.6 | 3.98 m/s | 19.1 |  | 2 | m/s |  | 3.98 | m/s | 8.51 | 0.0097217 | 9.9245 |  | -1.5 | 64 | 0.064 | 155.0698 | 6.9925 | 5.9889 | 0.020572 | 26.4168 | 0.24227
2025-05-19 18:48 | 1021 | Keep | 2025-05-19 | 18:48 | ST | GS | - | 66 | g | 0 | 112.7 | 11.783 | 1171.5 | 60305 | 8:31 | 29.3 | 2.09 m/s | 23.1 | 30.6 | 3.86 m/s | 16.8 |  | 2.09 | m/s |  | 3.86 | m/s | 8.5183 | 0.0097625 | 9.9342 |  | 2 | 66 | 0.066 | 150.5186 | 6.75 | 5.2677 | 0.020752 | 26.4376 | 0.24964
2025-05-19 18:48 | 1022 | Remove | 2025-05-19 | 18:48 | ST | GS | - | 64 | g | 0 | 112.7 | 11.776 | 1170.8 | 60315 | 8:32 | 29.4 | 1.98 m/s | 21.7 | 30.6 | 4.07 m/s | 17.6 |  | 1.98 | m/s |  | 4.07 | m/s | 8.5267 | 0.0097567 | 9.944 |  | -2 | 64 | 0.064 | 155.3748 | 6.3755 | 5.5186 | 0.018569 | 26.4562 | 0.24191
2025-05-19 18:49 | 1023 | Remove | 2025-05-19 | 18:49 | US | GS | - | 63.5 | g | 0 | 112.7 | 11.769 | 1170.2 | 60325 | 8:32 | 29.4 | 2.23 m/s | 22.5 | 30.6 | 3.93 m/s | 19.7 |  | 2.23 | m/s |  | 3.93 | m/s | 8.535 | 0.0097517 | 9.9537 |  | -0.5 | 63.5 | 0.0635 | 156.7517 | 6.6106 | 6.1771 | 0.021684 | 26.4778 | 0.23982
2025-05-19 18:49 | 1024 | Remove | 2025-05-19 | 18:49 | US | GS | - | 71.5 | g | 0 | 112.6 | 11.777 | 1170.5 | 60335 | 8:33 | 29.4 | 2.68 m/s | 23.1 | 30.6 | 3.96 m/s | 17.2 |  | 2.68 | m/s |  | 3.96 | m/s | 8.5433 | 0.0097542 | 9.9635 |  | 8 | 71.5 | 0.0715 | 139.3495 | 6.7869 | 5.3932 | 0.026755 | 26.5046 | 0.26976
2025-05-19 18:50 | 1025 | Remove | 2025-05-19 | 18:50 | ST | GS | - | 64.5 | g | 0 | 112.7 | 11.782 | 1171.8 | 60345 | 8:33 | 29.4 | 2.2 m/s | 24.1 | 30.6 | 4.09 m/s | 17.9 |  | 2.2 | m/s |  | 4.09 | m/s | 8.5517 | 0.009765 | 9.9733 |  | -7 | 64.5 | 0.0645 | 154.6241 | 7.0807 | 5.6127 | 0.022914 | 26.5275 | 0.24314
2025-05-19 18:50 | 1026 | Remove | 2025-05-19 | 18:50 | US | GS | - | 65 | g | 0 | 112.7 | 11.771 | 1170 | 60354 | 8:34 | 29.4 | 2.45 m/s | 21.7 | 30.6 | 3.98 m/s | 17.2 |  | 2.45 | m/s |  | 3.98 | m/s | 8.56 | 0.00975 | 9.983 |  | 0.5 | 65 | 0.065 | 153.5847 | 6.3755 | 5.3932 | 0.022977 | 26.5505 | 0.24482
2025-05-19 18:51 | 1027 | Remove | 2025-05-19 | 18:51 | US | GS | - | 65.5 | g | 0 | 112.6 | 11.775 | 1170.9 | 60364 | 8:34 | 29.4 | 2.2 m/s | 23.2 | 30.6 | 3.97 m/s | 17.1 |  | 2.2 | m/s |  | 3.97 | m/s | 8.5683 | 0.0097575 | 9.9928 |  | 0.5 | 65.5 | 0.0655 | 152.5613 | 6.8162 | 5.3618 | 0.022058 | 26.5725 | 0.24649
2025-05-19 18:51 | 1028 | Remove | 2025-05-19 | 18:51 | US | GS | - | 71 | g | 0 | 112.7 | 11.766 | 1169.4 | 60374 | 8:35 | 29.4 | 2.16 m/s | 21.4 | 30.6 | 3.84 m/s | 18.1 |  | 2.16 | m/s |  | 3.84 | m/s | 8.5767 | 0.009745 | 10.0025 |  | 5.5 | 71 | 0.071 | 140.8804 | 6.2874 | 5.6754 | 0.019977 | 26.5925 | 0.26699
2025-05-19 18:52 | 1029 | Remove | 2025-05-19 | 18:52 | ST | GS | - | 65.5 | g | 0 | 112.7 | 11.776 | 1171.5 | 60384 | 8:35 | 29.4 | 2.62 m/s | 21.6 | 30.6 | 3.97 m/s | 17.8 |  | 2.62 | m/s |  | 3.97 | m/s | 8.585 | 0.0097625 | 10.0123 |  | -5.5 | 65.5 | 0.0655 | 152.8591 | 6.3462 | 5.5813 | 0.024458 | 26.617 | 0.24608
2025-05-19 18:52 | 1030 | Remove | 2025-05-19 | 18:52 | US | GS | - | 65.5 | g | 0 | 112.5 | 11.754 | 1168.1 | 60393 | 8:36 | 29.4 | 2.52 m/s | 22 | 30.6 | 4.18 m/s | 17.3 |  | 2.52 | m/s |  | 4.18 | m/s | 8.5933 | 0.0097342 | 10.022 |  | 0 | 65.5 | 0.0655 | 153.0077 | 6.4637 | 5.4245 | 0.02396 | 26.6409 | 0.24586
2025-05-19 18:53 | 1031 | Remove | 2025-05-19 | 18:53 | ST | GS | - | 64 | g | 0 | 112.7 | 11.721 | 1164.4 | 60403 | 8:36 | 29.4 | 2.01 m/s | 22.1 | 30.6 | 4.16 m/s | 18.1 |  | 2.01 | m/s |  | 4.16 | m/s | 8.6017 | 0.0097033 | 10.0317 |  | -1.5 | 64 | 0.064 | 156.7454 | 6.4931 | 5.6754 | 0.019198 | 26.6601 | 0.24006
2025-05-19 18:53 | 1032 | Remove | 2025-05-19 | 18:53 | ST | GS | - | 65 | g | 0 | 112.7 | 11.769 | 1170 | 60413 | 8:37 | 29.4 | 2.11 m/s | 23 | 30.6 | 4.04 m/s | 17.9 |  | 2.11 | m/s |  | 4.04 | m/s | 8.6103 | 0.00975 | 10.0415 |  | 1 | 65 | 0.065 | 154.484 | 6.7575 | 5.6127 | 0.020973 | 26.6811 | 0.24362
2025-05-19 18:54 | 1033 | Remove | 2025-05-19 | 18:54 | US | GS | - | 69 | g | 0 | 112.6 | 11.755 | 1168.4 | 60423 | 8:37 | 29.3 | 2.27 m/s | 22.2 | 30.6 | 3.93 m/s | 17.5 |  | 2.27 | m/s |  | 3.93 | m/s | 8.6186 | 0.0097367 | 10.0512 |  | 4 | 69 | 0.069 | 145.6695 | 6.487 | 5.4872 | 0.021661 | 26.7028 | 0.2584
2025-05-19 18:54 | 1034 | Remove | 2025-05-19 | 18:54 | ST | GS | - | 67 | g | 0 | 112.6 | 11.751 | 1167.5 | 60433 | 8:38 | 29.3 | 2.12 m/s | 22 | 30.6 | 4.0 m/s | 17.9 |  | 2.12 | m/s |  | 4 | m/s | 8.6269 | 0.0097292 | 10.0609 |  | -2 | 67 | 0.067 | 150.163 | 6.4286 | 5.6127 | 0.020047 | 26.7228 | 0.25072
2025-05-19 18:55 | 1035 | Remove | 2025-05-19 | 18:55 | ST | GS | - | 66 | g | 0 | 112.6 | 11.735 | 1165.3 | 60442 | 8:38 | 29.3 | 2.08 m/s | 23.2 | 30.6 | 4.06 m/s | 17.7 |  | 2.08 | m/s |  | 4.06 | m/s | 8.6353 | 0.0097108 | 10.0706 |  | -1 | 66 | 0.066 | 152.5854 | 6.7792 | 5.5499 | 0.020742 | 26.7436 | 0.24679
2025-05-19 18:55 | 1036 | Remove | 2025-05-19 | 18:55 | US | GS | - | 71.5 | g | 0 | 112.7 | 11.745 | 1166.8 | 60452 | 8:39 | 29.3 | 2.38 m/s | 23.2 | 30.6 | 4.27 m/s | 17.8 |  | 2.38 | m/s |  | 4.27 | m/s | 8.6436 | 0.0097233 | 10.0804 |  | 5.5 | 71.5 | 0.0715 | 140.984 | 6.7792 | 5.5813 | 0.023733 | 26.7673 | 0.26712
2025-05-19 18:56 | 1037 | Remove | 2025-05-19 | 18:56 | ST | GS | - | 66 | g | 0 | 112.6 | 11.764 | 1168.8 | 60462 | 8:39 | 29.3 | 2.44 m/s | 22.2 | 30.6 | 3.88 m/s | 17.8 |  | 2.44 | m/s |  | 3.88 | m/s | 8.6519 | 0.00974 | 10.0901 |  | -5.5 | 66 | 0.066 | 152.8803 | 6.487 | 5.5813 | 0.023283 | 26.7906 | 0.24636
2025-05-19 18:56 | 1038 | Remove | 2025-05-19 | 18:56 | US | GS | - | 75 | g | 0 | 112.6 | 11.767 | 1169.7 | 60472 | 8:40 | 29.3 | 2.4 m/s | 21.9 | 30.6 | 4.09 m/s | 17.3 |  | 2.4 | m/s |  | 4.09 | m/s | 8.6603 | 0.0097475 | 10.0998 |  | 9 | 75 | 0.075 | 134.6646 | 6.3993 | 5.4245 | 0.022592 | 26.8132 | 0.27971
2025-05-19 18:57 | 1039 | Remove | 2025-05-19 | 18:57 | US | GS | - | 68.5 | g | 0 | 112.6 | 11.767 | 1170 | 60481 | 8:40 | 29.3 | 2.4 m/s | 22.9 | 30.6 | 3.88 m/s | 16.7 |  | 2.4 | m/s |  | 3.88 | m/s | 8.6686 | 0.00975 | 10.1096 |  | -6.5 | 68.5 | 0.0685 | 147.5853 | 6.6915 | 5.2364 | 0.023623 | 26.8368 | 0.25525
2025-05-19 18:57 | 1040 | Remove | 2025-05-19 | 18:57 | ST | GS | - | 66 | g | 0 | 112.7 | 11.755 | 1167.6 | 60491 | 8:41 | 29.3 | 2.38 m/s | 22.3 | 30.6 | 4.09 m/s | 17.7 |  | 2.38 | m/s |  | 4.09 | m/s | 8.6769 | 0.00973 | 10.1193 |  | -2.5 | 66 | 0.066 | 153.3231 | 6.5162 | 5.5499 | 0.022813 | 26.8596 | 0.24572
2025-05-19 18:58 | 1041 | Remove | 2025-05-19 | 18:58 | ST | GS | - | 65 | g | 0 | 112.7 | 11.711 | 1163.2 | 60501 | 8:41 | 29.3 | 2.05 m/s | 22.1 | 30.6 | 4.09 m/s | 19.5 |  | 2.05 | m/s |  | 4.09 | m/s | 8.6853 | 0.0096933 | 10.129 |  | -1 | 65 | 0.065 | 155.8311 | 6.4578 | 6.1143 | 0.019473 | 26.8791 | 0.24182
2025-05-19 18:58 | 1042 | Remove | 2025-05-19 | 18:58 | US | GS | - | 71 | g | 0 | 112.7 | 11.75 | 1168.1 | 60511 | 8:42 | 29.3 | 2.44 m/s | 25.4 | 30.6 | 4.18 m/s | 17.3 |  | 2.44 | m/s |  | 4.18 | m/s | 8.6936 | 0.0097342 | 10.1388 |  | 6 | 71 | 0.071 | 142.7993 | 7.4221 | 5.4245 | 0.026639 | 26.9057 | 0.26388
2025-05-19 18:59 | 1043 | Remove | 2025-05-19 | 18:59 | ST | GS | - | 65 | g | 0 | 112.7 | 11.783 | 1172 | 60520 | 8:42 | 29.3 | 2.22 m/s | 22 | 30.6 | 3.94 m/s | 17.3 |  | 2.22 | m/s |  | 3.94 | m/s | 8.7019 | 0.0097667 | 10.1485 |  | -6 | 65 | 0.065 | 156.1311 | 6.4286 | 5.4245 | 0.020993 | 26.9267 | 0.2414
2025-05-19 18:59 | 1044 | Remove | 2025-05-19 | 18:59 | ST | GS | - | 65 | g | 0 | 112.7 | 11.749 | 1167.7 | 60530 | 8:43 | 29.3 | 2.34 m/s | 22 | 30.6 | 4.0 m/s | 16.4 |  | 2.34 | m/s |  | 4 | m/s | 8.7103 | 0.0097308 | 10.1583 |  | 0 | 65 | 0.065 | 156.2808 | 6.4286 | 5.1423 | 0.022127 | 26.9488 | 0.2412
2025-05-19 19:00 | 1045 | Remove | 2025-05-19 | 19:00 | ST | GS | - | 65.5 | g | 0 | 112.8 | 11.72 | 1164.8 | 60540 | 8:43 | 29.3 | 2.26 m/s | 23 | 30.6 | 4.04 m/s | 20 |  | 2.26 | m/s |  | 4.04 | m/s | 8.7186 | 0.0097067 | 10.168 |  | 0.5 | 65.5 | 0.0655 | 155.236 | 6.7208 | 6.2711 | 0.022342 | 26.9712 | 0.24285
2025-05-19 19:00 | 1046 | Remove | 2025-05-19 | 19:00 | US | GS | - | 65.5 | g | 0 | 112.6 | 11.742 | 1166.7 | 60550 | 8:44 | 29.3 | 2.41 m/s | 26 | 30.6 | 4.15 m/s | 18.2 |  | 2.41 | m/s |  | 4.15 | m/s | 8.7269 | 0.0097225 | 10.1777 |  | 0 | 65.5 | 0.0655 | 155.3844 | 7.5974 | 5.7067 | 0.026933 | 26.9981 | 0.24261
2025-05-19 19:01 | 1047 | Remove | 2025-05-19 | 19:01 | ST | GS | - | 65.5 | g | 0 | 112.5 | 11.776 | 1171.2 | 60559 | 8:44 | 29.3 | 2.45 m/s | 23.6 | 30.6 | 3.88 m/s | 17.2 |  | 2.45 | m/s |  | 3.88 | m/s | 8.7353 | 0.00976 | 10.1874 |  | 0 | 65.5 | 0.0655 | 155.5334 | 6.8961 | 5.3932 | 0.024853 | 27.023 | 0.24239
2025-05-19 19:01 | 1048 | Remove | 2025-05-19 | 19:01 | ST | GS | - | 72 | g | 0 | 112.6 | 11.759 | 1169.1 | 60569 | 8:45 | 29.3 | 2.22 m/s | 22 | 30.6 | 3.79 m/s | 17.3 |  | 2.22 | m/s |  | 3.79 | m/s | 8.7436 | 0.0097425 | 10.1972 |  | 6.5 | 72 | 0.072 | 141.6275 | 6.4286 | 5.4245 | 0.020993 | 27.044 | 0.26623
2025-05-19 19:02 | 1049 | Remove | 2025-05-19 | 19:02 | US | GS | - | 72 | g | 0 | 112.5 | 11.776 | 1170.8 | 60579 | 8:45 | 29.3 | 2.09 m/s | 22.5 | 30.6 | 3.8 m/s | 16.8 |  | 2.09 | m/s |  | 3.8 | m/s | 8.7522 | 0.0097567 | 10.2069 |  | 0 | 72 | 0.072 | 141.763 | 6.5747 | 5.2677 | 0.020213 | 27.0642 | 0.26603
2025-05-19 19:02 | 1050 | Remove | 2025-05-19 | 19:02 | ST | GS | - | 65 | g | 0 | 112.5 | 11.773 | 1170.1 | 60589 | 8:46 | 29.3 | 2.31 m/s | 21.6 | 30.6 | 4.1 m/s | 17.3 |  | 2.31 | m/s |  | 4.1 | m/s | 8.7606 | 0.0097508 | 10.2167 |  | -7 | 65 | 0.065 | 157.1798 | 6.3117 | 5.4245 | 0.021447 | 27.0856 | 0.23998
2025-05-19 19:03 | 1051 | Keep | 2025-05-19 | 19:03 | ST | GS | - | 68.5 | g | 0 | 112.5 | 11.779 | 1171.5 | 60599 | 8:46 | 29.4 | 2.4 m/s | 21.8 | 30.6 | 3.96 m/s | 16.5 |  | 2.4 | m/s |  | 3.96 | m/s | 8.7689 | 0.0097625 | 10.2265 |  | 3.5 | 68.5 | 0.0685 | 149.2913 | 6.4049 | 5.1737 | 0.022611 | 27.1082 | 0.25269
2025-05-19 19:03 | 1052 | Remove | 2025-05-19 | 19:03 | US | GS | - | 73 | g | 0 | 112.5 | 11.784 | 1172.4 | 60608 | 8:47 | 29.4 | 2.05 m/s | 21 | 30.6 | 3.88 m/s | 18.2 |  | 2.05 | m/s |  | 3.88 | m/s | 8.7772 | 0.00977 | 10.2362 |  | 4.5 | 73 | 0.073 | 140.2222 | 6.1699 | 5.7067 | 0.018605 | 27.1268 | 0.26911
2025-05-19 19:04 | 1053 | Remove | 2025-05-19 | 19:04 | US | GS | - | 68.5 | g | 0 | 112.6 | 11.775 | 1170.9 | 60618 | 8:47 | 29.4 | 2.11 m/s | 21.5 | 30.6 | 3.92 m/s | 16.8 |  | 2.11 | m/s |  | 3.92 | m/s | 8.7856 | 0.0097575 | 10.246 |  | -4.5 | 68.5 | 0.0685 | 149.5763 | 6.3168 | 5.2677 | 0.019606 | 27.1464 | 0.25234
2025-05-19 19:04 | 1054 | Remove | 2025-05-19 | 19:04 | ST | GS | - | 66.5 | g | 0 | 112.5 | 11.785 | 1171.8 | 60628 | 8:48 | 29.4 | 2.19 m/s | 20.8 | 30.6 | 4.04 m/s | 16.8 |  | 2.19 | m/s |  | 4.04 | m/s | 8.7939 | 0.009765 | 10.2557 |  | -2 | 66.5 | 0.0665 | 154.2217 | 6.1111 | 5.2677 | 0.019686 | 27.1661 | 0.24479
2025-05-19 19:05 | 1055 | Remove | 2025-05-19 | 19:05 | ST | GS | - | 69 | g | 0 | 112.5 | 11.771 | 1170 | 60638 | 8:48 | 29.4 | 2.51 m/s | 21.5 | 30.6 | 3.94 m/s | 17.4 |  | 2.51 | m/s |  | 3.94 | m/s | 8.8022 | 0.00975 | 10.2655 |  | 2.5 | 69 | 0.069 | 148.7753 | 6.3168 | 5.4559 | 0.023322 | 27.1894 | 0.25377
2025-05-19 19:05 | 1056 | Remove | 2025-05-19 | 19:05 | US | GS | - | 65 | g | 0 | 112.6 | 11.784 | 1172.1 | 60647 | 8:49 | 29.4 | 2.2 m/s | 23.1 | 30.6 | 3.97 m/s | 16.8 |  | 2.2 | m/s |  | 3.97 | m/s | 8.8106 | 0.0097675 | 10.2753 |  | -4 | 65 | 0.065 | 158.0809 | 6.7869 | 5.2677 | 0.021963 | 27.2114 | 0.23887
2025-05-19 19:06 | 1057 | Remove | 2025-05-19 | 19:06 | US | GS | - | 72 | g | 0 | 112.5 | 11.788 | 1172.5 | 60657 | 8:49 | 29.4 | 2.25 m/s | 22.3 | 30.6 | 3.93 m/s | 16.7 |  | 2.25 | m/s |  | 3.93 | m/s | 8.8189 | 0.0097708 | 10.285 |  | 7 | 72 | 0.072 | 142.8477 | 6.5518 | 5.2364 | 0.021684 | 27.2331 | 0.26438
2025-05-19 19:06 | 1058 | Remove | 2025-05-19 | 19:06 | ST | GS | - | 66 | g | 0 | 112.6 | 11.772 | 1170.5 | 60667 | 8:50 | 29.4 | 2.16 m/s | 22.5 | 30.6 | 4.04 m/s | 18.1 |  | 2.16 | m/s |  | 4.04 | m/s | 8.8272 | 0.0097542 | 10.2948 |  | -6 | 66 | 0.066 | 155.9816 | 6.6106 | 5.6754 | 0.021004 | 27.2541 | 0.24217
2025-05-19 19:07 | 1059 | Remove | 2025-05-19 | 19:07 | US | GS | - | 67.5 | g | 0 | 112.6 | 11.749 | 1167 | 60677 | 8:50 | 29.4 | 2.38 m/s | 21.9 | 30.6 | 3.98 m/s | 17.8 |  | 2.38 | m/s |  | 3.98 | m/s | 8.8356 | 0.009725 | 10.3045 |  | 1.5 | 67.5 | 0.0675 | 152.6594 | 6.4343 | 5.5813 | 0.022526 | 27.2766 | 0.24746
2025-05-19 19:07 | 1060 | Remove | 2025-05-19 | 19:07 | ST | GS | - | 67.5 | g | 0 | 112.6 | 11.768 | 1169.5 | 60687 | 8:51 | 29.4 | 2.12 m/s | 21.9 | 30.6 | 4.4 m/s | 17.9 |  | 2.12 | m/s |  | 4.4 | m/s | 8.8439 | 0.0097458 | 10.3143 |  | 0 | 67.5 | 0.0675 | 152.8038 | 6.4343 | 5.6127 | 0.020065 | 27.2967 | 0.24728
2025-05-19 19:08 | 1061 | Remove | 2025-05-19 | 19:08 | US | GS | - | 70 | g | 0 | 112.6 | 11.75 | 1168.3 | 60696 | 8:51 | 29.3 | 2.3 m/s | 23.2 | 30.6 | 3.92 m/s | 17.5 |  | 2.3 | m/s |  | 3.92 | m/s | 8.8522 | 0.0097358 | 10.324 |  | 2.5 | 70 | 0.07 | 147.4856 | 6.7792 | 5.4872 | 0.022936 | 27.3196 | 0.25623
2025-05-19 19:08 | 1062 | Remove | 2025-05-19 | 19:08 | US | GS | - | 74 | g | 0 | 112.7 | 11.747 | 1167.7 | 60706 | 8:52 | 29.3 | 2.19 m/s | 22.3 | 30.6 | 3.72 m/s | 18.5 |  | 2.19 | m/s |  | 3.72 | m/s | 8.8606 | 0.0097308 | 10.3337 |  | 4 | 74 | 0.074 | 139.6449 | 6.5162 | 5.8008 | 0.020991 | 27.3406 | 0.27066
2025-05-19 19:09 | 1063 | Remove | 2025-05-19 | 19:09 | ST | GS | - | 69.5 | g | 0 | 112.6 | 11.798 | 1174.1 | 60716 | 8:52 | 29.3 | 2.11 m/s | 22.7 | 30.5 | 3.85 m/s | 16.9 |  | 2.11 | m/s |  | 3.85 | m/s | 8.8689 | 0.0097842 | 10.3435 |  | -4.5 | 69.5 | 0.0695 | 148.8275 | 6.6331 | 5.2706 | 0.020587 | 27.3612 | 0.25401
2025-05-19 19:09 | 1064 | Remove | 2025-05-19 | 19:09 | ST | GS | - | 71.5 | g | 0 | 112.6 | 11.788 | 1172.4 | 60726 | 8:53 | 29.3 | 2.71 m/s | 21.5 | 30.5 | 3.81 m/s | 17.3 |  | 2.71 | m/s |  | 3.81 | m/s | 8.8772 | 0.00977 | 10.3533 |  | 2 | 71.5 | 0.0715 | 144.8011 | 6.2825 | 5.3953 | 0.025044 | 27.3862 | 0.26108
2025-05-19 19:10 | 1065 | Remove | 2025-05-19 | 19:10 | US | GS | - | 67.5 | g | 0 | 112.5 | 11.766 | 1169.7 | 60735 | 8:53 | 29.4 | 2.33 m/s | 21.2 | 30.5 | 3.92 m/s | 18.7 |  | 2.33 | m/s |  | 3.92 | m/s | 8.8856 | 0.0097475 | 10.363 |  | -4 | 67.5 | 0.0675 | 153.5263 | 6.2286 | 5.8319 | 0.021348 | 27.4076 | 0.24628
2025-05-19 19:10 | 1066 | Remove | 2025-05-19 | 19:10 | ST | GS | - | 68.5 | g | 0 | 112.5 | 11.776 | 1171.4 | 60745 | 8:54 | 29.4 | 2.26 m/s | 21.4 | 30.5 | 3.89 m/s | 17 |  | 2.26 | m/s |  | 3.89 | m/s | 8.8939 | 0.0097617 | 10.3728 |  | 1 | 68.5 | 0.0685 | 151.4276 | 6.2874 | 5.3017 | 0.020902 | 27.4285 | 0.24974
2025-05-19 19:11 | 1067 | Remove | 2025-05-19 | 19:11 | ST | GS | - | 67.5 | g | 0 | 112.5 | 11.736 | 1166.4 | 60755 | 8:54 | 29.3 | 2.23 m/s | 21.8 | 30.5 | 4.0 m/s | 17.6 |  | 2.23 | m/s |  | 4 | m/s | 8.9025 | 0.00972 | 10.3825 |  | -1 | 67.5 | 0.0675 | 153.8149 | 6.3701 | 5.4889 | 0.020896 | 27.4494 | 0.24591
2025-05-19 19:11 | 1068 | Remove | 2025-05-19 | 19:11 | US | GS | - | 71.5 | g | 0 | 112.6 | 11.777 | 1171.2 | 60765 | 8:55 | 29.4 | 2.27 m/s | 22.1 | 30.6 | 3.94 m/s | 16 |  | 2.27 | m/s |  | 3.94 | m/s | 8.9108 | 0.00976 | 10.3923 |  | 4 | 71.5 | 0.0715 | 145.3464 | 6.4931 | 5.0169 | 0.021681 | 27.4711 | 0.26027
2025-05-19 19:12 | 1069 | Remove | 2025-05-19 | 19:12 | ST | GS | - | 70 | g | 0 | 112.7 | 11.731 | 1166.3 | 60774 | 8:55 | 29.4 | 2.38 m/s | 22.7 | 30.6 | 3.92 m/s | 17.7 |  | 2.38 | m/s |  | 3.92 | m/s | 8.9192 | 0.0097192 | 10.402 |  | -1.5 | 70 | 0.07 | 148.5998 | 6.6693 | 5.5499 | 0.023349 | 27.4944 | 0.2546
2025-05-19 19:12 | 1070 | Remove | 2025-05-19 | 19:12 | US | GS | - | 69.5 | g | 0 | 112.7 | 11.752 | 1168.6 | 60784 | 8:56 | 29.3 | 2.22 m/s | 23.2 | 30.6 | 4.01 m/s | 17.6 |  | 2.22 | m/s |  | 4.01 | m/s | 8.9275 | 0.0097383 | 10.4117 |  | -0.5 | 69.5 | 0.0695 | 149.809 | 6.7792 | 5.5186 | 0.022138 | 27.5166 | 0.25258
2025-05-19 19:13 | 1071 | Remove | 2025-05-19 | 19:13 | ST | GS | - | 66.5 | g | 0 | 112.7 | 11.772 | 1171.3 | 60794 | 8:56 | 29.3 | 2.38 m/s | 22.1 | 30.6 | 4.0 m/s | 16.2 |  | 2.38 | m/s |  | 4 | m/s | 8.9358 | 0.0097608 | 10.4215 |  | -3 | 66.5 | 0.0665 | 156.7141 | 6.4578 | 5.0796 | 0.022608 | 27.5392 | 0.24147
2025-05-19 19:13 | 1072 | Remove | 2025-05-19 | 19:13 | US | GS | - | 69 | g | 0 | 112.8 | 11.73 | 1165.8 | 60804 | 8:57 | 29.3 | 2.26 m/s | 21.4 | 30.6 | 4.0 m/s | 18 |  | 2.26 | m/s |  | 4 | m/s | 8.9442 | 0.009715 | 10.4312 |  | 2.5 | 69 | 0.069 | 151.1768 | 6.2532 | 5.644 | 0.020788 | 27.56 | 0.25036
2025-05-19 19:14 | 1073 | Remove | 2025-05-19 | 19:14 | ST | GS | - | 68.5 | g | 0 | 112.8 | 11.745 | 1167.1 | 60814 | 8:57 | 29.3 | 2.38 m/s | 21.4 | 30.5 | 4.09 m/s | 16.7 |  | 2.38 | m/s |  | 4.09 | m/s | 8.9525 | 0.0097258 | 10.4409 |  | -0.5 | 68.5 | 0.0685 | 152.4223 | 6.2532 | 5.2082 | 0.021892 | 27.5818 | 0.24835
2025-05-19 19:14 | 1074 | Remove | 2025-05-19 | 19:14 | ST | GS | - | 67.5 | g | 0 | 112.8 | 11.721 | 1164.7 | 60823 | 8:58 | 29.3 | 2.19 m/s | 22.2 | 30.6 | 4.09 m/s | 17.4 |  | 2.19 | m/s |  | 4.09 | m/s | 8.9608 | 0.0097058 | 10.4506 |  | -1 | 67.5 | 0.0675 | 154.8242 | 6.487 | 5.4559 | 0.020897 | 27.6027 | 0.24454
2025-05-19 19:15 | 1075 | Remove | 2025-05-19 | 19:15 | ST | GS | - | 67.5 | g | 0 | 112.7 | 11.723 | 1165 | 60833 | 8:58 | 29.3 | 2.18 m/s | 23.1 | 30.6 | 4.06 m/s | 17.5 |  | 2.18 | m/s |  | 4.06 | m/s | 8.9692 | 0.0097083 | 10.4603 |  | 0 | 67.5 | 0.0675 | 154.968 | 6.75 | 5.4872 | 0.021645 | 27.6244 | 0.24435
2025-05-19 19:15 | 1076 | Remove | 2025-05-19 | 19:15 | ST | GS | - | 71.5 | g | 0 | 112.7 | 11.773 | 1170.8 | 60843 | 8:59 | 29.3 | 2.44 m/s | 21.7 | 30.5 | 3.94 m/s | 16.3 |  | 2.44 | m/s |  | 3.94 | m/s | 8.9775 | 0.0097567 | 10.4701 |  | 4 | 71.5 | 0.0715 | 146.4349 | 6.3409 | 5.0834 | 0.022758 | 27.6472 | 0.25862
2025-05-19 19:16 | 1077 | Remove | 2025-05-19 | 19:16 | ST | GS | - | 69 | g | 0 | 112.7 | 11.766 | 1170.4 | 60853 | 8:59 | 29.3 | 2.37 m/s | 22 | 30.5 | 3.84 m/s | 17.3 |  | 2.37 | m/s |  | 3.84 | m/s | 8.9858 | 0.0097533 | 10.4799 |  | -2.5 | 69 | 0.069 | 151.8819 | 6.4286 | 5.3953 | 0.022411 | 27.6696 | 0.24937
2025-05-19 19:16 | 1078 | Remove | 2025-05-19 | 19:16 | ST | GS | - | 77 | g | 0 | 112.8 | 11.767 | 1170.1 | 60862 | 9:00 | 29.3 | 2.25 m/s | 21.8 | 30.5 | 4.12 m/s | 17.3 |  | 2.25 | m/s |  | 4.12 | m/s | 8.9942 | 0.0097508 | 10.4896 |  | 8 | 77 | 0.077 | 136.2286 | 6.3701 | 5.3953 | 0.021083 | 27.6906 | 0.27807
2025-05-19 19:17 | 1079 | Remove | 2025-05-19 | 19:17 | ST | GS | - | 67.5 | g | 0 | 112.8 | 11.71 | 1162.9 | 60872 | 9:00 | 29.3 | 2.13 m/s | 21.8 | 30.5 | 4.0 m/s | 19.6 |  | 2.13 | m/s |  | 4 | m/s | 9.0025 | 0.0096908 | 10.4993 |  | -9.5 | 67.5 | 0.0675 | 155.5451 | 6.3701 | 6.1126 | 0.019959 | 27.7106 | 0.24359
2025-05-19 19:17 | 1080 | Remove | 2025-05-19 | 19:17 | ST | GS | - | 76 | g | 0 | 112.6 | 11.74 | 1166.2 | 60882 | 9:01 | 29.3 | 2.94 m/s | 24.1 | 30.5 | 4.03 m/s | 17.1 |  | 2.94 | m/s |  | 4.03 | m/s | 9.0108 | 0.0097183 | 10.509 |  | 8.5 | 76 | 0.076 | 138.2765 | 7.0422 | 5.3329 | 0.030455 | 27.7411 | 0.27396
2025-05-19 19:18 | 1081 | Keep | 2025-05-19 | 19:18 | US | GS | - | 72.5 | g | 0 | 112.8 | 11.716 | 1163.4 | 60892 | 9:01 | 29.3 | 2.27 m/s | 24 | 30.5 | 4.23 m/s | 17.7 |  | 2.27 | m/s |  | 4.23 | m/s | 9.0192 | 0.009695 | 10.5187 |  | -3.5 | 72.5 | 0.0725 | 145.0856 | 7.013 | 5.5201 | 0.023417 | 27.7645 | 0.26113
2025-05-19 19:18 | 1082 | Remove | 2025-05-19 | 19:18 | ST | GS | - | 74 | g | 0 | 112.7 | 11.719 | 1163.8 | 60901 | 9:02 | 29.3 | 2.34 m/s | 23 | 30.5 | 4.29 m/s | 17.3 |  | 2.34 | m/s |  | 4.29 | m/s | 9.0275 | 0.0096983 | 10.5284 |  | 1.5 | 74 | 0.074 | 142.2757 | 6.7208 | 5.3953 | 0.023133 | 27.7876 | 0.26631
2025-05-19 19:19 | 1083 | Remove | 2025-05-19 | 19:19 | US | GS | - | 70 | g | 0 | 112.8 | 11.751 | 1167.5 | 60911 | 9:02 | 29.3 | 2.44 m/s | 22.7 | 30.5 | 3.81 m/s | 16.9 |  | 2.44 | m/s |  | 3.81 | m/s | 9.0358 | 0.0097292 | 10.5381 |  | -4 | 70 | 0.07 | 150.5448 | 6.6331 | 5.2706 | 0.023807 | 27.8114 | 0.2517
2025-05-19 19:19 | 1084 | Remove | 2025-05-19 | 19:19 | ST | GS | - | 71.5 | g | 0 | 112.8 | 11.722 | 1164.4 | 60921 | 9:03 | 29.3 | 2.55 m/s | 22.8 | 30.5 | 3.9 m/s | 19.6 |  | 2.55 | m/s |  | 3.9 | m/s | 9.0444 | 0.0097033 | 10.5478 |  | 1.5 | 71.5 | 0.0715 | 147.5222 | 6.6623 | 6.1126 | 0.02499 | 27.8364 | 0.25686
2025-05-19 19:20 | 1085 | Remove | 2025-05-19 | 19:20 | ST | GS | - | 72 | g | 0 | 112.8 | 11.735 | 1166.4 | 60931 | 9:03 | 29.3 | 2.45 m/s | 22.3 | 30.5 | 4.1 m/s | 16.9 |  | 2.45 | m/s |  | 4.1 | m/s | 9.0528 | 0.00972 | 10.5576 |  | 0.5 | 72 | 0.072 | 146.6327 | 6.5162 | 5.2706 | 0.023484 | 27.8599 | 0.25844
2025-05-19 19:20 | 1086 | Remove | 2025-05-19 | 19:20 | US | GS | - | 70.5 | g | 0 | 112.7 | 11.739 | 1166.2 | 60940 | 9:04 | 29.3 | 2.2 m/s | 22.5 | 30.5 | 3.94 m/s | 18.2 |  | 2.2 | m/s |  | 3.94 | m/s | 9.0611 | 0.0097183 | 10.5673 |  | -1.5 | 70.5 | 0.0705 | 149.8904 | 6.5747 | 5.676 | 0.021276 | 27.8812 | 0.25286
2025-05-19 19:21 | 1087 | Remove | 2025-05-19 | 19:21 | ST | GS | - | 71.5 | g | 0 | 112.9 | 11.717 | 1164.1 | 60950 | 9:04 | 29.3 | 2.2 m/s | 24.5 | 30.5 | 3.9 m/s | 19.7 |  | 2.2 | m/s |  | 3.9 | m/s | 9.0694 | 0.0097008 | 10.577 |  | 1 | 71.5 | 0.0715 | 147.9297 | 7.1591 | 6.1438 | 0.023168 | 27.9043 | 0.25623
2025-05-19 19:21 | 1088 | Remove | 2025-05-19 | 19:21 | US | GS | - | 71 | g | 0 | 112.8 | 11.743 | 1166.6 | 60960 | 9:05 | 29.3 | 2.5 m/s | 25 | 30.5 | 3.76 m/s | 18.7 |  | 2.5 | m/s |  | 3.76 | m/s | 9.0778 | 0.0097217 | 10.5867 |  | -0.5 | 71 | 0.071 | 149.1084 | 7.3052 | 5.8319 | 0.026864 | 27.9312 | 0.2542
2025-05-19 19:22 | 1089 | Remove | 2025-05-19 | 19:22 | ST | GS | - | 69 | g | 0 | 112.7 | 11.773 | 1170.4 | 60970 | 9:05 | 29.3 | 2.34 m/s | 22.1 | 30.5 | 3.88 m/s | 17 |  | 2.34 | m/s |  | 3.88 | m/s | 9.0861 | 0.0097533 | 10.5965 |  | -2 | 69 | 0.069 | 153.5718 | 6.4578 | 5.3017 | 0.022228 | 27.9534 | 0.24684
2025-05-19 19:22 | 1090 | Remove | 2025-05-19 | 19:22 | US | GS | - | 68 | g | 0 | 112.8 | 11.725 | 1164.8 | 60979 | 9:06 | 29.3 | 2.31 m/s | 21.3 | 30.5 | 4.13 m/s | 17.5 |  | 2.31 | m/s |  | 4.13 | m/s | 9.0944 | 0.0097067 | 10.6062 |  | -1 | 68 | 0.068 | 155.9729 | 6.224 | 5.4577 | 0.021149 | 27.9746 | 0.24308
2025-05-19 19:23 | 1091 | Remove | 2025-05-19 | 19:23 | ST | GS | - | 68 | g | 0 | 112.8 | 11.721 | 1164.4 | 60989 | 9:06 | 29.3 | 2.2 m/s | 23.4 | 30.5 | 3.88 m/s | 18.5 |  | 2.2 | m/s |  | 3.88 | m/s | 9.1028 | 0.0097033 | 10.6159 |  | 0 | 68 | 0.068 | 156.1156 | 6.8376 | 5.7695 | 0.022127 | 27.9967 | 0.24289
2025-05-19 19:23 | 1092 | Remove | 2025-05-19 | 19:23 | ST | GS | - | 73 | g | 0 | 112.9 | 11.742 | 1166.9 | 60999 | 9:07 | 29.3 | 2.25 m/s | 23.9 | 30.5 | 4.12 m/s | 18 |  | 2.25 | m/s |  | 4.12 | m/s | 9.1111 | 0.0097242 | 10.6256 |  | 5 | 73 | 0.073 | 145.556 | 6.9837 | 5.6136 | 0.023114 | 28.0198 | 0.26053
2025-05-19 19:24 | 1093 | Remove | 2025-05-19 | 19:24 | US | GS | - | 74.5 | g | 0 | 112.8 | 11.729 | 1165.3 | 61009 | 9:07 | 29.3 | 2.74 m/s | 23.2 | 30.5 | 4.13 m/s | 17.8 |  | 2.74 | m/s |  | 4.13 | m/s | 9.1194 | 0.0097108 | 10.6353 |  | 1.5 | 74.5 | 0.0745 | 142.7556 | 6.7792 | 5.5512 | 0.027323 | 28.0471 | 0.26562
2025-05-19 19:24 | 1094 | Remove | 2025-05-19 | 19:24 | US | GS | - | 68.5 | g | 0 | 112.8 | 11.709 | 1163.2 | 61018 | 9:08 | 29.3 | 2.19 m/s | 23.7 | 30.5 | 4.06 m/s | 18.2 |  | 2.19 | m/s |  | 4.06 | m/s | 9.1278 | 0.0096933 | 10.645 |  | -6 | 68.5 | 0.0685 | 155.4013 | 6.9253 | 5.676 | 0.022309 | 28.0694 | 0.24404
2025-05-19 19:25 | 1095 | Remove | 2025-05-19 | 19:25 | ST | GS | - | 73 | g | 0 | 112.8 | 11.741 | 1166.7 | 61028 | 9:08 | 29.3 | 2.38 m/s | 22.2 | 30.5 | 4.09 m/s | 18.1 |  | 2.38 | m/s |  | 4.09 | m/s | 9.1361 | 0.0097225 | 10.6547 |  | 4.5 | 73 | 0.073 | 145.955 | 6.487 | 5.6448 | 0.02271 | 28.0922 | 0.25986
2025-05-19 19:25 | 1096 | Remove | 2025-05-19 | 19:25 | ST | GS | - | 68.5 | g | 0 | 112.8 | 11.726 | 1164.8 | 61038 | 9:09 | 29.3 | 2.47 m/s | 22.5 | 30.5 | 4.16 m/s | 17.6 |  | 2.47 | m/s |  | 4.16 | m/s | 9.1444 | 0.0097067 | 10.6644 |  | -4.5 | 68.5 | 0.0685 | 155.6849 | 6.5747 | 5.4889 | 0.023888 | 28.116 | 0.24363
2025-05-19 19:26 | 1097 | Remove | 2025-05-19 | 19:26 | ST | GS | - | 70 | g | 0 | 112.8 | 11.729 | 1165.2 | 61048 | 9:09 | 29.3 | 2.35 m/s | 21.9 | 30.5 | 4.07 m/s | 18.6 |  | 2.35 | m/s |  | 4.07 | m/s | 9.1528 | 0.00971 | 10.6741 |  | 1.5 | 70 | 0.07 | 152.4875 | 6.3993 | 5.8007 | 0.022121 | 28.1382 | 0.24877
2025-05-19 19:26 | 1098 | Remove | 2025-05-19 | 19:26 | ST | GS | - | 70.5 | g | 0 | 112.8 | 11.762 | 1169.3 | 61057 | 9:10 | 29.3 | 2.34 m/s | 21.9 | 30.5 | 3.85 m/s | 17.1 |  | 2.34 | m/s |  | 3.85 | m/s | 9.1611 | 0.0097442 | 10.6839 |  | 0.5 | 70.5 | 0.0705 | 151.5443 | 6.3993 | 5.3329 | 0.022027 | 28.1602 | 0.25035
2025-05-19 19:27 | 1099 | Remove | 2025-05-19 | 19:27 | ST | GS | - | 70.5 | g | 0 | 112.9 | 11.733 | 1165.8 | 61067 | 9:10 | 29.3 | 2.05 m/s | 25.1 | 30.5 | 3.89 m/s | 18.3 |  | 2.05 | m/s |  | 3.89 | m/s | 9.1694 | 0.009715 | 10.6936 |  | 0 | 70.5 | 0.0705 | 151.6821 | 7.3344 | 5.7072 | 0.022117 | 28.1823 | 0.25016
2025-05-19 19:27 | 1100 | Remove | 2025-05-19 | 19:27 | US | GS | - | 71 | g | 0 | 112.9 | 11.712 | 1163.6 | 61077 | 9:11 | 29.3 | 2.06 m/s | 24.5 | 30.5 | 3.79 m/s | 18.8 |  | 2.06 | m/s |  | 3.79 | m/s | 9.1778 | 0.0096967 | 10.7033 |  | 0.5 | 71 | 0.071 | 150.7505 | 7.1591 | 5.8631 | 0.021693 | 28.204 | 0.25174
2025-05-19 19:28 | 1101 | Remove | 2025-05-19 | 19:28 | ST | GS | - | 72 | g | 0 | 112.9 | 11.73 | 1165.5 | 61087 | 9:11 | 29.3 | 2.31 m/s | 21.9 | 30.5 | 3.81 m/s | 18.2 |  | 2.31 | m/s |  | 3.81 | m/s | 9.1864 | 0.0097125 | 10.713 |  | 1 | 72 | 0.072 | 148.7916 | 6.3993 | 5.676 | 0.021744 | 28.2257 | 0.25509
2025-05-19 19:28 | 1102 | Remove | 2025-05-19 | 19:28 | ST | GS | - | 71.5 | g | 0 | 112.9 | 11.736 | 1166.8 | 61096 | 9:12 | 29.3 | 2.19 m/s | 22.2 | 30.5 | 3.88 m/s | 18.4 |  | 2.19 | m/s |  | 3.88 | m/s | 9.1947 | 0.0097233 | 10.7227 |  | -0.5 | 71.5 | 0.0715 | 149.9681 | 6.487 | 5.7384 | 0.020897 | 28.2466 | 0.25313
2025-05-19 19:29 | 1103 | Remove | 2025-05-19 | 19:29 | ST | GS | - | 69 | g | 0 | 113 | 11.7 | 1162.3 | 61106 | 9:12 | 29.3 | 2.27 m/s | 22.2 | 30.5 | 4.15 m/s | 17.6 |  | 2.27 | m/s |  | 4.15 | m/s | 9.2031 | 0.0096858 | 10.7324 |  | -2.5 | 69 | 0.069 | 155.5421 | 6.487 | 5.4889 | 0.021661 | 28.2683 | 0.24409
2025-05-19 19:29 | 1104 | Remove | 2025-05-19 | 19:29 | ST | GS | - | 72 | g | 0 | 112.9 | 11.704 | 1162.6 | 61116 | 9:13 | 29.3 | 2.04 m/s | 23 | 30.5 | 3.9 m/s | 18.2 |  | 2.04 | m/s |  | 3.9 | m/s | 9.2114 | 0.0096883 | 10.7421 |  | 3 | 72 | 0.072 | 149.1958 | 6.7208 | 5.676 | 0.020167 | 28.2885 | 0.25452
2025-05-19 19:30 | 1105 | Remove | 2025-05-19 | 19:30 | ST | GS | - | 69.5 | g | 0 | 112.9 | 11.749 | 1168.3 | 61125 | 9:13 | 29.3 | 2.04 m/s | 22.5 | 30.5 | 3.85 m/s | 16.4 |  | 2.04 | m/s |  | 3.85 | m/s | 9.2197 | 0.0097358 | 10.7518 |  | -2.5 | 69.5 | 0.0695 | 154.7026 | 6.5747 | 5.1146 | 0.019729 | 28.3082 | 0.24551
2025-05-19 19:30 | 1106 | Remove | 2025-05-19 | 19:30 | ST | GS | - | 72.5 | g | 0 | 113 | 11.727 | 1165.4 | 61135 | 9:14 | 29.3 | 2.42 m/s | 21.2 | 30.5 | 4.13 m/s | 17.9 |  | 2.42 | m/s |  | 4.13 | m/s | 9.2281 | 0.0097117 | 10.7615 |  | 3 | 72.5 | 0.0725 | 148.4351 | 6.1948 | 5.5824 | 0.022052 | 28.3303 | 0.25591
2025-05-19 19:31 | 1107 | Remove | 2025-05-19 | 19:31 | ST | GS | - | 69.5 | g | 0 | 113 | 11.705 | 1163 | 61145 | 9:14 | 29.3 | 2.15 m/s | 22.9 | 30.5 | 3.96 m/s | 17.7 |  | 2.15 | m/s |  | 3.96 | m/s | 9.2364 | 0.0096917 | 10.7712 |  | -3 | 69.5 | 0.0695 | 154.9818 | 6.6915 | 5.5201 | 0.021162 | 28.3514 | 0.24514
2025-05-19 19:31 | 1108 | Remove | 2025-05-19 | 19:31 | US | GS | - | 72.5 | g | 0 | 113 | 11.725 | 1164.9 | 61155 | 9:15 | 29.3 | 2.26 m/s | 22 | 30.5 | 3.93 m/s | 18.5 |  | 2.26 | m/s |  | 3.93 | m/s | 9.2447 | 0.0097075 | 10.7809 |  | 3 | 72.5 | 0.0725 | 148.7026 | 6.4286 | 5.7695 | 0.021371 | 28.3728 | 0.25553
2025-05-19 19:32 | 1109 | Remove | 2025-05-19 | 19:32 | ST | GS | - | 71 | g | 0 | 113 | 11.727 | 1165.8 | 61164 | 9:15 | 29.3 | 2.3 m/s | 21.8 | 30.5 | 3.89 m/s | 17.8 |  | 2.3 | m/s |  | 3.89 | m/s | 9.2531 | 0.009715 | 10.7907 |  | -1.5 | 71 | 0.071 | 151.9811 | 6.3701 | 5.5512 | 0.021551 | 28.3943 | 0.25005
2025-05-19 19:32 | 1110 | Remove | 2025-05-19 | 19:32 | US | GS | - | 70.5 | g | 0 | 113 | 11.754 | 1168.4 | 61174 | 9:16 | 29.3 | 2.4 m/s | 20.9 | 30.5 | 4.06 m/s | 17.6 |  | 2.4 | m/s |  | 4.06 | m/s | 9.2614 | 0.0097367 | 10.8004 |  | -0.5 | 70.5 | 0.0705 | 153.1971 | 6.1071 | 5.4889 | 0.02156 | 28.4159 | 0.2481
2025-05-19 19:33 | 1111 | Keep | 2025-05-19 | 19:33 | US | GS | - | 72 | g | 0 | 113.1 | 11.726 | 1165.9 | 61184 | 9:16 | 29.3 | 2.64 m/s | 21.9 | 30.5 | 4.15 m/s | 17.3 |  | 2.64 | m/s |  | 4.15 | m/s | 9.2697 | 0.0097158 | 10.8101 |  | 1.5 | 72 | 0.072 | 150.1404 | 6.3993 | 5.3953 | 0.024851 | 28.4408 | 0.25316
2025-05-19 19:33 | 1112 | Remove | 2025-05-19 | 19:33 | ST | GS | - | 70 | g | 0 | 113.1 | 11.746 | 1168.9 | 61194 | 9:17 | 29.3 | 2.54 m/s | 22.1 | 30.5 | 4.01 m/s | 16.7 |  | 2.54 | m/s |  | 4.01 | m/s | 9.2781 | 0.0097408 | 10.8198 |  | -2 | 70 | 0.07 | 154.5693 | 6.4578 | 5.2082 | 0.024128 | 28.4649 | 0.24592
2025-05-19 19:34 | 1113 | Remove | 2025-05-19 | 19:34 | US | GS | - | 70 | g | 0 | 113.1 | 11.71 | 1164.2 | 61203 | 9:17 | 29.3 | 2.13 m/s | 22.8 | 30.5 | 4.04 m/s | 17.1 |  | 2.13 | m/s |  | 4.04 | m/s | 9.2864 | 0.0097017 | 10.8296 |  | 0 | 70 | 0.07 | 154.7079 | 6.6623 | 5.3329 | 0.020874 | 28.4858 | 0.24574
2025-05-19 19:34 | 1114 | Remove | 2025-05-19 | 19:34 | US | GS | - | 86 | g | 0 | 113 | 11.747 | 1167.8 | 61213 | 9:18 | 29.3 | 2.31 m/s | 21.2 | 30.5 | 3.73 m/s | 17.6 |  | 2.31 | m/s |  | 3.73 | m/s | 9.2947 | 0.0097317 | 10.8393 |  | 16 | 86 | 0.086 | 126.0382 | 6.1948 | 5.4889 | 0.021049 | 28.5068 | 0.30168
2025-05-19 19:35 | 1115 | Remove | 2025-05-19 | 19:35 | US | GS | - | 74.5 | g | 0 | 113 | 11.747 | 1168.4 | 61223 | 9:18 | 29.3 | 2.12 m/s | 21.4 | 30.5 | 3.94 m/s | 16.5 |  | 2.12 | m/s |  | 3.94 | m/s | 9.3031 | 0.0097367 | 10.849 |  | -11.5 | 74.5 | 0.0745 | 145.6244 | 6.2532 | 5.1458 | 0.0195 | 28.5263 | 0.26116
2025-05-19 19:35 | 1116 | Remove | 2025-05-19 | 19:35 | ST | GS | - | 73 | g | 0 | 113 | 11.732 | 1166.2 | 61233 | 9:19 | 29.3 | 2.41 m/s | 22.5 | 30.5 | 4.09 m/s | 17.1 |  | 2.41 | m/s |  | 4.09 | m/s | 9.3114 | 0.0097183 | 10.8587 |  | -1.5 | 73 | 0.073 | 148.7498 | 6.5747 | 5.3329 | 0.023307 | 28.5496 | 0.2557
2025-05-19 19:36 | 1117 | Remove | 2025-05-19 | 19:36 | US | GS | - | 71 | g | 0 | 113 | 11.713 | 1164.6 | 61242 | 9:19 | 29.3 | 2.31 m/s | 23.4 | 30.5 | 4.09 m/s | 17.8 |  | 2.31 | m/s |  | 4.09 | m/s | 9.3197 | 0.009705 | 10.8684 |  | -2 | 71 | 0.071 | 153.0767 | 6.8376 | 5.5512 | 0.023234 | 28.5728 | 0.24849
2025-05-19 19:36 | 1118 | Remove | 2025-05-19 | 19:36 | ST | GS | - | 71 | g | 0 | 113 | 11.714 | 1164.7 | 61252 | 9:20 | 29.3 | 2.55 m/s | 22.6 | 30.5 | 4.13 m/s | 18.4 |  | 2.55 | m/s |  | 4.13 | m/s | 9.3283 | 0.0097058 | 10.8781 |  | 0 | 71 | 0.071 | 153.2134 | 6.6039 | 5.7384 | 0.024771 | 28.5976 | 0.24827
2025-05-19 19:37 | 1119 | Remove | 2025-05-19 | 19:37 | ST | GS | - | 71 | g | 0 | 113.1 | 11.687 | 1161.3 | 61262 | 9:20 | 29.3 | 2.13 m/s | 23.6 | 30.5 | 4.13 m/s | 19.6 |  | 2.13 | m/s |  | 4.13 | m/s | 9.3367 | 0.0096775 | 10.8878 |  | 0 | 71 | 0.071 | 153.3497 | 6.8961 | 6.1126 | 0.021607 | 28.6192 | 0.24809
2025-05-19 19:37 | 1120 | Remove | 2025-05-19 | 19:37 | US | GS | - | 70.5 | g | 0 | 113.1 | 11.669 | 1158.9 | 61272 | 9:21 | 29.3 | 2.09 m/s | 26.5 | 30.5 | 4.07 m/s | 21.2 |  | 2.09 | m/s |  | 4.07 | m/s | 9.345 | 0.0096575 | 10.8975 |  | -0.5 | 70.5 | 0.0705 | 154.5742 | 7.7435 | 6.6116 | 0.023806 | 28.643 | 0.24613
2025-05-19 19:38 | 1121 | Remove | 2025-05-19 | 19:38 | ST | GS | - | 70 | g | 0 | 113.1 | 11.704 | 1162.5 | 61281 | 9:21 | 29.3 | 2.74 m/s | 23.7 | 30.5 | 3.92 m/s | 18.4 |  | 2.74 | m/s |  | 3.92 | m/s | 9.3533 | 0.0096875 | 10.9072 |  | -0.5 | 70 | 0.07 | 155.8167 | 6.9253 | 5.7384 | 0.027912 | 28.6709 | 0.24415
2025-05-19 19:38 | 1122 | Remove | 2025-05-19 | 19:38 | ST | GS | - | 72 | g | 0 | 112.9 | 11.698 | 1161.8 | 61291 | 9:22 | 29.3 | 2.26 m/s | 22.5 | 30.5 | 4.36 m/s | 18.5 |  | 2.26 | m/s |  | 4.36 | m/s | 9.3617 | 0.0096817 | 10.9169 |  | 2 | 72 | 0.072 | 151.623 | 6.5747 | 5.7695 | 0.021857 | 28.6928 | 0.25093
2025-05-19 19:39 | 1123 | Remove | 2025-05-19 | 19:39 | ST | GS | - | 71 | g | 0 | 113.1 | 11.682 | 1160.4 | 61301 | 9:22 | 29.3 | 2.35 m/s | 24.7 | 30.5 | 3.96 m/s | 17.9 |  | 2.35 | m/s |  | 3.96 | m/s | 9.37 | 0.00967 | 10.9265 |  | -1 | 71 | 0.071 | 153.8947 | 7.2175 | 5.5824 | 0.024949 | 28.7177 | 0.24723
2025-05-19 19:39 | 1124 | Remove | 2025-05-19 | 19:39 | ST | GS | - | 71.5 | g | 0 | 113 | 11.694 | 1161.2 | 61310 | 9:23 | 29.3 | 2.23 m/s | 23.4 | 30.5 | 3.94 m/s | 18.8 |  | 2.23 | m/s |  | 3.94 | m/s | 9.3783 | 0.0096767 | 10.9362 |  | 0.5 | 71.5 | 0.0715 | 152.9538 | 6.8376 | 5.8631 | 0.022429 | 28.7402 | 0.24878
2025-05-19 19:40 | 1125 | Remove | 2025-05-19 | 19:40 | US | GS | - | 71.5 | g | 0 | 113 | 11.738 | 1167.2 | 61320 | 9:23 | 29.3 | 2.26 m/s | 22.2 | 30.5 | 3.9 m/s | 17.1 |  | 2.26 | m/s |  | 3.9 | m/s | 9.3867 | 0.0097267 | 10.9459 |  | 0 | 71.5 | 0.0715 | 153.0899 | 6.487 | 5.3329 | 0.021565 | 28.7617 | 0.24859
2025-05-19 19:40 | 1126 | Remove | 2025-05-19 | 19:40 | ST | GS | - | 69 | g | 0 | 113 | 11.717 | 1164 | 61330 | 9:24 | 29.3 | 2.06 m/s | 23 | 30.5 | 3.97 m/s | 17.1 |  | 2.06 | m/s |  | 3.97 | m/s | 9.395 | 0.0097 | 10.9556 |  | -2.5 | 69 | 0.069 | 158.7772 | 6.7208 | 5.3329 | 0.020365 | 28.7821 | 0.23973
2025-05-19 19:41 | 1127 | Remove | 2025-05-19 | 19:41 | US | GS | - | 71.5 | g | 0 | 112.9 | 11.731 | 1166.4 | 61340 | 9:24 | 29.3 | 2.11 m/s | 21.8 | 30.5 | 4.06 m/s | 17.1 |  | 2.11 | m/s |  | 4.06 | m/s | 9.4033 | 0.00972 | 10.9653 |  | 2.5 | 71.5 | 0.0715 | 153.3615 | 6.3701 | 5.3329 | 0.019771 | 28.8019 | 0.24825
2025-05-19 19:41 | 1128 | Remove | 2025-05-19 | 19:41 | ST | GS | - | 75 | g | 0 | 113 | 11.684 | 1160.5 | 61349 | 9:25 | 29.3 | 2.2 m/s | 23.5 | 30.5 | 3.88 m/s | 19.6 |  | 2.2 | m/s |  | 3.88 | m/s | 9.4117 | 0.0096708 | 10.975 |  | 3.5 | 75 | 0.075 | 146.3336 | 6.8669 | 6.1126 | 0.022222 | 28.8241 | 0.2602
2025-05-19 19:42 | 1129 | Remove | 2025-05-19 | 19:42 | ST | GS | - | 70.5 | g | 0 | 113 | 11.705 | 1162.8 | 61359 | 9:25 | 29.3 | 2.44 m/s | 24.1 | 30.5 | 3.88 m/s | 18 |  | 2.44 | m/s |  | 3.88 | m/s | 9.42 | 0.00969 | 10.9847 |  | -4.5 | 70.5 | 0.0705 | 155.8114 | 7.0422 | 5.6136 | 0.025276 | 28.8494 | 0.24437
2025-05-19 19:42 | 1130 | Remove | 2025-05-19 | 19:42 | ST | GS | - | 72 | g | 0 | 112.9 | 11.692 | 1161.3 | 61369 | 9:26 | 29.3 | 2.31 m/s | 23.4 | 30.5 | 4.18 m/s | 17.9 |  | 2.31 | m/s |  | 4.18 | m/s | 9.4283 | 0.0096775 | 10.9944 |  | 1.5 | 72 | 0.072 | 152.6998 | 6.8376 | 5.5824 | 0.023234 | 28.8726 | 0.24937
2025-05-19 19:43 | 1131 | Remove | 2025-05-19 | 19:43 | ST | GS | - | 72.5 | g | 0 | 113.1 | 11.703 | 1163.1 | 61378 | 9:26 | 29.3 | 2.5 m/s | 22.5 | 30.5 | 3.98 m/s | 17.7 |  | 2.5 | m/s |  | 3.98 | m/s | 9.4367 | 0.0096925 | 11.0041 |  | 0.5 | 72.5 | 0.0725 | 151.7804 | 6.5747 | 5.5201 | 0.024178 | 28.8968 | 0.25089
2025-05-19 19:43 | 1132 | Remove | 2025-05-19 | 19:43 | US | GS | - | 71 | g | 0 | 112.9 | 11.708 | 1163 | 61388 | 9:27 | 29.3 | 2.38 m/s | 23.2 | 30.5 | 4.24 m/s | 17.1 |  | 2.38 | m/s |  | 4.24 | m/s | 9.445 | 0.0096917 | 11.0138 |  | -1.5 | 71 | 0.071 | 155.1235 | 6.7792 | 5.3329 | 0.023733 | 28.9205 | 0.2455
2025-05-19 19:44 | 1133 | Remove | 2025-05-19 | 19:44 | ST | GS | - | 71.5 | g | 0 | 113 | 11.689 | 1161.2 | 61398 | 9:27 | 29.3 | 2.12 m/s | 23.7 | 30.5 | 4.03 m/s | 18.4 |  | 2.12 | m/s |  | 4.03 | m/s | 9.4533 | 0.0096767 | 11.0234 |  | 0.5 | 71.5 | 0.0715 | 154.1741 | 6.9253 | 5.7384 | 0.021596 | 28.9421 | 0.24704
2025-05-19 19:44 | 1134 | Remove | 2025-05-19 | 19:44 | US | GS | - | 73 | g | 0 | 113 | 11.684 | 1160.6 | 61408 | 9:28 | 29.3 | 2.42 m/s | 22.6 | 30.5 | 4.21 m/s | 18 |  | 2.42 | m/s |  | 4.21 | m/s | 9.4617 | 0.0096717 | 11.0331 |  | 1.5 | 73 | 0.073 | 151.1386 | 6.6039 | 5.6136 | 0.023508 | 28.9656 | 0.25202
2025-05-19 19:45 | 1135 | Remove | 2025-05-19 | 19:45 | ST | GS | - | 71 | g | 0 | 113.1 | 11.653 | 1156.4 | 61417 | 9:28 | 29.3 | 2.3 m/s | 22.2 | 30.5 | 4.29 m/s | 18.5 |  | 2.3 | m/s |  | 4.29 | m/s | 9.47 | 0.0096367 | 11.0428 |  | -2 | 71 | 0.071 | 155.5317 | 6.487 | 5.7695 | 0.021947 | 28.9876 | 0.24493
2025-05-19 19:45 | 1136 | Remove | 2025-05-19 | 19:45 | ST | GS | - | 79.5 | g | 0 | 113.1 | 11.672 | 1158.7 | 61427 | 9:29 | 29.2 | 2.37 m/s | 23.2 | 30.5 | 4.2 m/s | 18.5 |  | 2.37 | m/s |  | 4.2 | m/s | 9.4786 | 0.0096558 | 11.0524 |  | 8.5 | 79.5 | 0.0795 | 139.024 | 6.7423 | 5.7695 | 0.023505 | 29.0111 | 0.27403
2025-05-19 19:46 | 1137 | Remove | 2025-05-19 | 19:46 | ST | GS | - | 75.5 | g | 0 | 113 | 11.69 | 1161.4 | 61437 | 9:29 | 29.2 | 2.45 m/s | 22.8 | 30.5 | 3.97 m/s | 19.3 |  | 2.45 | m/s |  | 3.97 | m/s | 9.4872 | 0.0096783 | 11.0621 |  | -4 | 75.5 | 0.0755 | 146.5177 | 6.6261 | 6.019 | 0.02388 | 29.035 | 0.26003
2025-05-19 19:46 | 1138 | Remove | 2025-05-19 | 19:46 | ST | GS | - | 74 | g | 0 | 113 | 11.7 | 1162.3 | 61446 | 9:30 | 29.2 | 2.44 m/s | 23.5 | 30.5 | 3.9 m/s | 17.9 |  | 2.44 | m/s |  | 3.9 | m/s | 9.4956 | 0.0096858 | 11.0718 |  | -1.5 | 74 | 0.074 | 149.6186 | 6.8295 | 5.5824 | 0.024512 | 29.0595 | 0.25465
2025-05-19 19:47 | 1139 | Remove | 2025-05-19 | 19:47 | ST | GS | - | 71 | g | 0 | 113 | 11.705 | 1162.3 | 61456 | 9:30 | 29.2 | 2.19 m/s | 23.2 | 30.5 | 4.0 m/s | 17.1 |  | 2.19 | m/s |  | 4 | m/s | 9.5039 | 0.0096858 | 11.0815 |  | -3 | 71 | 0.071 | 156.0769 | 6.7423 | 5.3329 | 0.02172 | 29.0812 | 0.24414
2025-05-19 19:47 | 1140 | Remove | 2025-05-19 | 19:47 | ST | GS | - | 73.5 | g | 0 | 113 | 11.698 | 1162.4 | 61466 | 9:31 | 29.2 | 2.12 m/s | 22.5 | 30.5 | 3.9 m/s | 17.2 |  | 2.12 | m/s |  | 3.9 | m/s | 9.5122 | 0.0096867 | 11.0911 |  | 2.5 | 73.5 | 0.0735 | 150.8999 | 6.5389 | 5.3641 | 0.020391 | 29.1016 | 0.25256
2025-05-19 19:48 | 1141 | Keep | 2025-05-19 | 19:48 | ST | GS | - | 75 | g | 0 | 113.1 | 11.666 | 1158 | 61475 | 9:31 | 29.2 | 2.26 m/s | 22 | 30.5 | 3.8 m/s | 20.1 |  | 2.26 | m/s |  | 3.8 | m/s | 9.5206 | 0.00965 | 11.1008 |  | 1.5 | 75 | 0.075 | 148.0106 | 6.3936 | 6.2685 | 0.021255 | 29.1228 | 0.25753
2025-05-19 19:48 | 1142 | Remove | 2025-05-19 | 19:48 | ST | GS | - | 71.5 | g | 0 | 113.1 | 11.683 | 1160.2 | 61485 | 9:32 | 29.2 | 2.26 m/s | 22.3 | 30.5 | 3.85 m/s | 18.9 |  | 2.26 | m/s |  | 3.85 | m/s | 9.5289 | 0.0096683 | 11.1105 |  | -3.5 | 71.5 | 0.0715 | 155.3911 | 6.4808 | 5.8943 | 0.021545 | 29.1444 | 0.24533
2025-05-19 19:49 | 1143 | Remove | 2025-05-19 | 19:49 | ST | GS | - | 74.5 | g | 0 | 113.1 | 11.701 | 1163 | 61495 | 9:32 | 29.2 | 2.45 m/s | 21.9 | 30.4 | 4.04 m/s | 18 |  | 2.45 | m/s |  | 4.04 | m/s | 9.5372 | 0.0096917 | 11.1202 |  | 3 | 74.5 | 0.0745 | 149.2638 | 6.3645 | 5.5834 | 0.022937 | 29.1673 | 0.25542
2025-05-19 19:49 | 1144 | Remove | 2025-05-19 | 19:49 | US | GS | - | 72.5 | g | 0 | 113.1 | 11.7 | 1162.5 | 61505 | 9:33 | 29.2 | 2.11 m/s | 22.7 | 30.4 | 3.89 m/s | 17.2 |  | 2.11 | m/s |  | 3.89 | m/s | 9.5456 | 0.0096875 | 11.1298 |  | -2 | 72.5 | 0.0725 | 153.5151 | 6.597 | 5.3352 | 0.020475 | 29.1878 | 0.24839
2025-05-19 19:50 | 1145 | Remove | 2025-05-19 | 19:50 | US | GS | - | 75 | g | 0 | 113.1 | 11.709 | 1163.5 | 61514 | 9:33 | 29.2 | 2.23 m/s | 22.1 | 30.4 | 3.89 m/s | 17.8 |  | 2.23 | m/s |  | 3.89 | m/s | 9.5539 | 0.0096958 | 11.1395 |  | 2.5 | 75 | 0.075 | 148.5272 | 6.4227 | 5.5213 | 0.021068 | 29.2089 | 0.25677
2025-05-19 19:50 | 1146 | Remove | 2025-05-19 | 19:50 | ST | GS | - | 72 | g | 0 | 113.1 | 11.708 | 1163.1 | 61524 | 9:34 | 29.2 | 2.38 m/s | 23 | 30.4 | 3.88 m/s | 17.3 |  | 2.38 | m/s |  | 3.88 | m/s | 9.5622 | 0.0096925 | 11.1492 |  | -3 | 72 | 0.072 | 154.8504 | 6.6842 | 5.3662 | 0.023401 | 29.2323 | 0.2463
2025-05-19 19:51 | 1147 | Remove | 2025-05-19 | 19:51 | ST | GS | - | 75 | g | 0 | 113.1 | 11.682 | 1159.7 | 61534 | 9:34 | 29.2 | 2.48 m/s | 22.7 | 30.4 | 4.03 m/s | 18.8 |  | 2.48 | m/s |  | 4.03 | m/s | 9.5706 | 0.0096642 | 11.1589 |  | 3 | 75 | 0.075 | 148.7853 | 6.597 | 5.8315 | 0.024066 | 29.2563 | 0.25635
2025-05-19 19:51 | 1148 | Remove | 2025-05-19 | 19:51 | US | GS | - | 80.5 | g | 0 | 113.1 | 11.671 | 1158.9 | 61543 | 9:35 | 29.2 | 2.45 m/s | 22.6 | 30.4 | 4.09 m/s | 18.6 |  | 2.45 | m/s |  | 4.09 | m/s | 9.5789 | 0.0096575 | 11.1686 |  | 5.5 | 80.5 | 0.0805 | 138.7398 | 6.568 | 5.7695 | 0.02367 | 29.28 | 0.27493
2025-05-19 19:52 | 1149 | Remove | 2025-05-19 | 19:52 | US | GS | - | 72 | g | 0 | 113 | 11.682 | 1159.9 | 61553 | 9:35 | 29.2 | 2.27 m/s | 23.4 | 30.4 | 3.89 m/s | 18.9 |  | 2.27 | m/s |  | 3.89 | m/s | 9.5872 | 0.0096658 | 11.1782 |  | -8.5 | 72 | 0.072 | 155.253 | 6.8005 | 5.8625 | 0.022707 | 29.3027 | 0.24571
2025-05-19 19:52 | 1150 | Remove | 2025-05-19 | 19:52 | US | GS | - | 74.5 | g | 0 | 113.1 | 11.657 | 1157.4 | 61563 | 9:36 | 29.2 | 2.25 m/s | 24.3 | 30.4 | 4.07 m/s | 18.6 |  | 2.25 | m/s |  | 4.07 | m/s | 9.5956 | 0.009645 | 11.1879 |  | 2.5 | 74.5 | 0.0745 | 150.1727 | 7.062 | 5.7695 | 0.023373 | 29.3261 | 0.25404
2025-05-19 19:53 | 1151 | Remove | 2025-05-19 | 19:53 | US | GS | - | 90.5 | g | 0 | 113.1 | 11.69 | 1160.9 | 61572 | 9:36 | 29.2 | 2.37 m/s | 23.7 | 30.4 | 3.86 m/s | 18.5 |  | 2.37 | m/s |  | 3.86 | m/s | 9.6039 | 0.0096742 | 11.1975 |  | 16 | 90.5 | 0.0905 | 123.7297 | 6.8876 | 5.7385 | 0.024012 | 29.3501 | 0.30835
2025-05-19 19:53 | 1152 | Remove | 2025-05-19 | 19:53 | ST | GS | - | 73 | g | 0 | 112.9 | 11.656 | 1156.5 | 61582 | 9:37 | 29.2 | 2.22 m/s | 23.1 | 30.4 | 3.96 m/s | 19.7 |  | 2.22 | m/s |  | 3.96 | m/s | 9.6125 | 0.0096375 | 11.2072 |  | -17.5 | 73 | 0.073 | 153.523 | 6.7133 | 6.1107 | 0.021922 | 29.372 | 0.24854
2025-05-19 19:54 | 1153 | Remove | 2025-05-19 | 19:54 | ST | GS | - | 77.5 | g | 0 | 113 | 11.702 | 1162 | 61592 | 9:37 | 29.2 | 2.23 m/s | 23.2 | 30.4 | 4.03 m/s | 17.3 |  | 2.23 | m/s |  | 4.03 | m/s | 9.6208 | 0.0096833 | 11.2169 |  | 4.5 | 77.5 | 0.0775 | 144.7337 | 6.7423 | 5.3662 | 0.022117 | 29.3941 | 0.26366
2025-05-19 19:54 | 1154 | Remove | 2025-05-19 | 19:54 | US | GS | - | 74 | g | 0 | 112.9 | 11.667 | 1158.1 | 61602 | 9:38 | 29.2 | 2.08 m/s | 24 | 30.4 | 3.89 m/s | 18.7 |  | 2.08 | m/s |  | 3.89 | m/s | 9.6292 | 0.0096508 | 11.2265 |  | -3.5 | 74 | 0.074 | 151.7096 | 6.9748 | 5.8005 | 0.02134 | 29.4155 | 0.25157
2025-05-19 19:55 | 1155 | Remove | 2025-05-19 | 19:55 | ST | GS | - | 73 | g | 0 | 112.7 | 11.68 | 1158.8 | 61611 | 9:38 | 29.2 | 2.35 m/s | 22.5 | 30.4 | 3.92 m/s | 18.4 |  | 2.35 | m/s |  | 3.92 | m/s | 9.6375 | 0.0096567 | 11.2362 |  | -1 | 73 | 0.073 | 153.9201 | 6.5389 | 5.7074 | 0.022603 | 29.4381 | 0.24798
2025-05-19 19:55 | 1156 | Remove | 2025-05-19 | 19:55 | US | GS | - | 81.5 | g | 0 | 112.6 | 11.733 | 1164.8 | 61621 | 9:39 | 29.2 | 2.61 m/s | 22.7 | 30.4 | 3.81 m/s | 17 |  | 2.61 | m/s |  | 3.81 | m/s | 9.6458 | 0.0097067 | 11.2459 |  | 8.5 | 81.5 | 0.0815 | 137.9862 | 6.597 | 5.2732 | 0.025327 | 29.4634 | 0.27661
2025-05-19 19:56 | 1157 | Remove | 2025-05-19 | 19:56 | US | GS | - | 74.5 | g | 0 | 112.7 | 11.698 | 1161 | 61631 | 9:39 | 29.2 | 2.33 m/s | 22 | 30.4 | 4.01 m/s | 19.1 |  | 2.33 | m/s |  | 4.01 | m/s | 9.6542 | 0.009675 | 11.2555 |  | -7 | 74.5 | 0.0745 | 151.0812 | 6.3936 | 5.9246 | 0.021913 | 29.4853 | 0.25267
2025-05-19 19:56 | 1158 | Remove | 2025-05-19 | 19:56 | ST | GS | - | 81.5 | g | 0 | 112.7 | 11.702 | 1161.1 | 61640 | 9:40 | 29.2 | 2.47 m/s | 24.6 | 30.4 | 3.86 m/s | 17.8 |  | 2.47 | m/s |  | 3.86 | m/s | 9.6625 | 0.0096758 | 11.2652 |  | 7 | 81.5 | 0.0815 | 138.2236 | 7.1492 | 5.5213 | 0.025975 | 29.5113 | 0.27617
2025-05-19 19:57 | 1159 | Remove | 2025-05-19 | 19:57 | ST | GS | - | 73 | g | 0 | 112.8 | 11.682 | 1159.4 | 61650 | 9:40 | 29.2 | 2.67 m/s | 22.3 | 30.4 | 4.07 m/s | 18.4 |  | 2.67 | m/s |  | 4.07 | m/s | 9.6708 | 0.0096617 | 11.2749 |  | -8.5 | 73 | 0.073 | 154.4505 | 6.4808 | 5.7074 | 0.025453 | 29.5367 | 0.24715
2025-05-19 19:57 | 1160 | Remove | 2025-05-19 | 19:57 | ST | GS | - | 73.5 | g | 0 | 112.7 | 11.666 | 1157.2 | 61660 | 9:41 | 29.2 | 2.44 m/s | 23.9 | 30.4 | 4.07 m/s | 18.4 |  | 2.44 | m/s |  | 4.07 | m/s | 9.6792 | 0.0096433 | 11.2845 |  | 0.5 | 73.5 | 0.0735 | 153.531 | 6.9458 | 5.7074 | 0.024929 | 29.5617 | 0.24863
2025-05-19 19:58 | 1161 | Remove | 2025-05-19 | 19:58 | ST | GS | - | 76.5 | g | 0 | 112.7 | 11.666 | 1156.9 | 61669 | 9:41 | 29.2 | 2.15 m/s | 24.8 | 30.4 | 3.93 m/s | 20.2 |  | 2.15 | m/s |  | 3.93 | m/s | 9.6875 | 0.0096408 | 11.2942 |  | 3 | 76.5 | 0.0765 | 147.6362 | 7.2073 | 6.2658 | 0.022794 | 29.5845 | 0.25858
2025-05-19 19:58 | 1162 | Remove | 2025-05-19 | 19:58 | US | GS | - | 70.5 | g | 0 | 112.8 | 11.66 | 1157 | 61679 | 9:42 | 29.2 | 2.3 m/s | 25.7 | 30.4 | 4.12 m/s | 18.7 |  | 2.3 | m/s |  | 4.12 | m/s | 9.6958 | 0.0096417 | 11.3038 |  | -6 | 70.5 | 0.0705 | 160.3378 | 7.4689 | 5.8005 | 0.025269 | 29.6097 | 0.2381
2025-05-19 19:59 | 1163 | Remove | 2025-05-19 | 19:59 | ST | GS | - | 76.5 | g | 0 | 112.8 | 11.701 | 1161.3 | 61689 | 9:42 | 29.2 | 2.47 m/s | 23.2 | 30.4 | 3.85 m/s | 19 |  | 2.47 | m/s |  | 3.85 | m/s | 9.7042 | 0.0096775 | 11.3135 |  | 6 | 76.5 | 0.0765 | 147.8887 | 6.7423 | 5.8935 | 0.024497 | 29.6342 | 0.25815
2025-05-19 19:59 | 1164 | Remove | 2025-05-19 | 19:59 | ST | GS | - | 74.5 | g | 0 | 112.8 | 11.698 | 1161.4 | 61698 | 9:43 | 29.2 | 2.26 m/s | 22.7 | 30.4 | 3.86 m/s | 18.1 |  | 2.26 | m/s |  | 3.86 | m/s | 9.7125 | 0.0096783 | 11.3232 |  | -2 | 74.5 | 0.0745 | 151.9888 | 6.597 | 5.6144 | 0.021931 | 29.6562 | 0.25121
2025-05-19 20:00 | 1165 | Remove | 2025-05-19 | 20:00 | ST | GS | - | 76.5 | g | 0 | 112.8 | 11.691 | 1160.5 | 61708 | 9:43 | 29.2 | 2.15 m/s | 22.2 | 30.4 | 3.96 m/s | 18.1 |  | 2.15 | m/s |  | 3.96 | m/s | 9.7208 | 0.0096708 | 11.3328 |  | 2 | 76.5 | 0.0765 | 148.1417 | 6.4517 | 5.6144 | 0.020404 | 29.6766 | 0.25778
2025-05-19 20:00 | 1166 | Remove | 2025-05-19 | 20:00 | ST | GS | - | 76.5 | g | 0 | 112.7 | 11.679 | 1159 | 61718 | 9:44 | 29.2 | 2.15 m/s | 24 | 30.4 | 3.96 m/s | 17.5 |  | 2.15 | m/s |  | 3.96 | m/s | 9.7292 | 0.0096583 | 11.3425 |  | 0 | 76.5 | 0.0765 | 148.2679 | 6.9748 | 5.4283 | 0.022058 | 29.6986 | 0.25759
2025-05-19 20:01 | 1167 | Remove | 2025-05-19 | 20:01 | ST | GS | - | 77 | g | 0 | 112.7 | 11.677 | 1158.2 | 61728 | 9:44 | 29.2 | 2.57 m/s | 24.1 | 30.4 | 4.2 m/s | 18.2 |  | 2.57 | m/s |  | 4.2 | m/s | 9.7375 | 0.0096517 | 11.3521 |  | 0.5 | 77 | 0.077 | 147.4305 | 7.0039 | 5.6454 | 0.026477 | 29.7251 | 0.25904
2025-05-19 20:01 | 1168 | Remove | 2025-05-19 | 20:01 | ST | GS | - | 76.5 | g | 0 | 112.8 | 11.689 | 1160.5 | 61737 | 9:45 | 29.2 | 2.4 m/s | 24.2 | 30.4 | 3.96 m/s | 19.5 |  | 2.4 | m/s |  | 3.96 | m/s | 9.7458 | 0.0096708 | 11.3618 |  | -0.5 | 76.5 | 0.0765 | 148.5205 | 7.033 | 6.0486 | 0.024829 | 29.7499 | 0.25714
2025-05-19 20:02 | 1169 | Remove | 2025-05-19 | 20:02 | ST | GS | - | 74.5 | g | 0 | 112.8 | 11.64 | 1154.6 | 61747 | 9:45 | 29.2 | 2.22 m/s | 22.5 | 30.4 | 4.15 m/s | 17.6 |  | 2.22 | m/s |  | 4.15 | m/s | 9.7544 | 0.0096217 | 11.3714 |  | -2 | 74.5 | 0.0745 | 152.6368 | 6.5389 | 5.4593 | 0.021353 | 29.7713 | 0.25024
2025-05-19 20:02 | 1170 | Remove | 2025-05-19 | 20:02 | ST | GS | - | 76.5 | g | 0 | 112.8 | 11.652 | 1155.2 | 61756 | 9:46 | 29.2 | 2.15 m/s | 25.9 | 30.4 | 4.23 m/s | 19.3 |  | 2.15 | m/s |  | 4.23 | m/s | 9.7628 | 0.0096267 | 11.3811 |  | 2 | 76.5 | 0.0765 | 148.7721 | 7.527 | 5.9866 | 0.023805 | 29.7951 | 0.25675
2025-05-19 20:03 | 1171 | Keep | 2025-05-19 | 20:03 | ST | GS | - | 73 | g | 0 | 112.8 | 11.673 | 1158.6 | 61766 | 9:46 | 29.2 | 2.33 m/s | 22.3 | 30.4 | 3.79 m/s | 18.4 |  | 2.33 | m/s |  | 3.79 | m/s | 9.7711 | 0.009655 | 11.3907 |  | -3.5 | 73 | 0.073 | 156.0373 | 6.4808 | 5.7074 | 0.022212 | 29.8173 | 0.24482
2025-05-19 20:03 | 1172 | Remove | 2025-05-19 | 20:03 | ST | GS | - | 73.5 | g | 0 | 112.8 | 11.652 | 1155.9 | 61776 | 9:47 | 29.2 | 2.18 m/s | 23.1 | 30.4 | 3.86 m/s | 18.1 |  | 2.18 | m/s |  | 3.86 | m/s | 9.7794 | 0.0096325 | 11.4004 |  | 0.5 | 73.5 | 0.0735 | 155.1069 | 6.7133 | 5.6144 | 0.021527 | 29.8388 | 0.24632
2025-05-19 20:04 | 1173 | Remove | 2025-05-19 | 20:04 | ST | GS | - | 76 | g | 0 | 112.8 | 11.699 | 1161.2 | 61786 | 9:47 | 29.2 | 2.27 m/s | 24.4 | 30.4 | 3.97 m/s | 18.5 |  | 2.27 | m/s |  | 3.97 | m/s | 9.7878 | 0.0096767 | 11.41 |  | 2.5 | 76 | 0.076 | 150.132 | 7.0911 | 5.7385 | 0.023678 | 29.8625 | 0.2545
2025-05-19 20:04 | 1174 | Remove | 2025-05-19 | 20:04 | ST | GS | - | 75.5 | g | 0 | 112.8 | 11.67 | 1158.1 | 61795 | 9:48 | 29.2 | 2.42 m/s | 24 | 30.4 | 4.15 m/s | 17.2 |  | 2.42 | m/s |  | 4.15 | m/s | 9.7961 | 0.0096508 | 11.4197 |  | -0.5 | 75.5 | 0.0755 | 151.2541 | 6.9748 | 5.3352 | 0.024829 | 29.8873 | 0.25262
2025-05-19 20:05 | 1175 | Remove | 2025-05-19 | 20:05 | ST | GS | - | 75 | g | 0 | 112.8 | 11.685 | 1159.8 | 61805 | 9:48 | 29.2 | 2.37 m/s | 23.6 | 30.4 | 4.16 m/s | 18 |  | 2.37 | m/s |  | 4.16 | m/s | 9.8044 | 0.009665 | 11.4293 |  | -0.5 | 75 | 0.075 | 152.3913 | 6.8586 | 5.5834 | 0.02391 | 29.9112 | 0.25074
2025-05-19 20:05 | 1176 | Remove | 2025-05-19 | 20:05 | US | GS | - | 80.5 | g | 0 | 112.8 | 11.695 | 1160.9 | 61815 | 9:49 | 29.2 | 2.37 m/s | 23.4 | 30.4 | 3.89 m/s | 17.5 |  | 2.37 | m/s |  | 3.89 | m/s | 9.8128 | 0.0096742 | 11.439 |  | 5.5 | 80.5 | 0.0805 | 142.0996 | 6.8005 | 5.4283 | 0.023708 | 29.9349 | 0.26892
2025-05-19 20:06 | 1177 | Remove | 2025-05-19 | 20:06 | ST | GS | - | 73 | g | 0 | 112.9 | 11.647 | 1155.1 | 61824 | 9:49 | 29.2 | 2.38 m/s | 21.3 | 30.4 | 3.79 m/s | 17.6 |  | 2.38 | m/s |  | 3.79 | m/s | 9.8211 | 0.0096258 | 11.4486 |  | -7.5 | 73 | 0.073 | 156.8308 | 6.1902 | 5.4593 | 0.021671 | 29.9566 | 0.24369
2025-05-19 20:06 | 1178 | Remove | 2025-05-19 | 20:06 | ST | GS | - | 73.5 | g | 0 | 112.9 | 11.64 | 1154.7 | 61834 | 9:50 | 29.2 | 2.35 m/s | 23.4 | 30.4 | 4.0 m/s | 19.7 |  | 2.35 | m/s |  | 4 | m/s | 9.8294 | 0.0096225 | 11.4583 |  | 0.5 | 73.5 | 0.0735 | 155.8948 | 6.8005 | 6.1107 | 0.023508 | 29.9801 | 0.24516
2025-05-19 20:07 | 1179 | Remove | 2025-05-19 | 20:07 | US | GS | - | 75.5 | g | 0 | 112.9 | 11.671 | 1157.6 | 61844 | 9:50 | 29.2 | 2.44 m/s | 24.3 | 30.4 | 4.07 m/s | 18.5 |  | 2.44 | m/s |  | 4.07 | m/s | 9.8378 | 0.0096467 | 11.4679 |  | 2 | 75.5 | 0.0755 | 151.8929 | 7.062 | 5.7385 | 0.025347 | 30.0055 | 0.25162
2025-05-19 20:07 | 1180 | Remove | 2025-05-19 | 20:07 | US | GS | - | 77.5 | g | 0 | 112.9 | 11.672 | 1158.1 | 61853 | 9:51 | 29.2 | 2.35 m/s | 23 | 30.4 | 3.93 m/s | 18 |  | 2.35 | m/s |  | 3.93 | m/s | 9.8461 | 0.0096508 | 11.4776 |  | 2 | 77.5 | 0.0775 | 148.0976 | 6.6842 | 5.5834 | 0.023106 | 30.0286 | 0.25809
2025-05-19 20:08 | 1181 | Remove | 2025-05-19 | 20:08 | US | GS | - | 78.5 | g | 0 | 112.9 | 11.675 | 1158.7 | 61863 | 9:51 | 29.2 | 2.44 m/s | 23.3 | 30.3 | 3.81 m/s | 17.6 |  | 2.44 | m/s |  | 3.81 | m/s | 9.8544 | 0.0096558 | 11.4872 |  | 1 | 78.5 | 0.0785 | 146.3341 | 6.7714 | 5.4298 | 0.024304 | 30.0529 | 0.26121
2025-05-19 20:08 | 1182 | Remove | 2025-05-19 | 20:08 | US | GS | - | 82 | g | 0 | 112.8 | 11.654 | 1156.1 | 61873 | 9:52 | 29.2 | 2.01 m/s | 24.1 | 30.4 | 3.65 m/s | 19 |  | 2.01 | m/s |  | 3.65 | m/s | 9.8628 | 0.0096342 | 11.4969 |  | 3.5 | 82 | 0.082 | 140.2056 | 7.0039 | 5.8935 | 0.020708 | 30.0736 | 0.27266
2025-05-19 20:09 | 1183 | Remove | 2025-05-19 | 20:09 | US | GS | - | 78 | g | 0 | 112.9 | 11.652 | 1155.8 | 61882 | 9:52 | 29.2 | 2.27 m/s | 23.3 | 30.3 | 3.87 m/s | 18.8 |  | 2.27 | m/s |  | 3.87 | m/s | 9.8711 | 0.0096317 | 11.5065 |  | -4 | 78 | 0.078 | 147.5191 | 6.7714 | 5.8001 | 0.02261 | 30.0962 | 0.25917
2025-05-19 20:09 | 1184 | Remove | 2025-05-19 | 20:09 | US | GS | - | 82.5 | g | 0 | 112.9 | 11.641 | 1154.5 | 61892 | 9:53 | 29.2 | 2.38 m/s | 24.8 | 30.3 | 4.04 m/s | 18.6 |  | 2.38 | m/s |  | 4.04 | m/s | 9.8794 | 0.0096208 | 11.5161 |  | 4.5 | 82.5 | 0.0825 | 139.5892 | 7.2073 | 5.7384 | 0.025232 | 30.1214 | 0.27389
2025-05-19 20:10 | 1185 | Remove | 2025-05-19 | 20:10 | US | GS | - | 79 | g | 0 | 112.9 | 11.663 | 1157.4 | 61902 | 9:53 | 29.2 | 2.58 m/s | 23.5 | 30.3 | 4.01 m/s | 19.5 |  | 2.58 | m/s |  | 4.01 | m/s | 9.8878 | 0.009645 | 11.5258 |  | -3.5 | 79 | 0.079 | 145.8956 | 6.8295 | 6.016 | 0.025919 | 30.1473 | 0.26205
2025-05-19 20:10 | 1186 | Remove | 2025-05-19 | 20:10 | US | GS | - | 93.5 | g | 0 | 112.9 | 11.661 | 1156.4 | 61911 | 9:54 | 29.2 | 2.52 m/s | 23.6 | 30.3 | 3.92 m/s | 18.7 |  | 2.52 | m/s |  | 3.92 | m/s | 9.8961 | 0.0096367 | 11.5354 |  | 14.5 | 93.5 | 0.0935 | 123.3732 | 6.8586 | 5.7692 | 0.025424 | 30.1728 | 0.30988
2025-05-19 20:11 | 1187 | Remove | 2025-05-19 | 20:11 | ST | GS | - | 80 | g | 0 | 112.8 | 11.674 | 1158 | 61921 | 9:54 | 29.2 | 2.4 m/s | 23 | 30.3 | 4.09 m/s | 18.1 |  | 2.4 | m/s |  | 4.09 | m/s | 9.9044 | 0.00965 | 11.545 |  | -13.5 | 80 | 0.08 | 144.313 | 6.6842 | 5.5841 | 0.023597 | 30.1964 | 0.26493
2025-05-19 20:11 | 1188 | Remove | 2025-05-19 | 20:11 | US | GS | - | 80 | g | 0 | 112.8 | 11.66 | 1156.4 | 61931 | 9:55 | 29.2 | 2.16 m/s | 22.3 | 30.3 | 3.76 m/s | 18.3 |  | 2.16 | m/s |  | 3.76 | m/s | 9.9131 | 0.0096367 | 11.5547 |  | 0 | 80 | 0.08 | 144.4335 | 6.4808 | 5.6458 | 0.020591 | 30.217 | 0.26475
2025-05-19 20:12 | 1189 | Remove | 2025-05-19 | 20:12 | ST | GS | - | 78.5 | g | 0 | 112.8 | 11.658 | 1156.2 | 61940 | 9:55 | 29.2 | 2.25 m/s | 23.8 | 30.3 | 3.9 m/s | 18.2 |  | 2.25 | m/s |  | 3.9 | m/s | 9.9214 | 0.009635 | 11.5643 |  | -1.5 | 78.5 | 0.0785 | 147.3161 | 6.9167 | 5.6149 | 0.022892 | 30.2399 | 0.25959
2025-05-19 20:12 | 1190 | Remove | 2025-05-19 | 20:12 | US | GS | - | 75.5 | g | 0 | 112.9 | 11.628 | 1152.7 | 61950 | 9:56 | 29.2 | 2.4 m/s | 23.9 | 30.3 | 4.03 m/s | 17.9 |  | 2.4 | m/s |  | 4.03 | m/s | 9.9297 | 0.0096058 | 11.5739 |  | -3 | 75.5 | 0.0755 | 153.2969 | 6.9458 | 5.5224 | 0.024521 | 30.2644 | 0.24947
2025-05-19 20:13 | 1191 | Remove | 2025-05-19 | 20:13 | ST | GS | - | 76.5 | g | 0 | 112.9 | 11.644 | 1155 | 61960 | 9:56 | 29.2 | 2.33 m/s | 25.3 | 30.4 | 3.89 m/s | 20.3 |  | 2.33 | m/s |  | 3.89 | m/s | 9.9381 | 0.009625 | 11.5835 |  | 1 | 76.5 | 0.0765 | 151.4189 | 7.3526 | 6.2968 | 0.0252 | 30.2896 | 0.25256
2025-05-19 20:13 | 1192 | Remove | 2025-05-19 | 20:13 | ST | GS | - | 77.5 | g | 0 | 112.8 | 11.652 | 1155.9 | 61969 | 9:57 | 29.2 | 2.31 m/s | 23.6 | 30.3 | 4.07 m/s | 18.3 |  | 2.31 | m/s |  | 4.07 | m/s | 9.9464 | 0.0096325 | 11.5932 |  | 1 | 77.5 | 0.0775 | 149.5894 | 6.8586 | 5.6458 | 0.023305 | 30.3129 | 0.25567
2025-05-19 20:14 | 1193 | Remove | 2025-05-19 | 20:14 | ST | GS | - | 77 | g | 0 | 112.8 | 11.665 | 1157.1 | 61979 | 9:57 | 29.2 | 2.44 m/s | 26 | 30.3 | 3.9 m/s | 18.3 |  | 2.44 | m/s |  | 3.9 | m/s | 9.9547 | 0.0096425 | 11.6028 |  | -0.5 | 77 | 0.077 | 150.686 | 7.5561 | 5.6458 | 0.02712 | 30.34 | 0.25379
2025-05-19 20:14 | 1194 | Remove | 2025-05-19 | 20:14 | US | GS | - | 84.5 | g | 0 | 112.8 | 11.66 | 1156.8 | 61989 | 9:58 | 29.2 | 2.41 m/s | 23.8 | 30.3 | 4.03 m/s | 18.1 |  | 2.41 | m/s |  | 4.03 | m/s | 9.9631 | 0.00964 | 11.6125 |  | 7.5 | 84.5 | 0.0845 | 137.4256 | 6.9167 | 5.5841 | 0.02452 | 30.3645 | 0.27829
2025-05-19 20:15 | 1195 | Remove | 2025-05-19 | 20:15 | ST | GS | - | 75.5 | g | 0 | 112.9 | 11.633 | 1153.1 | 61998 | 9:58 | 29.2 | 2.25 m/s | 24 | 30.3 | 3.81 m/s | 18 |  | 2.25 | m/s |  | 3.81 | m/s | 9.9714 | 0.0096092 | 11.6221 |  | -9 | 75.5 | 0.0755 | 153.9347 | 6.9748 | 5.5532 | 0.023084 | 30.3876 | 0.24846
2025-05-19 20:15 | 1196 | Remove | 2025-05-19 | 20:15 | ST | GS | - | 75 | g | 0 | 112.9 | 11.628 | 1152.6 | 62008 | 9:59 | 29.2 | 2.38 m/s | 23.4 | 30.3 | 3.81 m/s | 18.8 |  | 2.38 | m/s |  | 3.81 | m/s | 9.9797 | 0.009605 | 11.6317 |  | -0.5 | 75 | 0.075 | 155.089 | 6.8005 | 5.8001 | 0.023808 | 30.4114 | 0.24662
2025-05-19 20:16 | 1197 | Remove | 2025-05-19 | 20:16 | ST | GS | - | 81 | g | 0 | 112.9 | 11.664 | 1157 | 62018 | 9:59 | 29.2 | 2.04 m/s | 22.7 | 30.3 | 4.13 m/s | 18.5 |  | 2.04 | m/s |  | 4.13 | m/s | 9.9881 | 0.0096417 | 11.6413 |  | 6 | 81 | 0.081 | 143.7199 | 6.597 | 5.7075 | 0.019796 | 30.4312 | 0.26617
2025-05-19 20:16 | 1198 | Remove | 2025-05-19 | 20:16 | US | GS | - | 76 | g | 0 | 112.9 | 11.637 | 1154.3 | 62027 | 10:00 | 29.2 | 2.26 m/s | 23.6 | 30.3 | 4.0 m/s | 19 |  | 2.26 | m/s |  | 4 | m/s | 9.9964 | 0.0096192 | 11.6509 |  | -5 | 76 | 0.076 | 153.3018 | 6.8586 | 5.8618 | 0.022801 | 30.454 | 0.24956
2025-05-19 20:17 | 1199 | Remove | 2025-05-19 | 20:17 | US | GS | - | 81.5 | g | 0 | 112.9 | 11.634 | 1153.2 | 62037 | 10:00 | 29.2 | 2.23 m/s | 24.1 | 30.3 | 4.12 m/s | 17.8 |  | 2.23 | m/s |  | 4.12 | m/s | 10.0047 | 0.00961 | 11.6605 |  | 5.5 | 81.5 | 0.0815 | 143.0742 | 7.0039 | 5.4915 | 0.022975 | 30.477 | 0.26741
2025-05-19 20:17 | 1200 | Remove | 2025-05-19 | 20:17 | ST | GS | - | 77.5 | g | 0 | 112.9 | 11.645 | 1154.5 | 62046 | 10:01 | 29.2 | 2.48 m/s | 22.6 | 30.3 | 3.92 m/s | 18.1 |  | 2.48 | m/s |  | 3.92 | m/s | 10.0131 | 0.0096208 | 11.6702 |  | -4 | 77.5 | 0.0775 | 150.5828 | 6.568 | 5.5841 | 0.02396 | 30.5009 | 0.25409
2025-05-19 20:18 | 1201 | Keep | 2025-05-19 | 20:18 | US | GS | - | 85.5 | g | 0 | 112.9 | 11.627 | 1152.8 | 62056 | 10:01 | 29.2 | 2.35 m/s | 23.6 | 30.3 | 4.09 m/s | 17.3 |  | 2.35 | m/s |  | 4.09 | m/s | 10.0214 | 0.0096067 | 11.6798 |  | 8 | 85.5 | 0.0855 | 136.6055 | 6.8586 | 5.3373 | 0.023709 | 30.5247 | 0.2801
2025-05-19 20:18 | 1202 | Remove | 2025-05-19 | 20:18 | US | GS | - | 77.5 | g | 0 | 113 | 11.628 | 1152.5 | 62066 | 10:02 | 29.1 | 2.06 m/s | 24.6 | 30.3 | 4.24 m/s | 19 |  | 2.06 | m/s |  | 4.24 | m/s | 10.0297 | 0.0096042 | 11.6894 |  | -8 | 77.5 | 0.0775 | 150.8307 | 7.1103 | 5.8618 | 0.021546 | 30.5462 | 0.25371
2025-05-19 20:19 | 1203 | Remove | 2025-05-19 | 20:19 | ST | GS | - | 78 | g | 0 | 112.9 | 11.612 | 1150 | 62075 | 10:02 | 29.1 | 2.3 m/s | 23.4 | 30.3 | 4.13 m/s | 17.9 |  | 2.3 | m/s |  | 4.13 | m/s | 10.0381 | 0.0095833 | 11.699 |  | 0.5 | 78 | 0.078 | 149.9867 | 6.7635 | 5.5224 | 0.022882 | 30.5691 | 0.25516
2025-05-19 20:19 | 1204 | Remove | 2025-05-19 | 20:19 | ST | GS | - | 82.5 | g | 0 | 113 | 11.633 | 1153.5 | 62085 | 10:03 | 29.1 | 2.16 m/s | 24.3 | 30.3 | 3.93 m/s | 18.2 |  | 2.16 | m/s |  | 3.93 | m/s | 10.0464 | 0.0096125 | 11.7086 |  | 4.5 | 82.5 | 0.0825 | 141.9221 | 7.0236 | 5.6149 | 0.022316 | 30.5914 | 0.26968
2025-05-19 20:20 | 1205 | Remove | 2025-05-19 | 20:20 | US | GS | - | 84.5 | g | 0 | 112.9 | 11.629 | 1152.9 | 62095 | 10:03 | 29.1 | 2.25 m/s | 22.8 | 30.3 | 3.92 m/s | 17.6 |  | 2.25 | m/s |  | 3.92 | m/s | 10.0547 | 0.0096075 | 11.7182 |  | 2 | 84.5 | 0.0845 | 138.6767 | 6.59 | 5.4298 | 0.021811 | 30.6132 | 0.27602
2025-05-19 20:20 | 1206 | Remove | 2025-05-19 | 20:20 | US | GS | - | 81 | g | 0 | 113 | 11.618 | 1151.2 | 62104 | 10:04 | 29.1 | 2.16 m/s | 23.3 | 30.3 | 3.94 m/s | 18.4 |  | 2.16 | m/s |  | 3.94 | m/s | 10.0633 | 0.0095933 | 11.7278 |  | -3.5 | 81 | 0.081 | 144.7873 | 6.7345 | 5.6767 | 0.021398 | 30.6346 | 0.26441
2025-05-19 20:21 | 1207 | Remove | 2025-05-19 | 20:21 | ST | GS | - | 78.5 | g | 0 | 113 | 11.592 | 1148.3 | 62114 | 10:04 | 29.1 | 2.26 m/s | 26.4 | 30.3 | 3.9 m/s | 18.5 |  | 2.26 | m/s |  | 3.9 | m/s | 10.0717 | 0.0095692 | 11.7373 |  | -2.5 | 78.5 | 0.0785 | 149.5203 | 7.6306 | 5.7075 | 0.025367 | 30.66 | 0.25603
2025-05-19 20:22 | 1208 | Remove | 2025-05-19 | 20:22 | US | GS | - | 81.5 | g | 0 | 113 | 11.621 | 1152.1 | 62124 | 10:05 | 29.1 | 2.26 m/s | 25.9 | 30.3 | 4.04 m/s | 21.4 |  | 2.26 | m/s |  | 4.04 | m/s | 10.08 | 0.0096008 | 11.7469 |  | 3 | 81.5 | 0.0815 | 144.1343 | 7.486 | 6.6022 | 0.024886 | 30.6849 | 0.2656
2025-05-19 20:22 | 1209 | Remove | 2025-05-19 | 20:22 | ST | GS | - | 77 | g | 0 | 113 | 11.627 | 1153.3 | 62133 | 10:05 | 29.1 | 2.12 m/s | 23.4 | 30.3 | 3.9 m/s | 17.4 |  | 2.12 | m/s |  | 3.9 | m/s | 10.0883 | 0.0096108 | 11.7566 |  | -4.5 | 77 | 0.077 | 152.6825 | 6.7635 | 5.3681 | 0.021091 | 30.7059 | 0.25077
2025-05-19 20:22 | 1210 | Remove | 2025-05-19 | 20:22 | ST | GS | - | 77 | g | 0 | 113 | 11.604 | 1149.6 | 62143 | 10:06 | 29.1 | 2.25 m/s | 23.7 | 30.3 | 4.01 m/s | 18.3 |  | 2.25 | m/s |  | 4.01 | m/s | 10.0967 | 0.00958 | 11.7661 |  | 0 | 77 | 0.077 | 152.8069 | 6.8502 | 5.6458 | 0.022672 | 30.7286 | 0.25058
2025-05-19 20:23 | 1211 | Remove | 2025-05-19 | 20:23 | ST | GS | - | 77 | g | 0 | 113 | 11.624 | 1152.7 | 62152 | 10:06 | 29.1 | 2.41 m/s | 23.1 | 30.3 | 3.94 m/s | 19 |  | 2.41 | m/s |  | 3.94 | m/s | 10.105 | 0.0096058 | 11.7757 |  | 0 | 77 | 0.077 | 152.9317 | 6.6767 | 5.8618 | 0.023669 | 30.7523 | 0.25039
2025-05-19 20:24 | 1212 | Remove | 2025-05-19 | 20:24 | ST | GS | - | 77 | g | 0 | 112.9 | 11.644 | 1155 | 62162 | 10:07 | 29.1 | 2.31 m/s | 22.6 | 30.3 | 4.06 m/s | 18.7 |  | 2.31 | m/s |  | 4.06 | m/s | 10.1133 | 0.009625 | 11.7854 |  | 0 | 77 | 0.077 | 153.0567 | 6.5322 | 5.7692 | 0.022196 | 30.7745 | 0.25021
2025-05-19 20:24 | 1213 | Remove | 2025-05-19 | 20:24 | ST | GS | - | 77 | g | 0 | 112.9 | 11.619 | 1152.1 | 62172 | 10:07 | 29.1 | 2.15 m/s | 22.6 | 30.3 | 3.94 m/s | 18 |  | 2.15 | m/s |  | 3.94 | m/s | 10.1217 | 0.0096008 | 11.795 |  | 0 | 77 | 0.077 | 153.1814 | 6.5322 | 5.5532 | 0.020659 | 30.7951 | 0.25004
2025-05-19 20:24 | 1214 | Remove | 2025-05-19 | 20:24 | ST | GS | - | 77.5 | g | 0 | 113 | 11.597 | 1149 | 62181 | 10:08 | 29.1 | 2.3 m/s | 24.7 | 30.3 | 4.01 m/s | 19 |  | 2.3 | m/s |  | 4.01 | m/s | 10.13 | 0.009575 | 11.8045 |  | 0.5 | 77.5 | 0.0775 | 152.3166 | 7.1392 | 5.8618 | 0.024153 | 30.8193 | 0.25147
2025-05-19 20:25 | 1215 | Remove | 2025-05-19 | 20:25 | ST | GS | - | 76.5 | g | 0 | 112.8 | 11.623 | 1152.2 | 62191 | 10:08 | 29.1 | 2.5 m/s | 23.1 | 30.3 | 3.98 m/s | 18 |  | 2.5 | m/s |  | 3.98 | m/s | 10.1383 | 0.0096017 | 11.8141 |  | -1 | 76.5 | 0.0765 | 154.4332 | 6.6767 | 5.5532 | 0.024553 | 30.8439 | 0.24802
2025-05-19 20:26 | 1216 | Remove | 2025-05-19 | 20:26 | ST | GS | - | 77.5 | g | 0 | 113 | 11.605 | 1150.1 | 62201 | 10:09 | 29.1 | 2.19 m/s | 24.4 | 30.3 | 3.85 m/s | 17.1 |  | 2.19 | m/s |  | 3.85 | m/s | 10.1467 | 0.0095842 | 11.8237 |  | 1 | 77.5 | 0.0775 | 152.5642 | 7.0525 | 5.2756 | 0.022719 | 30.8666 | 0.25108
2025-05-19 20:26 | 1217 | Remove | 2025-05-19 | 20:26 | ST | GS | - | 78.5 | g | 0 | 113 | 11.572 | 1147 | 62210 | 10:09 | 29.1 | 2.09 m/s | 23.6 | 30.3 | 3.89 m/s | 19.7 |  | 2.09 | m/s |  | 3.89 | m/s | 10.155 | 0.0095583 | 11.8333 |  | 1 | 78.5 | 0.0785 | 150.7425 | 6.8213 | 6.0777 | 0.020971 | 30.8875 | 0.25415
2025-05-19 20:26 | 1218 | Remove | 2025-05-19 | 20:26 | US | GS | - | 79.5 | g | 0 | 112.9 | 11.618 | 1152.2 | 62220 | 10:10 | 29.1 | 2.27 m/s | 23.5 | 30.3 | 4.18 m/s | 18.2 |  | 2.27 | m/s |  | 4.18 | m/s | 10.1633 | 0.0096017 | 11.8429 |  | 1 | 79.5 | 0.0795 | 148.9671 | 6.7924 | 5.6149 | 0.02268 | 30.9102 | 0.2572
2025-05-19 20:27 | 1219 | Remove | 2025-05-19 | 20:27 | US | GS | - | 82 | g | 0 | 112.9 | 11.616 | 1151.6 | 62229 | 10:10 | 29.1 | 2.33 m/s | 23.4 | 30.3 | 4.01 m/s | 18.2 |  | 2.33 | m/s |  | 4.01 | m/s | 10.1717 | 0.0095967 | 11.8525 |  | 2.5 | 82 | 0.082 | 144.5425 | 6.7635 | 5.6149 | 0.023181 | 30.9334 | 0.26509
2025-05-19 20:28 | 1220 | Remove | 2025-05-19 | 20:28 | US | GS | - | 82 | g | 0 | 112.8 | 11.616 | 1151.8 | 62239 | 10:11 | 29.1 | 2.18 m/s | 23.2 | 30.3 | 4.01 m/s | 17.7 |  | 2.18 | m/s |  | 4.01 | m/s | 10.18 | 0.0095983 | 11.8621 |  | 0 | 82 | 0.082 | 144.6595 | 6.7056 | 5.4607 | 0.021503 | 30.9549 | 0.2649
2025-05-19 20:28 | 1221 | Remove | 2025-05-19 | 20:28 | ST | GS | - | 78.5 | g | 0 | 113 | 11.615 | 1151.2 | 62249 | 10:11 | 29.1 | 2.31 m/s | 27.2 | 30.3 | 3.92 m/s | 17.4 |  | 2.31 | m/s |  | 3.92 | m/s | 10.1883 | 0.0095933 | 11.8717 |  | -3.5 | 78.5 | 0.0785 | 151.2315 | 7.8618 | 5.3681 | 0.026714 | 30.9816 | 0.25338
2025-05-19 20:28 | 1222 | Remove | 2025-05-19 | 20:28 | US | GS | - | 81.5 | g | 0 | 113 | 11.615 | 1152.1 | 62258 | 10:12 | 29.1 | 2.35 m/s | 22.6 | 30.3 | 4.07 m/s | 17.4 |  | 2.35 | m/s |  | 4.07 | m/s | 10.1967 | 0.0096008 | 11.8813 |  | 3 | 81.5 | 0.0815 | 145.7825 | 6.5322 | 5.3681 | 0.02258 | 31.0042 | 0.26287
2025-05-19 20:29 | 1223 | Remove | 2025-05-19 | 20:29 | US | GS | - | 77 | g | 0 | 112.9 | 11.614 | 1151.7 | 62268 | 10:12 | 29.1 | 2.12 m/s | 23.3 | 30.3 | 3.92 m/s | 17.8 |  | 2.12 | m/s |  | 3.92 | m/s | 10.2053 | 0.0095975 | 11.8909 |  | -4.5 | 77 | 0.077 | 154.4269 | 6.7345 | 5.4915 | 0.021001 | 31.0252 | 0.24819
2025-05-19 20:30 | 1224 | Remove | 2025-05-19 | 20:30 | ST | GS | - | 78.5 | g | 0 | 113 | 11.597 | 1149.2 | 62277 | 10:13 | 29.1 | 2.13 m/s | 22.9 | 30.3 | 3.98 m/s | 17.7 |  | 2.13 | m/s |  | 3.98 | m/s | 10.2136 | 0.0095767 | 11.9004 |  | 1.5 | 78.5 | 0.0785 | 151.5981 | 6.6189 | 5.4607 | 0.020738 | 31.0459 | 0.25285
2025-05-19 20:30 | 1225 | Remove | 2025-05-19 | 20:30 | ST | GS | - | 79.5 | g | 0 | 113.1 | 11.585 | 1148.8 | 62287 | 10:13 | 29.1 | 2.45 m/s | 25.4 | 30.3 | 3.89 m/s | 18.4 |  | 2.45 | m/s |  | 3.89 | m/s | 10.2219 | 0.0095733 | 11.91 |  | 1 | 79.5 | 0.0795 | 149.8116 | 7.3415 | 5.6767 | 0.026458 | 31.0724 | 0.25585
2025-05-19 20:31 | 1226 | Remove | 2025-05-19 | 20:31 | US | GS | - | 81.5 | g | 0 | 113 | 11.578 | 1147.4 | 62297 | 10:14 | 29.1 | 2.35 m/s | 23.1 | 30.3 | 3.97 m/s | 18.4 |  | 2.35 | m/s |  | 3.97 | m/s | 10.2303 | 0.0095617 | 11.9196 |  | 2 | 81.5 | 0.0815 | 146.2526 | 6.6767 | 5.6767 | 0.02308 | 31.0955 | 0.2621
2025-05-19 20:31 | 1227 | Remove | 2025-05-19 | 20:31 | ST | GS | - | 79 | g | 0 | 113 | 11.582 | 1148.5 | 62306 | 10:14 | 29.1 | 2.18 m/s | 24.5 | 30.3 | 4.01 m/s | 18.5 |  | 2.18 | m/s |  | 4.01 | m/s | 10.2386 | 0.0095708 | 11.9292 |  | -2.5 | 79 | 0.079 | 151.002 | 7.0814 | 5.7075 | 0.022708 | 31.1182 | 0.25387
2025-05-19 20:32 | 1228 | Remove | 2025-05-19 | 20:32 | ST | GS | - | 80 | g | 0 | 113.1 | 11.561 | 1146.1 | 62316 | 10:15 | 29.1 | 2.25 m/s | 24 | 30.3 | 4.23 m/s | 18.1 |  | 2.25 | m/s |  | 4.23 | m/s | 10.2469 | 0.0095508 | 11.9387 |  | 1 | 80 | 0.08 | 149.2338 | 6.9369 | 5.5841 | 0.022959 | 31.1411 | 0.25689
2025-05-19 20:32 | 1229 | Remove | 2025-05-19 | 20:32 | US | GS | - | 81.5 | g | 0 | 113 | 11.566 | 1145.8 | 62325 | 10:15 | 29.1 | 2.3 m/s | 25.5 | 30.3 | 4.13 m/s | 18.8 |  | 2.3 | m/s |  | 4.13 | m/s | 10.2553 | 0.0095483 | 11.9483 |  | 1.5 | 81.5 | 0.0815 | 146.6043 | 7.3704 | 5.8001 | 0.024936 | 31.1661 | 0.2615
2025-05-19 20:33 | 1230 | Remove | 2025-05-19 | 20:33 | ST | GS | - | 78.5 | g | 0 | 113 | 11.548 | 1143.5 | 62335 | 10:16 | 29.1 | 2.35 m/s | 25.4 | 30.3 | 3.98 m/s | 18.5 |  | 2.35 | m/s |  | 3.98 | m/s | 10.2636 | 0.0095292 | 11.9578 |  | -3 | 78.5 | 0.0785 | 152.3285 | 7.3415 | 5.7075 | 0.025378 | 31.1915 | 0.25167
2025-05-19 20:33 | 1231 | Keep | 2025-05-19 | 20:33 | ST | GS | - | 80.5 | g | 0 | 112.9 | 11.595 | 1148.8 | 62345 | 10:16 | 29.1 | 2.38 m/s | 23.5 | 30.3 | 3.89 m/s | 19.6 |  | 2.38 | m/s |  | 3.89 | m/s | 10.2719 | 0.0095733 | 11.9674 |  | 2 | 80.5 | 0.0805 | 148.6628 | 6.7924 | 6.0469 | 0.023779 | 31.2152 | 0.25789
2025-05-19 20:34 | 1232 | Remove | 2025-05-19 | 20:34 | ST | GS | - | 78 | g | 0 | 113.1 | 11.555 | 1144.2 | 62354 | 10:17 | 29.1 | 2.16 m/s | 24.3 | 30.3 | 4.04 m/s | 17.8 |  | 2.16 | m/s |  | 4.04 | m/s | 10.2803 | 0.009535 | 11.9769 |  | -2.5 | 78 | 0.078 | 153.5499 | 7.0236 | 5.4915 | 0.022316 | 31.2376 | 0.2497
2025-05-19 20:34 | 1233 | Remove | 2025-05-19 | 20:34 | ST | GS | - | 78.5 | g | 0 | 112.8 | 11.585 | 1147.3 | 62364 | 10:17 | 29.1 | 2.33 m/s | 26.1 | 30.3 | 4.04 m/s | 18.5 |  | 2.33 | m/s |  | 4.04 | m/s | 10.2886 | 0.0095608 | 11.9865 |  | 0.5 | 78.5 | 0.0785 | 152.6937 | 7.5438 | 5.7075 | 0.025855 | 31.2634 | 0.25109
2025-05-19 20:35 | 1234 | Remove | 2025-05-19 | 20:35 | US | GS | - | 81 | g | 0 | 113 | 11.551 | 1144.4 | 62373 | 10:18 | 29 | 2.05 m/s | 23.6 | 30.3 | 4.03 m/s | 18.6 |  | 2.05 | m/s |  | 4.03 | m/s | 10.2969 | 0.0095367 | 11.996 |  | 2.5 | 81 | 0.081 | 148.0986 | 6.7841 | 5.7384 | 0.020457 | 31.2839 | 0.25892
2025-05-19 20:35 | 1235 | Remove | 2025-05-19 | 20:35 | ST | GS | - | 82 | g | 0 | 113 | 11.57 | 1146.6 | 62383 | 10:18 | 29 | 2.22 m/s | 23 | 30.3 | 4.12 m/s | 17.4 |  | 2.22 | m/s |  | 4.12 | m/s | 10.3053 | 0.009555 | 12.0055 |  | 1 | 82 | 0.082 | 146.4091 | 6.6116 | 5.3681 | 0.021591 | 31.3055 | 0.26194
2025-05-19 20:36 | 1236 | Remove | 2025-05-19 | 20:36 | ST | GS | - | 79.5 | g | 0 | 112.9 | 11.548 | 1143.3 | 62393 | 10:19 | 29 | 2.27 m/s | 23.6 | 30.3 | 4.04 m/s | 17.6 |  | 2.27 | m/s |  | 4.04 | m/s | 10.3136 | 0.0095275 | 12.0151 |  | -2.5 | 79.5 | 0.0795 | 151.133 | 6.7841 | 5.4298 | 0.022653 | 31.3281 | 0.25377
2025-05-19 20:36 | 1237 | Remove | 2025-05-19 | 20:36 | ST | GS | - | 81.5 | g | 0 | 113.1 | 11.555 | 1144.8 | 62402 | 10:19 | 29 | 2.15 m/s | 25.1 | 30.3 | 4.09 m/s | 18.2 |  | 2.15 | m/s |  | 4.09 | m/s | 10.3219 | 0.00954 | 12.0246 |  | 2 | 81.5 | 0.0815 | 147.5412 | 7.2153 | 5.6149 | 0.022819 | 31.3509 | 0.25996
2025-05-19 20:37 | 1238 | Remove | 2025-05-19 | 20:37 | US | GS | - | 88 | g | 0 | 113 | 11.564 | 1146.1 | 62412 | 10:20 | 29 | 2.27 m/s | 23.1 | 30.3 | 3.93 m/s | 18.2 |  | 2.27 | m/s |  | 3.93 | m/s | 10.3303 | 0.0095508 | 12.0342 |  | 6.5 | 88 | 0.088 | 136.7518 | 6.6404 | 5.6149 | 0.022173 | 31.3731 | 0.2805
2025-05-19 20:37 | 1239 | Remove | 2025-05-19 | 20:37 | US | GS | - | 82.5 | g | 0 | 113.1 | 11.536 | 1142.3 | 62421 | 10:20 | 29 | 2.2 m/s | 23.3 | 30.3 | 3.97 m/s | 18.1 |  | 2.2 | m/s |  | 3.97 | m/s | 10.3386 | 0.0095192 | 12.0437 |  | -5.5 | 82.5 | 0.0825 | 145.984 | 6.6979 | 5.5841 | 0.021675 | 31.3948 | 0.26278
2025-05-19 20:38 | 1240 | Remove | 2025-05-19 | 20:38 | ST | GS | - | 83.5 | g | 0 | 113.1 | 11.575 | 1147.3 | 62431 | 10:21 | 29 | 2.3 m/s | 23.6 | 30.3 | 3.86 m/s | 18.7 |  | 2.3 | m/s |  | 3.86 | m/s | 10.3472 | 0.0095608 | 12.0532 |  | 1 | 83.5 | 0.0835 | 144.3502 | 6.7841 | 5.7692 | 0.022952 | 31.4177 | 0.26577
2025-05-19 20:38 | 1241 | Remove | 2025-05-19 | 20:38 | ST | GS | - | 83 | g | 0 | 113 | 11.553 | 1144.2 | 62440 | 10:21 | 29 | 2.35 m/s | 23 | 30.2 | 3.96 m/s | 18 |  | 2.35 | m/s |  | 3.96 | m/s | 10.3556 | 0.009535 | 12.0628 |  | -0.5 | 83 | 0.083 | 145.3347 | 6.6116 | 5.5233 | 0.022855 | 31.4406 | 0.26399
2025-05-19 20:39 | 1242 | Remove | 2025-05-19 | 20:39 | ST | GS | - | 82 | g | 0 | 113.1 | 11.559 | 1145.8 | 62450 | 10:22 | 29 | 2.31 m/s | 23 | 30.2 | 4.03 m/s | 18.2 |  | 2.31 | m/s |  | 4.03 | m/s | 10.3639 | 0.0095483 | 12.0723 |  | -1 | 82 | 0.082 | 147.2235 | 6.6116 | 5.5846 | 0.022466 | 31.463 | 0.26062
2025-05-19 20:39 | 1243 | Remove | 2025-05-19 | 20:39 | US | GS | - | 79 | g | 0 | 113 | 11.543 | 1143.4 | 62459 | 10:22 | 29 | 2.27 m/s | 23.5 | 30.2 | 4.0 m/s | 17.8 |  | 2.27 | m/s |  | 4 | m/s | 10.3722 | 0.0095283 | 12.0819 |  | -3 | 79 | 0.079 | 152.9349 | 6.7554 | 5.4619 | 0.022557 | 31.4856 | 0.25091
2025-05-19 20:40 | 1244 | Remove | 2025-05-19 | 20:40 | US | GS | - | 81.5 | g | 0 | 113.1 | 11.527 | 1141.2 | 62469 | 10:23 | 29 | 2.37 m/s | 24.8 | 30.2 | 4.04 m/s | 19.2 |  | 2.37 | m/s |  | 4.04 | m/s | 10.3806 | 0.00951 | 12.0914 |  | 2.5 | 81.5 | 0.0815 | 148.3603 | 7.1291 | 5.8915 | 0.024853 | 31.5105 | 0.25864
2025-05-19 20:40 | 1245 | Remove | 2025-05-19 | 20:40 | ST | GS | - | 86.5 | g | 0 | 113.1 | 11.546 | 1143.6 | 62479 | 10:23 | 29 | 2.15 m/s | 22.7 | 30.2 | 3.92 m/s | 18.1 |  | 2.15 | m/s |  | 3.92 | m/s | 10.3889 | 0.00953 | 12.1009 |  | 5 | 86.5 | 0.0865 | 139.8947 | 6.5254 | 5.554 | 0.020637 | 31.5311 | 0.27433
2025-05-19 20:41 | 1246 | Remove | 2025-05-19 | 20:41 | ST | GS | - | 81.5 | g | 0 | 113.1 | 11.537 | 1143 | 62488 | 10:24 | 29 | 2.31 m/s | 23.5 | 30.2 | 3.96 m/s | 18.8 |  | 2.31 | m/s |  | 3.96 | m/s | 10.3972 | 0.009525 | 12.1104 |  | -5 | 81.5 | 0.0815 | 148.5941 | 6.7554 | 5.7688 | 0.022954 | 31.554 | 0.25829
2025-05-19 20:41 | 1247 | Remove | 2025-05-19 | 20:41 | US | GS | - | 85 | g | 0 | 113.1 | 11.537 | 1142.7 | 62498 | 10:24 | 29 | 2.37 m/s | 23.7 | 30.2 | 3.94 m/s | 18.5 |  | 2.37 | m/s |  | 3.94 | m/s | 10.4056 | 0.0095225 | 12.1199 |  | 3.5 | 85 | 0.085 | 142.5875 | 6.8129 | 5.6767 | 0.023751 | 31.5778 | 0.26918
2025-05-19 20:42 | 1248 | Remove | 2025-05-19 | 20:42 | ST | GS | - | 85 | g | 0 | 113.2 | 11.551 | 1144.1 | 62507 | 10:25 | 29 | 2.38 m/s | 25.8 | 30.2 | 3.84 m/s | 19.3 |  | 2.38 | m/s |  | 3.84 | m/s | 10.4139 | 0.0095342 | 12.1295 |  | 0 | 85 | 0.085 | 142.6997 | 7.4165 | 5.9222 | 0.025964 | 31.6038 | 0.26896
2025-05-19 20:42 | 1249 | Remove | 2025-05-19 | 20:42 | ST | GS | - | 82 | g | 0 | 113.1 | 11.552 | 1143.7 | 62517 | 10:25 | 29 | 2.18 m/s | 24.2 | 30.2 | 3.96 m/s | 18.1 |  | 2.18 | m/s |  | 3.96 | m/s | 10.4222 | 0.0095308 | 12.139 |  | -3 | 82 | 0.082 | 148.0367 | 6.9566 | 5.554 | 0.022308 | 31.6261 | 0.25928
2025-05-19 20:43 | 1250 | Remove | 2025-05-19 | 20:43 | ST | GS | - | 84.5 | g | 0 | 113.2 | 11.564 | 1145.5 | 62526 | 10:26 | 29 | 2.31 m/s | 23.1 | 30.2 | 3.81 m/s | 17.4 |  | 2.31 | m/s |  | 3.81 | m/s | 10.4306 | 0.0095458 | 12.1486 |  | 2.5 | 84.5 | 0.0845 | 143.7699 | 6.6404 | 5.3392 | 0.022564 | 31.6486 | 0.26699
2025-05-19 20:43 | 1251 | Remove | 2025-05-19 | 20:43 | ST | GS | - | 83 | g | 0 | 113.1 | 11.522 | 1140.4 | 62536 | 10:26 | 29 | 2.38 m/s | 23.3 | 30.2 | 3.94 m/s | 18.8 |  | 2.38 | m/s |  | 3.94 | m/s | 10.4389 | 0.0095033 | 12.1581 |  | -1.5 | 83 | 0.083 | 146.4826 | 6.6979 | 5.7688 | 0.023449 | 31.6721 | 0.26206
2025-05-19 20:44 | 1252 | Remove | 2025-05-19 | 20:44 | US | GS | - | 88.5 | g | 0 | 113.2 | 11.549 | 1143.9 | 62546 | 10:27 | 29 | 2.51 m/s | 22.9 | 30.2 | 3.97 m/s | 19 |  | 2.51 | m/s |  | 3.97 | m/s | 10.4472 | 0.0095325 | 12.1676 |  | 5.5 | 88.5 | 0.0885 | 137.4869 | 6.5829 | 5.8301 | 0.024305 | 31.6964 | 0.27921
2025-05-19 20:44 | 1253 | Remove | 2025-05-19 | 20:44 | ST | GS | - | 80.5 | g | 0 | 113.1 | 11.52 | 1139.5 | 62555 | 10:27 | 29 | 2.4 m/s | 24 | 30.2 | 3.92 m/s | 18.8 |  | 2.4 | m/s |  | 3.92 | m/s | 10.4556 | 0.0094958 | 12.1771 |  | -8 | 80.5 | 0.0805 | 151.2681 | 6.8991 | 5.7688 | 0.024356 | 31.7207 | 0.25378
2025-05-19 20:45 | 1254 | Remove | 2025-05-19 | 20:45 | ST | GS | - | 82.5 | g | 0 | 113.2 | 11.528 | 1141.5 | 62564 | 10:28 | 29 | 2.31 m/s | 24 | 30.2 | 3.97 m/s | 19 |  | 2.31 | m/s |  | 3.97 | m/s | 10.4639 | 0.0095125 | 12.1866 |  | 2 | 82.5 | 0.0825 | 147.7163 | 6.8991 | 5.8301 | 0.023443 | 31.7442 | 0.25989
2025-05-19 20:45 | 1255 | Remove | 2025-05-19 | 20:45 | US | GS | - | 85 | g | 0 | 113.1 | 11.523 | 1140.8 | 62574 | 10:28 | 29 | 2.55 m/s | 24.8 | 30.2 | 3.94 m/s | 21.1 |  | 2.55 | m/s |  | 3.94 | m/s | 10.4722 | 0.0095067 | 12.1961 |  | 2.5 | 85 | 0.085 | 143.4836 | 7.1291 | 6.4745 | 0.026741 | 31.7709 | 0.26754
2025-05-19 20:46 | 1256 | Remove | 2025-05-19 | 20:46 | ST | GS | - | 86.5 | g | 0 | 113.2 | 11.557 | 1144.7 | 62584 | 10:29 | 29 | 2.34 m/s | 23.3 | 30.1 | 3.76 m/s | 18.5 |  | 2.34 | m/s |  | 3.76 | m/s | 10.4806 | 0.0095392 | 12.2056 |  | 1.5 | 86.5 | 0.0865 | 141.1057 | 6.6979 | 5.646 | 0.023054 | 31.794 | 0.27206
2025-05-19 20:46 | 1257 | Remove | 2025-05-19 | 20:46 | US | GS | - | 91 | g | 0 | 113.2 | 11.557 | 1144.9 | 62593 | 10:29 | 29 | 2.48 m/s | 23.1 | 30.1 | 3.84 m/s | 17.9 |  | 2.48 | m/s |  | 3.84 | m/s | 10.4889 | 0.0095408 | 12.2152 |  | 4.5 | 91 | 0.091 | 134.2328 | 6.6404 | 5.4629 | 0.024224 | 31.8182 | 0.286
2025-05-19 20:47 | 1258 | Remove | 2025-05-19 | 20:47 | ST | GS | - | 84.5 | g | 0 | 113.2 | 11.541 | 1142.8 | 62603 | 10:30 | 29 | 2.38 m/s | 24.2 | 30.1 | 3.81 m/s | 17.7 |  | 2.38 | m/s |  | 3.81 | m/s | 10.4975 | 0.0095233 | 12.2247 |  | -6.5 | 84.5 | 0.0845 | 144.6711 | 6.9566 | 5.4019 | 0.024354 | 31.8426 | 0.26537
2025-05-19 20:47 | 1259 | Remove | 2025-05-19 | 20:47 | ST | GS | - | 90 | g | 0 | 113.2 | 11.532 | 1141.9 | 62612 | 10:30 | 29 | 2.65 m/s | 25.7 | 30.1 | 3.86 m/s | 20.6 |  | 2.65 | m/s |  | 3.86 | m/s | 10.5058 | 0.0095158 | 12.2342 |  | 5.5 | 90 | 0.09 | 135.9358 | 7.3878 | 6.2869 | 0.028798 | 31.8714 | 0.28239
2025-05-19 20:48 | 1260 | Remove | 2025-05-19 | 20:48 | ST | GS | - | 82 | g | 0 | 113.3 | 11.52 | 1140.5 | 62622 | 10:31 | 29 | 2.31 m/s | 25.2 | 30.1 | 3.96 m/s | 18.5 |  | 2.31 | m/s |  | 3.96 | m/s | 10.5142 | 0.0095042 | 12.2437 |  | -8 | 82 | 0.082 | 149.3137 | 7.244 | 5.646 | 0.024615 | 31.896 | 0.25709
2025-05-19 20:48 | 1261 | Keep | 2025-05-19 | 20:48 | US | GS | - | 93 | g | 0 | 113.2 | 11.561 | 1145.1 | 62631 | 10:31 | 29 | 2.4 m/s | 23.2 | 30.1 | 3.79 m/s | 20.2 |  | 2.4 | m/s |  | 3.79 | m/s | 10.5225 | 0.0095425 | 12.2533 |  | 11 | 93 | 0.093 | 131.7556 | 6.6691 | 6.1649 | 0.023544 | 31.9195 | 0.29136
2025-05-19 20:49 | 1262 | Remove | 2025-05-19 | 20:49 | US | GS | - | 87.5 | g | 0 | 113.3 | 11.53 | 1141.8 | 62641 | 10:32 | 29 | 2.38 m/s | 24 | 30.1 | 3.88 m/s | 19.6 |  | 2.38 | m/s |  | 3.88 | m/s | 10.5308 | 0.009515 | 12.2628 |  | -5.5 | 87.5 | 0.0875 | 140.1461 | 6.8991 | 5.9817 | 0.024153 | 31.9437 | 0.27392
2025-05-19 20:49 | 1263 | Remove | 2025-05-19 | 20:49 | US | GS | - | 94 | g | 0 | 113.3 | 11.536 | 1143 | 62651 | 10:32 | 29 | 2.19 m/s | 24.5 | 30.1 | 3.92 m/s | 19 |  | 2.19 | m/s |  | 3.92 | m/s | 10.5392 | 0.009525 | 12.2723 |  | 6.5 | 94 | 0.094 | 130.5565 | 7.0428 | 5.7986 | 0.022688 | 31.9664 | 0.29406
2025-05-19 20:50 | 1264 | Remove | 2025-05-19 | 20:50 | US | GS | - | 82 | g | 0 | 113.3 | 11.539 | 1142.7 | 62660 | 10:33 | 29 | 2.2 m/s | 23.3 | 30.1 | 3.85 m/s | 18.5 |  | 2.2 | m/s |  | 3.85 | m/s | 10.5475 | 0.0095225 | 12.2818 |  | -12 | 82 | 0.082 | 149.7784 | 6.6979 | 5.646 | 0.021675 | 31.988 | 0.25635
2025-05-19 20:50 | 1265 | Remove | 2025-05-19 | 20:50 | ST | GS | - | 84 | g | 0 | 113.3 | 11.508 | 1138.4 | 62670 | 10:33 | 29 | 2.25 m/s | 24.2 | 30.1 | 4.13 m/s | 18.4 |  | 2.25 | m/s |  | 4.13 | m/s | 10.5558 | 0.0094867 | 12.2913 |  | 2 | 84 | 0.084 | 146.3252 | 6.9566 | 5.6155 | 0.023024 | 32.0111 | 0.26241
2025-05-19 20:51 | 1266 | Remove | 2025-05-19 | 20:51 | US | GS | - | 93.5 | g | 0 | 113.2 | 11.554 | 1144.1 | 62679 | 10:34 | 29 | 2.68 m/s | 23.9 | 30.1 | 3.8 m/s | 20.6 |  | 2.68 | m/s |  | 3.8 | m/s | 10.5642 | 0.0095342 | 12.3009 |  | 9.5 | 93.5 | 0.0935 | 131.5599 | 6.8703 | 6.2869 | 0.027084 | 32.0381 | 0.29184
2025-05-19 20:51 | 1267 | Remove | 2025-05-19 | 20:51 | US | GS | - | 92 | g | 0 | 113.2 | 11.527 | 1141.2 | 62689 | 10:34 | 29 | 2.52 m/s | 25.4 | 30.1 | 4.01 m/s | 17.8 |  | 2.52 | m/s |  | 4.01 | m/s | 10.5725 | 0.00951 | 12.3104 |  | -1.5 | 92 | 0.092 | 133.8083 | 7.3015 | 5.4324 | 0.027066 | 32.0652 | 0.28692
2025-05-19 20:52 | 1268 | Remove | 2025-05-19 | 20:52 | ST | GS | - | 83 | g | 0 | 113.1 | 11.517 | 1140.5 | 62698 | 10:35 | 29 | 2.34 m/s | 23.6 | 30.1 | 4.13 m/s | 19 |  | 2.34 | m/s |  | 4.13 | m/s | 10.5808 | 0.0095042 | 12.3199 |  | -9 | 83 | 0.083 | 148.4321 | 6.7841 | 5.7986 | 0.023351 | 32.0886 | 0.25866
2025-05-19 20:52 | 1269 | Remove | 2025-05-19 | 20:52 | ST | GS | - | 81.5 | g | 0 | 113.3 | 11.511 | 1139.5 | 62708 | 10:35 | 29 | 2.35 m/s | 24.4 | 30.1 | 3.93 m/s | 20 |  | 2.35 | m/s |  | 3.93 | m/s | 10.5892 | 0.0094958 | 12.3294 |  | -1.5 | 81.5 | 0.0815 | 151.2805 | 7.0141 | 6.1038 | 0.024246 | 32.1128 | 0.25379
2025-05-19 20:53 | 1270 | Remove | 2025-05-19 | 20:53 | ST | GS | - | 85.5 | g | 0 | 113.3 | 11.532 | 1142.2 | 62717 | 10:36 | 29 | 2.47 m/s | 24.4 | 30.1 | 4.1 m/s | 18.8 |  | 2.47 | m/s |  | 4.1 | m/s | 10.5975 | 0.0095183 | 12.3389 |  | 4 | 85.5 | 0.0855 | 144.3144 | 7.0141 | 5.7376 | 0.025484 | 32.1383 | 0.26604
2025-05-19 20:53 | 1271 | Remove | 2025-05-19 | 20:53 | ST | GS | - | 83 | g | 0 | 113.3 | 11.52 | 1140.6 | 62727 | 10:36 | 29 | 2.12 m/s | 23.8 | 30.1 | 4.07 m/s | 18.4 |  | 2.12 | m/s |  | 4.07 | m/s | 10.6058 | 0.009505 | 12.3484 |  | -2.5 | 83 | 0.083 | 148.7757 | 6.8416 | 5.6155 | 0.021335 | 32.1596 | 0.25809
2025-05-19 20:54 | 1272 | Remove | 2025-05-19 | 20:54 | US | GS | - | 86.5 | g | 0 | 113.4 | 11.504 | 1138.7 | 62736 | 10:37 | 29 | 2.31 m/s | 24.8 | 30.1 | 3.88 m/s | 18.3 |  | 2.31 | m/s |  | 3.88 | m/s | 10.6142 | 0.0094892 | 12.3579 |  | 3.5 | 86.5 | 0.0865 | 142.8656 | 7.1291 | 5.585 | 0.024224 | 32.1838 | 0.26877
2025-05-19 20:54 | 1273 | Remove | 2025-05-19 | 20:54 | US | GS | - | 82.5 | g | 0 | 113.3 | 11.521 | 1140.1 | 62746 | 10:37 | 29 | 2.31 m/s | 24.8 | 30.1 | 3.92 m/s | 19.1 |  | 2.31 | m/s |  | 3.92 | m/s | 10.6225 | 0.0095008 | 12.3674 |  | -4 | 82.5 | 0.0825 | 149.9076 | 7.1291 | 5.8292 | 0.024224 | 32.2081 | 0.25615
2025-05-19 20:55 | 1274 | Remove | 2025-05-19 | 20:55 | ST | GS | - | 82 | g | 0 | 113.3 | 11.526 | 1140.7 | 62755 | 10:38 | 29 | 2.25 m/s | 22.9 | 30.1 | 3.94 m/s | 19.5 |  | 2.25 | m/s |  | 3.94 | m/s | 10.6308 | 0.0095058 | 12.3769 |  | -0.5 | 82 | 0.082 | 150.9376 | 6.5829 | 5.9512 | 0.021787 | 32.2299 | 0.25442
2025-05-19 20:55 | 1275 | Remove | 2025-05-19 | 20:55 | ST | GS | - | 82.5 | g | 0 | 113.3 | 11.503 | 1137.7 | 62765 | 10:38 | 29 | 2.05 m/s | 24.5 | 30.1 | 4.09 m/s | 19.2 |  | 2.05 | m/s |  | 4.09 | m/s | 10.6394 | 0.0094808 | 12.3864 |  | 0.5 | 82.5 | 0.0825 | 150.1377 | 7.0428 | 5.8597 | 0.021237 | 32.2511 | 0.25581
2025-05-19 20:56 | 1276 | Remove | 2025-05-19 | 20:56 | US | GS | - | 91.5 | g | 0 | 113.3 | 11.533 | 1141.8 | 62775 | 10:39 | 29 | 2.42 m/s | 25.6 | 30.1 | 3.9 m/s | 18.6 |  | 2.42 | m/s |  | 3.9 | m/s | 10.6478 | 0.009515 | 12.3959 |  | 9 | 91.5 | 0.0915 | 135.4741 | 7.359 | 5.6766 | 0.026196 | 32.2773 | 0.28348
2025-05-19 20:56 | 1277 | Remove | 2025-05-19 | 20:56 | US | GS | - | 84 | g | 0 | 113.3 | 11.533 | 1141.9 | 62784 | 10:39 | 29 | 2.48 m/s | 23.9 | 30.1 | 3.98 m/s | 18.7 |  | 2.48 | m/s |  | 3.98 | m/s | 10.6561 | 0.0095158 | 12.4054 |  | -7.5 | 84 | 0.084 | 147.6833 | 6.8703 | 5.7071 | 0.025063 | 32.3024 | 0.26004
2025-05-19 20:57 | 1278 | Remove | 2025-05-19 | 20:57 | ST | GS | - | 82.5 | g | 0 | 113.3 | 11.506 | 1137.8 | 62793 | 10:40 | 29 | 2.09 m/s | 23.2 | 30.1 | 3.81 m/s | 18 |  | 2.09 | m/s |  | 3.81 | m/s | 10.6644 | 0.0094817 | 12.4149 |  | -1.5 | 82.5 | 0.0825 | 150.4833 | 6.6691 | 5.4934 | 0.020503 | 32.3229 | 0.25524
2025-05-19 20:57 | 1279 | Remove | 2025-05-19 | 20:57 | ST | GS | - | 83 | g | 0 | 113.4 | 11.503 | 1138.1 | 62803 | 10:40 | 29 | 2.15 m/s | 24 | 30.1 | 3.97 m/s | 18.4 |  | 2.15 | m/s |  | 3.97 | m/s | 10.6728 | 0.0094842 | 12.4244 |  | 0.5 | 83 | 0.083 | 149.6911 | 6.8991 | 5.6155 | 0.021819 | 32.3447 | 0.25661
2025-05-19 20:58 | 1280 | Remove | 2025-05-19 | 20:58 | ST | GS | - | 82.5 | g | 0 | 113.5 | 11.496 | 1137.6 | 62812 | 10:41 | 29 | 2.27 m/s | 23.6 | 30.1 | 4.01 m/s | 19.3 |  | 2.27 | m/s |  | 4.01 | m/s | 10.6811 | 0.00948 | 12.4338 |  | -0.5 | 82.5 | 0.0825 | 150.7132 | 6.7841 | 5.8902 | 0.022653 | 32.3673 | 0.25489
2025-05-19 20:58 | 1281 | Remove | 2025-05-19 | 20:58 | US | GS | - | 85 | g | 0 | 113.4 | 11.476 | 1134.6 | 62822 | 10:41 | 29 | 2.27 m/s | 27.6 | 30.1 | 3.93 m/s | 20 |  | 2.27 | m/s |  | 3.93 | m/s | 10.6894 | 0.009455 | 12.4433 |  | 2.5 | 85 | 0.085 | 146.3917 | 7.934 | 6.1038 | 0.026492 | 32.3938 | 0.2624
2025-05-19 20:59 | 1282 | Remove | 2025-05-19 | 20:59 | US | GS | - | 81.5 | g | 0 | 113.4 | 11.495 | 1136.8 | 62832 | 10:42 | 28.9 | 2.26 m/s | 27.1 | 30.1 | 4.18 m/s | 20.2 |  | 2.26 | m/s |  | 4.18 | m/s | 10.6978 | 0.0094733 | 12.4528 |  | -3.5 | 81.5 | 0.0815 | 152.7947 | 7.7478 | 6.1649 | 0.025757 | 32.4196 | 0.25139
2025-05-19 20:59 | 1283 | Remove | 2025-05-19 | 20:59 | US | GS | - | 86.5 | g | 0 | 113.4 | 11.51 | 1139.3 | 62841 | 10:42 | 28.9 | 2.32 m/s | 24.4 | 30.1 | 3.88 m/s | 19.7 |  | 2.32 | m/s |  | 3.88 | m/s | 10.7061 | 0.0094942 | 12.4623 |  | 5 | 86.5 | 0.0865 | 144.0724 | 6.9758 | 6.0123 | 0.023806 | 32.4434 | 0.26662
2025-05-19 21:00 | 1284 | Remove | 2025-05-19 | 21:00 | ST | GS | - | 82.5 | g | 0 | 113.5 | 11.487 | 1135.8 | 62851 | 10:43 | 28.9 | 2.01 m/s | 25.6 | 30.1 | 3.96 m/s | 19.3 |  | 2.01 | m/s |  | 3.96 | m/s | 10.7144 | 0.009465 | 12.4717 |  | -4 | 82.5 | 0.0825 | 151.1724 | 7.3189 | 5.8902 | 0.021639 | 32.465 | 0.25412
2025-05-19 21:00 | 1285 | Remove | 2025-05-19 | 21:00 | ST | GS | - | 82.5 | g | 0 | 113.3 | 11.503 | 1137.3 | 62860 | 10:43 | 28.9 | 2.16 m/s | 24.1 | 30.1 | 3.94 m/s | 19.7 |  | 2.16 | m/s |  | 3.94 | m/s | 10.7228 | 0.0094775 | 12.4812 |  | 0 | 82.5 | 0.0825 | 151.2873 | 6.8901 | 6.0123 | 0.021892 | 32.4869 | 0.25395
2025-05-19 21:01 | 1286 | Remove | 2025-05-19 | 21:01 | ST | GS | - | 85 | g | 0 | 113.4 | 11.492 | 1136.8 | 62870 | 10:44 | 28.9 | 2.18 m/s | 25.7 | 30.1 | 4.3 m/s | 19.7 |  | 2.18 | m/s |  | 4.3 | m/s | 10.7311 | 0.0094733 | 12.4907 |  | 2.5 | 85 | 0.085 | 146.9491 | 7.3475 | 6.0123 | 0.023561 | 32.5105 | 0.26145
2025-05-19 21:01 | 1287 | Remove | 2025-05-19 | 21:01 | ST | GS | - | 81.5 | g | 0 | 113.3 | 11.484 | 1135.2 | 62879 | 10:44 | 28.9 | 2.09 m/s | 24.2 | 30.1 | 3.94 m/s | 18.3 |  | 2.09 | m/s |  | 3.94 | m/s | 10.7394 | 0.00946 | 12.5001 |  | -3.5 | 81.5 | 0.0815 | 153.3759 | 6.9187 | 5.585 | 0.02127 | 32.5317 | 0.25052
2025-05-19 21:02 | 1288 | Remove | 2025-05-19 | 21:02 | ST | GS | - | 82 | g | 0 | 113.4 | 11.474 | 1134 | 62888 | 10:45 | 28.9 | 2.18 m/s | 25 | 30.1 | 4.63 m/s | 19.2 |  | 2.18 | m/s |  | 4.63 | m/s | 10.7478 | 0.00945 | 12.5096 |  | 0.5 | 82 | 0.082 | 152.5559 | 7.1474 | 5.8597 | 0.02292 | 32.5547 | 0.25188
2025-05-19 21:02 | 1289 | Remove | 2025-05-19 | 21:02 | ST | GS | - | 86.5 | g | 0 | 113.3 | 11.516 | 1139.1 | 62898 | 10:45 | 28.9 | 2.31 m/s | 23.8 | 30.1 | 4.04 m/s | 18.6 |  | 2.31 | m/s |  | 4.04 | m/s | 10.7561 | 0.0094925 | 12.5191 |  | 4.5 | 86.5 | 0.0865 | 144.7292 | 6.8043 | 5.6766 | 0.023121 | 32.5778 | 0.26552
2025-05-19 21:03 | 1290 | Remove | 2025-05-19 | 21:03 | ST | GS | - | 83 | g | 0 | 113.3 | 11.487 | 1135.5 | 62907 | 10:46 | 28.9 | 2.2 m/s | 26.5 | 30.1 | 3.96 m/s | 17.6 |  | 2.2 | m/s |  | 3.96 | m/s | 10.7644 | 0.0094625 | 12.5285 |  | -3.5 | 83 | 0.083 | 150.9463 | 7.5762 | 5.3714 | 0.024518 | 32.6023 | 0.25458
2025-05-19 21:03 | 1291 | Keep | 2025-05-19 | 21:03 | ST | GS | - | 84 | g | 0 | 113.4 | 11.474 | 1133.8 | 62917 | 10:46 | 28.9 | 2.11 m/s | 25.1 | 30.1 | 4.1 m/s | 19.5 |  | 2.11 | m/s |  | 4.1 | m/s | 10.7728 | 0.0094483 | 12.538 |  | 1 | 84 | 0.084 | 149.2618 | 7.176 | 5.9512 | 0.022272 | 32.6246 | 0.25747
2025-05-19 21:04 | 1292 | Remove | 2025-05-19 | 21:04 | ST | GS | - | 83.5 | g | 0 | 113.4 | 11.483 | 1135.8 | 62927 | 10:47 | 28.9 | 2.26 m/s | 24 | 30.1 | 4.0 m/s | 19.5 |  | 2.26 | m/s |  | 4 | m/s | 10.7814 | 0.009465 | 12.5475 |  | -0.5 | 83.5 | 0.0835 | 150.2689 | 6.8615 | 5.9512 | 0.02281 | 32.6474 | 0.25576
2025-05-19 21:04 | 1293 | Remove | 2025-05-19 | 21:04 | ST | GS | - | 82.5 | g | 0 | 113.4 | 11.493 | 1137 | 62936 | 10:47 | 28.9 | 2.12 m/s | 23.5 | 30.1 | 3.97 m/s | 19.2 |  | 2.12 | m/s |  | 3.97 | m/s | 10.7897 | 0.009475 | 12.5569 |  | -1 | 82.5 | 0.0825 | 152.2052 | 6.7185 | 5.8597 | 0.020951 | 32.6683 | 0.25254
2025-05-19 21:05 | 1294 | Remove | 2025-05-19 | 21:05 | ST | GS | - | 83 | g | 0 | 113.4 | 11.484 | 1135.9 | 62945 | 10:48 | 28.9 | 2.22 m/s | 25 | 30.1 | 4.0 m/s | 21 |  | 2.22 | m/s |  | 4 | m/s | 10.7983 | 0.0094658 | 12.5664 |  | 0.5 | 83 | 0.083 | 151.4024 | 7.1474 | 6.409 | 0.02334 | 32.6917 | 0.25389
2025-05-19 21:05 | 1295 | Remove | 2025-05-19 | 21:05 | US | GS | - | 89 | g | 0 | 113.4 | 11.484 | 1135.5 | 62955 | 10:48 | 28.9 | 2.48 m/s | 25.9 | 30.1 | 4.09 m/s | 19.8 |  | 2.48 | m/s |  | 4.09 | m/s | 10.8067 | 0.0094625 | 12.5759 |  | 6 | 89 | 0.089 | 141.3018 | 7.4047 | 6.0428 | 0.027012 | 32.7187 | 0.27202
2025-05-19 21:06 | 1296 | Remove | 2025-05-19 | 21:06 | ST | GS | - | 86 | g | 0 | 113.4 | 11.503 | 1138.7 | 62964 | 10:49 | 28.9 | 2.25 m/s | 24.2 | 30.1 | 4.03 m/s | 19.5 |  | 2.25 | m/s |  | 4.03 | m/s | 10.815 | 0.0094892 | 12.5853 |  | -3 | 86 | 0.086 | 146.3413 | 6.9187 | 5.9512 | 0.022899 | 32.7416 | 0.26266
2025-05-19 21:06 | 1297 | Remove | 2025-05-19 | 21:06 | ST | GS | - | 86.5 | g | 0 | 113.3 | 11.513 | 1138.9 | 62974 | 10:49 | 28.9 | 2.45 m/s | 23.4 | 30.1 | 4.0 m/s | 17.7 |  | 2.45 | m/s |  | 4 | m/s | 10.8233 | 0.0094908 | 12.5948 |  | 0.5 | 86.5 | 0.0865 | 145.6051 | 6.69 | 5.4019 | 0.02411 | 32.7657 | 0.264
2025-05-19 21:07 | 1298 | Remove | 2025-05-19 | 21:07 | ST | GS | - | 83.5 | g | 0 | 113.4 | 11.48 | 1135.2 | 62984 | 10:50 | 28.9 | 2.35 m/s | 23.8 | 30.1 | 4.12 m/s | 18.7 |  | 2.35 | m/s |  | 4.12 | m/s | 10.8317 | 0.00946 | 12.6043 |  | -3 | 83.5 | 0.0835 | 150.9497 | 6.8043 | 5.7071 | 0.023521 | 32.7892 | 0.25466
2025-05-19 21:07 | 1299 | Remove | 2025-05-19 | 21:07 | US | GS | - | 85.5 | g | 0 | 113.4 | 11.508 | 1139 | 62993 | 10:50 | 28.9 | 2.41 m/s | 23.4 | 30.1 | 4.0 m/s | 19.1 |  | 2.41 | m/s |  | 4 | m/s | 10.84 | 0.0094917 | 12.6138 |  | 2 | 85.5 | 0.0855 | 147.5297 | 6.69 | 5.8292 | 0.023716 | 32.8129 | 0.26057
2025-05-19 21:08 | 1300 | Remove | 2025-05-19 | 21:08 | ST | GS | - | 89 | g | 0 | 113.4 | 11.475 | 1134.9 | 63003 | 10:51 | 28.9 | 2.4 m/s | 24 | 30.1 | 3.96 m/s | 18.9 |  | 2.4 | m/s |  | 3.96 | m/s | 10.8483 | 0.0094575 | 12.6232 |  | 3.5 | 89 | 0.089 | 141.8343 | 6.8615 | 5.7681 | 0.024223 | 32.8372 | 0.27103
2025-05-19 21:08 | 1301 | Remove | 2025-05-19 | 21:08 | ST | GS | - | 87 | g | 0 | 113.4 | 11.5 | 1138.3 | 63012 | 10:51 | 28.9 | 2.51 m/s | 25 | 30.1 | 4.01 m/s | 17.6 |  | 2.51 | m/s |  | 4.01 | m/s | 10.8567 | 0.0094858 | 12.6327 |  | -2 | 87 | 0.087 | 145.2038 | 7.1474 | 5.3714 | 0.026389 | 32.8635 | 0.26473
2025-05-19 21:09 | 1302 | Remove | 2025-05-19 | 21:09 | US | GS | - | 90 | g | 0 | 113.4 | 11.491 | 1136.4 | 63022 | 10:52 | 28.9 | 2.27 m/s | 24.4 | 30.1 | 3.94 m/s | 18.4 |  | 2.27 | m/s |  | 3.94 | m/s | 10.865 | 0.00947 | 12.6422 |  | 3 | 90 | 0.09 | 140.4689 | 6.9758 | 5.6155 | 0.023293 | 32.8868 | 0.27367
2025-05-19 21:09 | 1303 | Remove | 2025-05-19 | 21:09 | ST | GS | - | 88 | g | 0 | 113.4 | 11.499 | 1138 | 63031 | 10:52 | 28.9 | 2.33 m/s | 24.3 | 30.1 | 3.86 m/s | 18.7 |  | 2.33 | m/s |  | 3.86 | m/s | 10.8733 | 0.0094833 | 12.6517 |  | -2 | 88 | 0.088 | 143.7692 | 6.9473 | 5.7071 | 0.023811 | 32.9107 | 0.26739
2025-05-19 21:10 | 1304 | Remove | 2025-05-19 | 21:10 | ST | GS | - | 85.5 | g | 0 | 113.5 | 11.482 | 1134.9 | 63040 | 10:53 | 28.9 | 2.25 m/s | 24.6 | 30.1 | 4.06 m/s | 18.8 |  | 2.25 | m/s |  | 4.06 | m/s | 10.8817 | 0.0094575 | 12.6611 |  | -2.5 | 85.5 | 0.0855 | 148.0836 | 7.033 | 5.7376 | 0.023277 | 32.9339 | 0.25961
2025-05-19 21:10 | 1305 | Remove | 2025-05-19 | 21:10 | ST | GS | - | 84.5 | g | 0 | 113.5 | 11.487 | 1136 | 63050 | 10:53 | 28.9 | 2.25 m/s | 24.7 | 30.1 | 4.18 m/s | 19.3 |  | 2.25 | m/s |  | 4.18 | m/s | 10.89 | 0.0094667 | 12.6706 |  | -1 | 84.5 | 0.0845 | 149.9481 | 7.0616 | 5.8902 | 0.023372 | 32.9573 | 0.25639
2025-05-19 21:11 | 1306 | Remove | 2025-05-19 | 21:11 | ST | GS | - | 84 | g | 0 | 113.5 | 11.438 | 1130.5 | 63059 | 10:54 | 28.9 | 2.2 m/s | 26.1 | 30.1 | 4.06 m/s | 18.4 |  | 2.2 | m/s |  | 4.06 | m/s | 10.8983 | 0.0094208 | 12.68 |  | -0.5 | 84 | 0.084 | 150.9528 | 7.4619 | 5.6155 | 0.024148 | 32.9814 | 0.25469
2025-05-19 21:11 | 1307 | Remove | 2025-05-19 | 21:11 | ST | GS | - | 87 | g | 0 | 113.5 | 11.481 | 1136.2 | 63069 | 10:54 | 28.9 | 2.48 m/s | 25.2 | 30.1 | 4.0 m/s | 18.7 |  | 2.48 | m/s |  | 4 | m/s | 10.9067 | 0.0094683 | 12.6895 |  | 3 | 87 | 0.087 | 145.8563 | 7.2046 | 5.7071 | 0.026282 | 33.0077 | 0.26357
2025-05-19 21:12 | 1308 | Remove | 2025-05-19 | 21:12 | US | GS | - | 86.5 | g | 0 | 113.3 | 11.497 | 1137.1 | 63078 | 10:55 | 28.9 | 2.25 m/s | 24.4 | 30.1 | 4.03 m/s | 19 |  | 2.25 | m/s |  | 4.03 | m/s | 10.915 | 0.0094758 | 12.699 |  | -0.5 | 86.5 | 0.0865 | 146.809 | 6.9758 | 5.7986 | 0.023088 | 33.0308 | 0.26188
2025-05-19 21:12 | 1309 | Remove | 2025-05-19 | 21:12 | ST | GS | - | 85.5 | g | 0 | 113.6 | 11.464 | 1134 | 63088 | 10:55 | 28.9 | 2.12 m/s | 24.1 | 30.1 | 3.98 m/s | 18.8 |  | 2.12 | m/s |  | 3.98 | m/s | 10.9236 | 0.00945 | 12.7084 |  | -1 | 85.5 | 0.0855 | 148.6366 | 6.8901 | 5.7376 | 0.021486 | 33.0523 | 0.25868
2025-05-19 21:13 | 1310 | Remove | 2025-05-19 | 21:13 | ST | GS | - | 84 | g | 0 | 113.5 | 11.469 | 1134.5 | 63097 | 10:56 | 28.9 | 2.09 m/s | 25 | 30.1 | 4.03 m/s | 18.5 |  | 2.09 | m/s |  | 4.03 | m/s | 10.9319 | 0.0094542 | 12.7179 |  | -1.5 | 84 | 0.084 | 151.4033 | 7.1474 | 5.646 | 0.021973 | 33.0743 | 0.25397
2025-05-19 21:13 | 1311 | Remove | 2025-05-19 | 21:13 | ST | GS | - | 87.5 | g | 0 | 113.5 | 11.481 | 1135.5 | 63107 | 10:56 | 28.9 | 2.33 m/s | 25.8 | 30.1 | 4.0 m/s | 19.6 |  | 2.33 | m/s |  | 4 | m/s | 10.9403 | 0.0094625 | 12.7273 |  | 3.5 | 87.5 | 0.0875 | 145.4554 | 7.3761 | 5.9817 | 0.02528 | 33.0996 | 0.26435
2025-05-19 21:14 | 1312 | Remove | 2025-05-19 | 21:14 | ST | GS | - | 88 | g | 0 | 113.5 | 11.457 | 1132.6 | 63116 | 10:57 | 28.9 | 2.31 m/s | 27 | 30.1 | 4.09 m/s | 20.2 |  | 2.31 | m/s |  | 4.09 | m/s | 10.9486 | 0.0094383 | 12.7368 |  | 0.5 | 88 | 0.088 | 144.7362 | 7.7192 | 6.1649 | 0.026229 | 33.1258 | 0.26565
2025-05-19 21:14 | 1313 | Remove | 2025-05-19 | 21:14 | ST | GS | - | 86.5 | g | 0 | 113.6 | 11.492 | 1136.6 | 63126 | 10:57 | 28.9 | 2.35 m/s | 24.5 | 30.1 | 4.09 m/s | 20.2 |  | 2.35 | m/s |  | 4.09 | m/s | 10.9569 | 0.0094717 | 12.7463 |  | -1.5 | 86.5 | 0.0865 | 147.3555 | 7.0044 | 6.1649 | 0.024213 | 33.15 | 0.26094
2025-05-19 21:15 | 1314 | Remove | 2025-05-19 | 21:15 | ST | GS | - | 87 | g | 0 | 113.5 | 11.49 | 1137.4 | 63135 | 10:58 | 28.9 | 2.25 m/s | 23.2 | 30.1 | 3.94 m/s | 17.6 |  | 2.25 | m/s |  | 3.94 | m/s | 10.9653 | 0.0094783 | 12.7557 |  | 0.5 | 87 | 0.087 | 146.6176 | 6.6328 | 5.3714 | 0.021952 | 33.172 | 0.26227
2025-05-19 21:15 | 1315 | Remove | 2025-05-19 | 21:15 | ST | GS | - | 85 | g | 0 | 113.5 | 11.445 | 1131.6 | 63145 | 10:58 | 28.9 | 2.19 m/s | 27 | 30.1 | 4.03 m/s | 18.8 |  | 2.19 | m/s |  | 4.03 | m/s | 10.9736 | 0.00943 | 12.7652 |  | -2 | 85 | 0.085 | 150.1784 | 7.7192 | 5.7376 | 0.024867 | 33.1968 | 0.25605
2025-05-19 21:16 | 1316 | Remove | 2025-05-19 | 21:16 | ST | GS | - | 88 | g | 0 | 113.4 | 11.486 | 1135.7 | 63154 | 10:59 | 28.9 | 2.37 m/s | 24.7 | 30.1 | 4.21 m/s | 20.6 |  | 2.37 | m/s |  | 4.21 | m/s | 10.9819 | 0.0094642 | 12.7746 |  | 3 | 88 | 0.088 | 145.1662 | 7.0616 | 6.2869 | 0.024618 | 33.2214 | 0.26489
2025-05-19 21:16 | 1317 | Remove | 2025-05-19 | 21:16 | ST | GS | - | 84.5 | g | 0 | 113.6 | 11.445 | 1131.8 | 63164 | 10:59 | 28.9 | 2.12 m/s | 23.7 | 30.1 | 4.01 m/s | 18.1 |  | 2.12 | m/s |  | 4.01 | m/s | 10.9903 | 0.0094317 | 12.7841 |  | -3.5 | 84.5 | 0.0845 | 151.2906 | 6.7757 | 5.524 | 0.02113 | 33.2426 | 0.25419
2025-05-19 21:17 | 1318 | Remove | 2025-05-19 | 21:17 | ST | GS | - | 87 | g | 0 | 113.6 | 11.464 | 1133.2 | 63173 | 11:00 | 28.9 | 2.26 m/s | 25 | 30.1 | 4.09 m/s | 20.2 |  | 2.26 | m/s |  | 4.09 | m/s | 10.9986 | 0.0094433 | 12.7935 |  | 2.5 | 87 | 0.087 | 147.0517 | 7.1474 | 6.1649 | 0.023761 | 33.2663 | 0.26153
2025-05-19 21:17 | 1319 | Remove | 2025-05-19 | 21:17 | US | GS | - | 91 | g | 0 | 113.5 | 11.49 | 1137.3 | 63183 | 11:00 | 28.9 | 2.37 m/s | 24.2 | 30.1 | 3.96 m/s | 19.1 |  | 2.37 | m/s |  | 3.96 | m/s | 11.0069 | 0.0094775 | 12.803 |  | 4 | 91 | 0.091 | 140.6921 | 6.9187 | 5.8292 | 0.02412 | 33.2904 | 0.27335
2025-05-19 21:18 | 1320 | Remove | 2025-05-19 | 21:18 | ST | GS | - | 86 | g | 0 | 113.5 | 11.442 | 1131.2 | 63192 | 11:01 | 28.9 | 2.13 m/s | 25 | 30.1 | 3.92 m/s | 19 |  | 2.13 | m/s |  | 3.92 | m/s | 11.0153 | 0.0094267 | 12.8124 |  | -5 | 86 | 0.086 | 148.9815 | 7.1474 | 5.7986 | 0.022394 | 33.3128 | 0.25816
2025-05-19 21:18 | 1321 | Keep | 2025-05-19 | 21:18 | ST | GS | - | 86 | g | 0 | 113.5 | 11.464 | 1134.2 | 63202 | 11:01 | 28.9 | 2.33 m/s | 26.3 | 30.1 | 3.97 m/s | 18.9 |  | 2.33 | m/s |  | 3.97 | m/s | 11.0236 | 0.0094517 | 12.8219 |  | 0 | 86 | 0.086 | 149.0914 | 7.519 | 5.7681 | 0.02577 | 33.3386 | 0.25796
2025-05-19 21:19 | 1322 | Remove | 2025-05-19 | 21:19 | ST | GS | - | 87 | g | 0 | 113.6 | 11.472 | 1134.2 | 63211 | 11:02 | 28.9 | 2.4 m/s | 24.7 | 30.1 | 3.98 m/s | 20 |  | 2.4 | m/s |  | 3.98 | m/s | 11.0319 | 0.0094517 | 12.8313 |  | 1 | 87 | 0.087 | 147.4863 | 7.0616 | 6.1038 | 0.02493 | 33.3635 | 0.26076
2025-05-19 21:19 | 1323 | Remove | 2025-05-19 | 21:19 | ST | GS | - | 86.5 | g | 0 | 113.6 | 11.462 | 1134 | 63221 | 11:02 | 28.9 | 2.2 m/s | 24.3 | 30.1 | 4.09 m/s | 18.8 |  | 2.2 | m/s |  | 4.09 | m/s | 11.0403 | 0.00945 | 12.8408 |  | -0.5 | 86.5 | 0.0865 | 148.4481 | 6.9473 | 5.7376 | 0.022482 | 33.386 | 0.25909
2025-05-19 21:20 | 1324 | Remove | 2025-05-19 | 21:20 | ST | GS | - | 86.5 | g | 0 | 113.5 | 11.481 | 1136 | 63230 | 11:03 | 28.9 | 2.19 m/s | 23 | 30.1 | 3.97 m/s | 18 |  | 2.19 | m/s |  | 3.97 | m/s | 11.0486 | 0.0094667 | 12.8502 |  | 0 | 86.5 | 0.0865 | 148.5575 | 6.5756 | 5.4934 | 0.021183 | 33.4072 | 0.25893
2025-05-19 21:20 | 1325 | Remove | 2025-05-19 | 21:20 | ST | GS | - | 86.5 | g | 0 | 113.5 | 11.481 | 1136.1 | 63240 | 11:03 | 28.9 | 2.33 m/s | 24.4 | 30.1 | 4.0 m/s | 19.5 |  | 2.33 | m/s |  | 4 | m/s | 11.0572 | 0.0094675 | 12.8597 |  | 0 | 86.5 | 0.0865 | 148.667 | 6.9758 | 5.9512 | 0.023909 | 33.4311 | 0.25874
2025-05-19 21:21 | 1326 | Remove | 2025-05-19 | 21:21 | US | GS | - | 87.5 | g | 0 | 113.6 | 11.487 | 1136.9 | 63249 | 11:04 | 28.9 | 2.35 m/s | 24 | 30.1 | 4.01 m/s | 18.6 |  | 2.35 | m/s |  | 4.01 | m/s | 11.0656 | 0.0094742 | 12.8692 |  | 1 | 87.5 | 0.0875 | 147.0762 | 6.8615 | 5.6766 | 0.023719 | 33.4548 | 0.26155
2025-05-19 21:21 | 1327 | Remove | 2025-05-19 | 21:21 | ST | GS | - | 85.5 | g | 0 | 113.6 | 11.486 | 1135.9 | 63259 | 11:04 | 28.9 | 2.26 m/s | 23 | 30.1 | 3.96 m/s | 18.7 |  | 2.26 | m/s |  | 3.96 | m/s | 11.0739 | 0.0094658 | 12.8786 |  | -2 | 85.5 | 0.0855 | 150.6273 | 6.5756 | 5.7071 | 0.02186 | 33.4767 | 0.2554
2025-05-19 21:22 | 1328 | Remove | 2025-05-19 | 21:22 | US | GS | - | 89.5 | g | 0 | 113.6 | 11.519 | 1140.7 | 63268 | 11:05 | 28.9 | 2.31 m/s | 23.1 | 30.1 | 3.93 m/s | 17.8 |  | 2.31 | m/s |  | 3.93 | m/s | 11.0822 | 0.0095058 | 12.8881 |  | 4 | 89.5 | 0.0895 | 144.0015 | 6.6042 | 5.4324 | 0.022441 | 33.4991 | 0.26717
2025-05-19 21:22 | 1329 | Remove | 2025-05-19 | 21:22 | ST | GS | - | 85.5 | g | 0 | 113.6 | 11.485 | 1135.9 | 63278 | 11:05 | 28.9 | 2.26 m/s | 24.2 | 30.1 | 4.09 m/s | 18.7 |  | 2.26 | m/s |  | 4.09 | m/s | 11.0906 | 0.0094658 | 12.8976 |  | -4 | 85.5 | 0.0855 | 150.8492 | 6.9187 | 5.7071 | 0.023 | 33.5221 | 0.25506
2025-05-19 21:23 | 1330 | Remove | 2025-05-19 | 21:23 | US | GS | - | 85.5 | g | 0 | 113.6 | 11.463 | 1133.9 | 63287 | 11:06 | 28.9 | 2.23 m/s | 23.8 | 30.1 | 4.09 m/s | 18.8 |  | 2.23 | m/s |  | 4.09 | m/s | 11.0989 | 0.0094492 | 12.9071 |  | 0 | 85.5 | 0.0855 | 150.9597 | 6.8043 | 5.7376 | 0.02232 | 33.5445 | 0.25489
2025-05-19 21:23 | 1331 | Remove | 2025-05-19 | 21:23 | ST | GS | - | 88 | g | 0 | 113.6 | 11.493 | 1137 | 63297 | 11:06 | 28.9 | 2.3 m/s | 24.3 | 30.1 | 4.07 m/s | 17.7 |  | 2.3 | m/s |  | 4.07 | m/s | 11.1072 | 0.009475 | 12.9165 |  | 2.5 | 88 | 0.088 | 146.7787 | 6.9473 | 5.4019 | 0.023504 | 33.568 | 0.26215
2025-05-19 21:24 | 1332 | Remove | 2025-05-19 | 21:24 | US | GS | - | 88.5 | g | 0 | 113.6 | 11.502 | 1138.2 | 63306 | 11:07 | 28.9 | 2.35 m/s | 23.3 | 30.1 | 3.93 m/s | 17.6 |  | 2.35 | m/s |  | 3.93 | m/s | 11.1156 | 0.009485 | 12.926 |  | 0.5 | 88.5 | 0.0885 | 146.0566 | 6.6614 | 5.3714 | 0.023027 | 33.591 | 0.26346
2025-05-19 21:24 | 1333 | Remove | 2025-05-19 | 21:24 | US | GS | - | 87 | g | 0 | 113.6 | 11.472 | 1134.1 | 63316 | 11:07 | 28.9 | 2.42 m/s | 25.5 | 30.1 | 3.94 m/s | 18.8 |  | 2.42 | m/s |  | 3.94 | m/s | 11.1239 | 0.0094508 | 12.9355 |  | -1.5 | 87 | 0.087 | 148.6835 | 7.2903 | 5.7376 | 0.025952 | 33.6169 | 0.2588
2025-05-19 21:25 | 1334 | Remove | 2025-05-19 | 21:25 | ST | GS | - | 85.5 | g | 0 | 113.6 | 11.495 | 1138.1 | 63325 | 11:08 | 28.9 | 2.15 m/s | 22.8 | 30.1 | 4.02 m/s | 18.8 |  | 2.15 | m/s |  | 4.02 | m/s | 11.1322 | 0.0094842 | 12.9449 |  | -1.5 | 85.5 | 0.0855 | 151.4029 | 6.5184 | 5.7376 | 0.020615 | 33.6376 | 0.25418
2025-05-19 21:25 | 1335 | Remove | 2025-05-19 | 21:25 | ST | GS | - | 87 | g | 0 | 113.6 | 11.457 | 1133.1 | 63334 | 11:08 | 28.9 | 2.2 m/s | 25.1 | 30.1 | 4.0 m/s | 17.9 |  | 2.2 | m/s |  | 4 | m/s | 11.1406 | 0.0094425 | 12.9544 |  | 1.5 | 87 | 0.087 | 148.901 | 7.176 | 5.4629 | 0.023222 | 33.6608 | 0.25846
2025-05-19 21:26 | 1336 | Remove | 2025-05-19 | 21:26 | ST | GS | - | 86 | g | 0 | 113.6 | 11.473 | 1135.7 | 63344 | 11:09 | 28.9 | 2.19 m/s | 23.6 | 30.1 | 3.97 m/s | 18.2 |  | 2.19 | m/s |  | 3.97 | m/s | 11.1489 | 0.0094642 | 12.9639 |  | -1 | 86 | 0.086 | 150.7425 | 6.7471 | 5.5545 | 0.021735 | 33.6825 | 0.25533
2025-05-19 21:26 | 1337 | Remove | 2025-05-19 | 21:26 | ST | GS | - | 87.5 | g | 0 | 113.6 | 11.481 | 1136.8 | 63354 | 11:09 | 28.9 | 2.16 m/s | 22.2 | 30.1 | 3.96 m/s | 17.6 |  | 2.16 | m/s |  | 3.96 | m/s | 11.1572 | 0.0094733 | 12.9733 |  | 1.5 | 87.5 | 0.0875 | 148.2666 | 6.3469 | 5.3714 | 0.020166 | 33.7027 | 0.25962
2025-05-19 21:27 | 1338 | Remove | 2025-05-19 | 21:27 | ST | GS | - | 87 | g | 0 | 113.6 | 11.482 | 1136.4 | 63363 | 11:10 | 28.9 | 2.42 m/s | 23.6 | 30.1 | 3.92 m/s | 18.4 |  | 2.42 | m/s |  | 3.92 | m/s | 11.1656 | 0.00947 | 12.9828 |  | -0.5 | 87 | 0.087 | 149.2276 | 6.7471 | 5.6155 | 0.024018 | 33.7267 | 0.25796
2025-05-19 21:27 | 1339 | Remove | 2025-05-19 | 21:27 | US | GS | - | 91 | g | 0 | 113.6 | 11.485 | 1136.7 | 63373 | 11:10 | 28.9 | 2.31 m/s | 26.2 | 30.1 | 4.01 m/s | 17.7 |  | 2.31 | m/s |  | 4.01 | m/s | 11.1739 | 0.0094725 | 12.9923 |  | 4 | 91 | 0.091 | 142.7722 | 7.4905 | 5.4019 | 0.025452 | 33.7521 | 0.26961
2025-05-19 21:28 | 1340 | Remove | 2025-05-19 | 21:28 | ST | GS | - | 86.5 | g | 0 | 113.6 | 11.487 | 1137.5 | 63382 | 11:11 | 28.9 | 2.12 m/s | 23.1 | 30.1 | 4.12 m/s | 18.2 |  | 2.12 | m/s |  | 4.12 | m/s | 11.1822 | 0.0094792 | 13.0018 |  | -4.5 | 86.5 | 0.0865 | 150.3092 | 6.6042 | 5.5545 | 0.020595 | 33.7727 | 0.25612
2025-05-19 21:28 | 1341 | Remove | 2025-05-19 | 21:28 | ST | GS | - | 86 | g | 0 | 113.6 | 11.494 | 1138.3 | 63392 | 11:11 | 28.9 | 2.09 m/s | 23 | 30.1 | 3.9 m/s | 17.8 |  | 2.09 | m/s |  | 3.9 | m/s | 11.1906 | 0.0094858 | 13.0112 |  | -0.5 | 86 | 0.086 | 151.2934 | 6.5756 | 5.4324 | 0.020215 | 33.793 | 0.25449
2025-05-19 21:29 | 1342 | Remove | 2025-05-19 | 21:29 | ST | GS | - | 92.5 | g | 0 | 113.6 | 11.502 | 1138.6 | 63401 | 11:12 | 28.9 | 2.42 m/s | 22.2 | 30.1 | 3.97 m/s | 17.9 |  | 2.42 | m/s |  | 3.97 | m/s | 11.1992 | 0.0094883 | 13.0207 |  | 6.5 | 92.5 | 0.0925 | 140.7646 | 6.3469 | 5.4629 | 0.022593 | 33.8155 | 0.27354
2025-05-19 21:29 | 1343 | Remove | 2025-05-19 | 21:29 | ST | GS | - | 86.5 | g | 0 | 113.5 | 11.502 | 1138.3 | 63411 | 11:12 | 28.9 | 2.31 m/s | 23.1 | 30.1 | 3.97 m/s | 17.8 |  | 2.31 | m/s |  | 3.97 | m/s | 11.2075 | 0.0094858 | 13.0302 |  | -6 | 86.5 | 0.0865 | 150.6383 | 6.6042 | 5.4324 | 0.022441 | 33.838 | 0.25563
2025-05-19 21:30 | 1344 | Remove | 2025-05-19 | 21:30 | ST | GS | - | 87 | g | 0 | 113.3 | 11.499 | 1137.7 | 63420 | 11:13 | 28.9 | 2.2 m/s | 22.5 | 30.1 | 3.97 m/s | 17.3 |  | 2.2 | m/s |  | 3.97 | m/s | 11.2158 | 0.0094808 | 13.0397 |  | 0.5 | 87 | 0.087 | 149.8815 | 6.4326 | 5.2798 | 0.020817 | 33.8588 | 0.25695
2025-05-19 21:30 | 1345 | Remove | 2025-05-19 | 21:30 | ST | GS | - | 87 | g | 0 | 113.4 | 11.442 | 1131 | 63429 | 11:13 | 28.9 | 2.11 m/s | 22.9 | 30.1 | 4.1 m/s | 17 |  | 2.11 | m/s |  | 4.1 | m/s | 11.2242 | 0.009425 | 13.0491 |  | 0 | 87 | 0.087 | 149.9898 | 6.547 | 5.1883 | 0.02032 | 33.8791 | 0.2568
2025-05-19 21:31 | 1346 | Remove | 2025-05-19 | 21:31 | ST | GS | - | 88 | g | 0 | 113.4 | 11.491 | 1136.9 | 63439 | 11:14 | 28.9 | 2.26 m/s | 22 | 30.1 | 3.94 m/s | 17.7 |  | 2.26 | m/s |  | 3.94 | m/s | 11.2325 | 0.0094742 | 13.0586 |  | 1 | 88 | 0.088 | 148.3931 | 6.2897 | 5.4019 | 0.020909 | 33.9 | 0.25959
2025-05-19 21:31 | 1347 | Remove | 2025-05-19 | 21:31 | ST | GS | - | 87 | g | 0 | 113.3 | 11.484 | 1136.1 | 63448 | 11:14 | 28.9 | 2.52 m/s | 23.1 | 30.1 | 3.9 m/s | 17.9 |  | 2.52 | m/s |  | 3.9 | m/s | 11.2408 | 0.0094675 | 13.0681 |  | -1 | 87 | 0.087 | 150.2076 | 6.6042 | 5.4629 | 0.024481 | 33.9245 | 0.25645
2025-05-19 21:32 | 1348 | Remove | 2025-05-19 | 21:32 | ST | GS | - | 86.5 | g | 0 | 113.4 | 11.467 | 1134.2 | 63458 | 11:15 | 28.9 | 2.06 m/s | 22.7 | 30.1 | 4.01 m/s | 18 |  | 2.06 | m/s |  | 4.01 | m/s | 11.2492 | 0.0094517 | 13.0775 |  | -0.5 | 86.5 | 0.0865 | 151.1851 | 6.4898 | 5.4934 | 0.019665 | 33.9442 | 0.25483
2025-05-19 21:32 | 1349 | Remove | 2025-05-19 | 21:32 | ST | GS | - | 86.5 | g | 0 | 113.5 | 11.463 | 1134 | 63468 | 11:15 | 28.9 | 2.34 m/s | 22.6 | 30.1 | 4.06 m/s | 18 |  | 2.34 | m/s |  | 4.06 | m/s | 11.2575 | 0.00945 | 13.087 |  | 0 | 86.5 | 0.0865 | 151.2943 | 6.4612 | 5.4934 | 0.02224 | 33.9664 | 0.25466
2025-05-19 21:33 | 1350 | Remove | 2025-05-19 | 21:33 | US | GS | - | 88 | g | 0 | 113.5 | 11.475 | 1134.4 | 63477 | 11:16 | 28.9 | 2.44 m/s | 22.8 | 30.1 | 4.03 m/s | 17.7 |  | 2.44 | m/s |  | 4.03 | m/s | 11.2658 | 0.0094533 | 13.0964 |  | 1.5 | 88 | 0.088 | 148.8229 | 6.5184 | 5.4019 | 0.023396 | 33.9898 | 0.2589
2025-05-19 21:33 | 1351 | Keep | 2025-05-19 | 21:33 | US | GS | - | 87 | g | 0 | 113.6 | 11.465 | 1133.5 | 63487 | 11:16 | 28.9 | 2.38 m/s | 23.7 | 30.1 | 4.12 m/s | 17.3 |  | 2.38 | m/s |  | 4.12 | m/s | 11.2742 | 0.0094458 | 13.1059 |  | -1 | 87 | 0.087 | 150.642 | 6.7757 | 5.2798 | 0.023721 | 34.0135 | 0.25578
2025-05-19 21:34 | 1352 | Remove | 2025-05-19 | 21:34 | US | GS | - | 87.5 | g | 0 | 113.5 | 11.476 | 1134.9 | 63496 | 11:17 | 28.9 | 2.25 m/s | 23.1 | 30.1 | 3.92 m/s | 16.9 |  | 2.25 | m/s |  | 3.92 | m/s | 11.2825 | 0.0094575 | 13.1153 |  | 0.5 | 87.5 | 0.0875 | 149.8893 | 6.6042 | 5.1577 | 0.021858 | 34.0354 | 0.25709
2025-05-19 21:34 | 1353 | Remove | 2025-05-19 | 21:34 | US | GS | - | 87.5 | g | 0 | 113.5 | 11.475 | 1134.3 | 63506 | 11:17 | 28.9 | 2.2 m/s | 22.8 | 30.1 | 4.04 m/s | 17.9 |  | 2.2 | m/s |  | 4.04 | m/s | 11.2908 | 0.0094525 | 13.1248 |  | 0 | 87.5 | 0.0875 | 149.9974 | 6.5184 | 5.4629 | 0.021094 | 34.0565 | 0.25693
2025-05-19 21:35 | 1354 | Remove | 2025-05-19 | 21:35 | ST | GS | - | 87.5 | g | 0 | 113.5 | 11.472 | 1135.3 | 63515 | 11:18 | 28.9 | 2.22 m/s | 23 | 30.1 | 3.97 m/s | 17.6 |  | 2.22 | m/s |  | 3.97 | m/s | 11.2992 | 0.0094608 | 13.1342 |  | 0 | 87.5 | 0.0875 | 150.1055 | 6.5756 | 5.3714 | 0.021473 | 34.078 | 0.25676
2025-05-19 21:35 | 1355 | Remove | 2025-05-19 | 21:35 | ST | GS | - | 89 | g | 0 | 113.6 | 11.455 | 1133.4 | 63524 | 11:18 | 28.9 | 2.23 m/s | 23.2 | 30.1 | 3.98 m/s | 17.1 |  | 2.23 | m/s |  | 3.98 | m/s | 11.3075 | 0.009445 | 13.1437 |  | 1.5 | 89 | 0.089 | 147.6817 | 6.6328 | 5.2188 | 0.021757 | 34.0997 | 0.261
2025-05-19 21:36 | 1356 | Remove | 2025-05-19 | 21:36 | US | GS | - | 93 | g | 0 | 113.6 | 11.461 | 1134.2 | 63534 | 11:19 | 28.9 | 2.35 m/s | 23.8 | 30.1 | 3.97 m/s | 18.4 |  | 2.35 | m/s |  | 3.97 | m/s | 11.3158 | 0.0094517 | 13.1531 |  | 4 | 93 | 0.093 | 141.4315 | 6.8043 | 5.6155 | 0.023521 | 34.1232 | 0.27254
2025-05-19 21:36 | 1357 | Remove | 2025-05-19 | 21:36 | ST | GS | - | 88.5 | g | 0 | 113.6 | 11.462 | 1133.2 | 63543 | 11:19 | 28.9 | 2.23 m/s | 23.8 | 30.1 | 3.94 m/s | 17.6 |  | 2.23 | m/s |  | 3.94 | m/s | 11.3242 | 0.0094433 | 13.1626 |  | -4.5 | 88.5 | 0.0885 | 148.7296 | 6.8043 | 5.3714 | 0.02232 | 34.1456 | 0.25918
2025-05-19 21:37 | 1358 | Remove | 2025-05-19 | 21:37 | US | GS | - | 91 | g | 0 | 113.6 | 11.48 | 1136.2 | 63553 | 11:20 | 28.9 | 2.31 m/s | 23.4 | 30.1 | 3.94 m/s | 17.3 |  | 2.31 | m/s |  | 3.94 | m/s | 11.3325 | 0.0094683 | 13.172 |  | 2.5 | 91 | 0.091 | 144.7477 | 6.69 | 5.2798 | 0.022732 | 34.1683 | 0.26633
2025-05-19 21:37 | 1359 | Remove | 2025-05-19 | 21:37 | ST | GS | - | 88.5 | g | 0 | 113.6 | 11.48 | 1135.3 | 63562 | 11:20 | 28.9 | 2.3 m/s | 23.2 | 30.1 | 3.92 m/s | 16.9 |  | 2.3 | m/s |  | 3.92 | m/s | 11.3411 | 0.0094608 | 13.1815 |  | -2.5 | 88.5 | 0.0885 | 148.9435 | 6.6328 | 5.1577 | 0.02244 | 34.1907 | 0.25884
2025-05-19 21:38 | 1360 | Remove | 2025-05-19 | 21:38 | US | GS | - | 92.5 | g | 0 | 113.7 | 11.45 | 1132.6 | 63572 | 11:21 | 28.9 | 2.34 m/s | 23.8 | 30.1 | 4.13 m/s | 18.5 |  | 2.34 | m/s |  | 4.13 | m/s | 11.3494 | 0.0094383 | 13.1909 |  | 4 | 92.5 | 0.0925 | 142.6047 | 6.8043 | 5.646 | 0.023421 | 34.2142 | 0.27036
2025-05-19 21:38 | 1361 | Remove | 2025-05-19 | 21:38 | ST | GS | - | 88.5 | g | 0 | 113.6 | 11.485 | 1135.8 | 63581 | 11:21 | 28.9 | 2.45 m/s | 22.5 | 30.1 | 3.84 m/s | 17.7 |  | 2.45 | m/s |  | 3.84 | m/s | 11.3578 | 0.009465 | 13.2004 |  | -4 | 88.5 | 0.0885 | 149.1571 | 6.4326 | 5.4019 | 0.023182 | 34.2373 | 0.25849
2025-05-19 21:39 | 1362 | Remove | 2025-05-19 | 21:39 | US | GS | - | 88.5 | g | 0 | 113.7 | 11.418 | 1128.2 | 63591 | 11:22 | 28.9 | 2.23 m/s | 27.6 | 30.1 | 4.06 m/s | 18.7 |  | 2.23 | m/s |  | 4.06 | m/s | 11.3661 | 0.0094017 | 13.2098 |  | 0 | 88.5 | 0.0885 | 149.2633 | 7.8907 | 5.7071 | 0.025884 | 34.2632 | 0.25829
2025-05-19 21:39 | 1363 | Remove | 2025-05-19 | 21:39 | US | GS | - | 90 | g | 0 | 113.6 | 11.445 | 1131.3 | 63600 | 11:22 | 28.9 | 2.47 m/s | 25.8 | 30.1 | 3.92 m/s | 18.4 |  | 2.47 | m/s |  | 3.92 | m/s | 11.3744 | 0.0094275 | 13.2192 |  | 1.5 | 90 | 0.09 | 146.8803 | 7.3761 | 5.6155 | 0.026799 | 34.29 | 0.26247
2025-05-19 21:40 | 1364 | Remove | 2025-05-19 | 21:40 | ST | GS | - | 87 | g | 0 | 113.6 | 11.438 | 1130 | 63610 | 11:23 | 28.8 | 2.27 m/s | 23.5 | 30.1 | 4.18 m/s | 18.2 |  | 2.27 | m/s |  | 4.18 | m/s | 11.3828 | 0.0094167 | 13.2286 |  | -3 | 87 | 0.087 | 152.0534 | 6.6819 | 5.5545 | 0.022311 | 34.3123 | 0.25355
2025-05-19 21:40 | 1365 | Remove | 2025-05-19 | 21:40 | US | GS | - | 89.5 | g | 0 | 113.6 | 11.423 | 1128.3 | 63619 | 11:23 | 28.8 | 2.26 m/s | 25.9 | 30.1 | 3.9 m/s | 17.8 |  | 2.26 | m/s |  | 3.9 | m/s | 11.3911 | 0.0094025 | 13.2381 |  | 2.5 | 89.5 | 0.0895 | 147.9112 | 7.3643 | 5.4324 | 0.024482 | 34.3368 | 0.26065
2025-05-19 21:41 | 1366 | Remove | 2025-05-19 | 21:41 | ST | GS | - | 95 | g | 0 | 113.6 | 11.445 | 1131.3 | 63629 | 11:24 | 28.8 | 2.4 m/s | 24.1 | 30 | 3.92 m/s | 19 |  | 2.4 | m/s |  | 3.92 | m/s | 11.3994 | 0.0094275 | 13.2475 |  | 5.5 | 95 | 0.095 | 139.4471 | 6.8525 | 5.7673 | 0.024191 | 34.361 | 0.27648
2025-05-19 21:41 | 1367 | Remove | 2025-05-19 | 21:41 | ST | GS | - | 94 | g | 0 | 113.5 | 11.461 | 1133 | 63638 | 11:24 | 28.8 | 2.19 m/s | 22.9 | 30 | 4.06 m/s | 17.3 |  | 2.19 | m/s |  | 4.06 | m/s | 11.4078 | 0.0094417 | 13.2569 |  | -1 | 94 | 0.094 | 141.0311 | 6.5113 | 5.2513 | 0.020976 | 34.382 | 0.2734
2025-05-19 21:42 | 1368 | Remove | 2025-05-19 | 21:42 | US | GS | - | 88.5 | g | 0 | 113.6 | 11.458 | 1133.1 | 63648 | 11:25 | 28.8 | 2.16 m/s | 22.8 | 30 | 4.01 m/s | 17.4 |  | 2.16 | m/s |  | 4.01 | m/s | 11.4161 | 0.0094425 | 13.2664 |  | -5.5 | 88.5 | 0.0885 | 149.9024 | 6.4829 | 5.2816 | 0.020598 | 34.4026 | 0.25725
2025-05-19 21:42 | 1369 | Remove | 2025-05-19 | 21:42 | ST | GS | - | 89.5 | g | 0 | 113.6 | 11.463 | 1133.7 | 63657 | 11:25 | 28.8 | 2.26 m/s | 22.5 | 30 | 4.01 m/s | 17 |  | 2.26 | m/s |  | 4.01 | m/s | 11.4244 | 0.0094475 | 13.2758 |  | 1 | 89.5 | 0.0895 | 148.3331 | 6.3976 | 5.1602 | 0.021268 | 34.4238 | 0.25999
2025-05-19 21:43 | 1370 | Remove | 2025-05-19 | 21:43 | ST | GS | - | 91.5 | g | 0 | 113.6 | 11.458 | 1133.8 | 63667 | 11:26 | 28.8 | 2.37 m/s | 22.2 | 30 | 3.88 m/s | 17.8 |  | 2.37 | m/s |  | 3.88 | m/s | 11.4328 | 0.0094483 | 13.2853 |  | 2 | 91.5 | 0.0915 | 145.1941 | 6.3123 | 5.403 | 0.022006 | 34.4459 | 0.26563
2025-05-19 21:43 | 1371 | Remove | 2025-05-19 | 21:43 | ST | GS | - | 88.5 | g | 0 | 113.5 | 11.442 | 1130.9 | 63676 | 11:26 | 28.8 | 2.02 m/s | 23.3 | 30 | 4.0 m/s | 18.1 |  | 2.02 | m/s |  | 4 | m/s | 11.4411 | 0.0094242 | 13.2947 |  | -3 | 88.5 | 0.0885 | 150.2224 | 6.625 | 5.4941 | 0.019685 | 34.4655 | 0.25678
2025-05-19 21:44 | 1372 | Remove | 2025-05-19 | 21:44 | ST | GS | - | 91 | g | 0 | 113.5 | 11.457 | 1132.2 | 63685 | 11:27 | 28.8 | 2.2 m/s | 23 | 30 | 4.01 m/s | 17.2 |  | 2.2 | m/s |  | 4.01 | m/s | 11.4494 | 0.009435 | 13.3041 |  | 2.5 | 91 | 0.091 | 146.1991 | 6.5397 | 5.2209 | 0.021163 | 34.4867 | 0.26387
2025-05-19 21:44 | 1373 | Remove | 2025-05-19 | 21:44 | ST | GS | - | 92 | g | 0 | 113.6 | 11.421 | 1128.5 | 63695 | 11:27 | 28.8 | 2.12 m/s | 24 | 30 | 4.03 m/s | 18.7 |  | 2.12 | m/s |  | 4.03 | m/s | 11.4578 | 0.0094042 | 13.3135 |  | 1 | 92 | 0.092 | 144.7122 | 6.8241 | 5.6762 | 0.02128 | 34.508 | 0.26661
2025-05-19 21:45 | 1374 | Remove | 2025-05-19 | 21:45 | ST | GS | - | 88.5 | g | 0 | 113.6 | 11.407 | 1126.6 | 63704 | 11:28 | 28.8 | 2.18 m/s | 25.4 | 30 | 4.18 m/s | 18.7 |  | 2.18 | m/s |  | 4.18 | m/s | 11.4661 | 0.0093883 | 13.3229 |  | -3.5 | 88.5 | 0.0885 | 150.5413 | 7.2221 | 5.6762 | 0.023159 | 34.5311 | 0.25629
2025-05-19 21:45 | 1375 | Remove | 2025-05-19 | 21:45 | ST | GS | - | 94 | g | 0 | 113.7 | 11.447 | 1131.3 | 63714 | 11:28 | 28.8 | 2.3 m/s | 23.4 | 30 | 3.88 m/s | 18.9 |  | 2.3 | m/s |  | 3.88 | m/s | 11.4744 | 0.0094275 | 13.3323 |  | 5.5 | 94 | 0.094 | 141.8334 | 6.6535 | 5.7369 | 0.02251 | 34.5536 | 0.27204
2025-05-19 21:46 | 1376 | Remove | 2025-05-19 | 21:46 | US | GS | - | 93.5 | g | 0 | 113.6 | 11.441 | 1131.2 | 63723 | 11:29 | 28.8 | 2.37 m/s | 22.6 | 30 | 4.01 m/s | 18 |  | 2.37 | m/s |  | 4.01 | m/s | 11.4828 | 0.0094267 | 13.3418 |  | -0.5 | 93.5 | 0.0935 | 142.6927 | 6.426 | 5.4637 | 0.022402 | 34.5761 | 0.27042
2025-05-19 21:46 | 1377 | Remove | 2025-05-19 | 21:46 | US | GS | - | 91 | g | 0 | 113.6 | 11.421 | 1128.5 | 63733 | 11:29 | 28.8 | 2.41 m/s | 23.6 | 30 | 3.96 m/s | 17.2 |  | 2.41 | m/s |  | 3.96 | m/s | 11.4911 | 0.0094042 | 13.3512 |  | -2.5 | 91 | 0.091 | 146.7161 | 6.7103 | 5.2209 | 0.023788 | 34.5998 | 0.26301
2025-05-19 21:47 | 1378 | Remove | 2025-05-19 | 21:47 | ST | GS | - | 90.5 | g | 0 | 113.7 | 11.385 | 1124.8 | 63742 | 11:30 | 28.8 | 2.31 m/s | 25.8 | 30 | 4.06 m/s | 18.8 |  | 2.31 | m/s |  | 4.06 | m/s | 11.4994 | 0.0093733 | 13.3605 |  | -0.5 | 90.5 | 0.0905 | 147.6303 | 7.3359 | 5.7066 | 0.024927 | 34.6248 | 0.26137
2025-05-19 21:47 | 1379 | Remove | 2025-05-19 | 21:47 | ST | GS | - | 92.5 | g | 0 | 113.7 | 11.414 | 1127.4 | 63751 | 11:30 | 28.8 | 2.22 m/s | 25.4 | 30 | 4.01 m/s | 19.7 |  | 2.22 | m/s |  | 4.01 | m/s | 11.5081 | 0.009395 | 13.3699 |  | 2 | 92.5 | 0.0925 | 144.5398 | 7.2221 | 5.9798 | 0.023584 | 34.6484 | 0.26697
2025-05-19 21:48 | 1380 | Remove | 2025-05-19 | 21:48 | ST | GS | - | 89 | g | 0 | 113.6 | 11.416 | 1127.4 | 63761 | 11:31 | 28.8 | 2.4 m/s | 24.1 | 30 | 4.0 m/s | 18.6 |  | 2.4 | m/s |  | 4 | m/s | 11.5164 | 0.009395 | 13.3793 |  | -3.5 | 89 | 0.089 | 150.3296 | 6.8525 | 5.6459 | 0.024191 | 34.6725 | 0.25669
2025-05-19 21:48 | 1381 | Keep | 2025-05-19 | 21:48 | ST | GS | - | 89 | g | 0 | 113.7 | 11.42 | 1128.1 | 63770 | 11:31 | 28.8 | 2.06 m/s | 24 | 30 | 4.01 m/s | 18.4 |  | 2.06 | m/s |  | 4.01 | m/s | 11.5247 | 0.0094008 | 13.3887 |  | 0 | 89 | 0.089 | 150.4352 | 6.8241 | 5.5852 | 0.020678 | 34.6932 | 0.25653
2025-05-19 21:49 | 1382 | Remove | 2025-05-19 | 21:49 | US | GS | - | 93 | g | 0 | 113.8 | 11.419 | 1128.4 | 63780 | 11:32 | 28.8 | 2.35 m/s | 23.4 | 30 | 3.96 m/s | 18.9 |  | 2.35 | m/s |  | 3.96 | m/s | 11.5331 | 0.0094033 | 13.3981 |  | 4 | 93 | 0.093 | 144.066 | 6.6535 | 5.7369 | 0.022999 | 34.7162 | 0.26789
2025-05-19 21:49 | 1383 | Remove | 2025-05-19 | 21:49 | ST | GS | - | 91.5 | g | 0 | 113.8 | 11.418 | 1127.7 | 63789 | 11:32 | 28.8 | 2.38 m/s | 25.4 | 30 | 3.94 m/s | 18 |  | 2.38 | m/s |  | 3.94 | m/s | 11.5414 | 0.0093975 | 13.4075 |  | -1.5 | 91.5 | 0.0915 | 146.5304 | 7.2221 | 5.4637 | 0.025284 | 34.7415 | 0.26337
2025-05-19 21:50 | 1384 | Remove | 2025-05-19 | 21:50 | ST | GS | - | 92 | g | 0 | 113.7 | 11.409 | 1126.7 | 63799 | 11:33 | 28.8 | 2.37 m/s | 24.4 | 30 | 3.88 m/s | 21 |  | 2.37 | m/s |  | 3.88 | m/s | 11.5497 | 0.0093892 | 13.4169 |  | 0.5 | 92 | 0.092 | 145.8361 | 6.9378 | 6.3744 | 0.024186 | 34.7657 | 0.26463
2025-05-19 21:50 | 1385 | Remove | 2025-05-19 | 21:50 | ST | GS | - | 92.5 | g | 0 | 113.7 | 11.418 | 1128.6 | 63808 | 11:33 | 28.8 | 2.51 m/s | 24.7 | 30 | 4.07 m/s | 19.6 |  | 2.51 | m/s |  | 4.07 | m/s | 11.5581 | 0.009405 | 13.4263 |  | 0.5 | 92.5 | 0.0925 | 145.1495 | 7.0231 | 5.9494 | 0.02593 | 34.7916 | 0.26587
2025-05-19 21:51 | 1386 | Remove | 2025-05-19 | 21:51 | US | GS | - | 93.5 | g | 0 | 113.8 | 11.388 | 1125.2 | 63817 | 11:34 | 28.8 | 2.35 m/s | 25.4 | 30 | 4.21 m/s | 18.6 |  | 2.35 | m/s |  | 4.21 | m/s | 11.5664 | 0.0093767 | 13.4357 |  | 1 | 93.5 | 0.0935 | 143.6974 | 7.2221 | 5.6459 | 0.024965 | 34.8166 | 0.26855
2025-05-19 21:51 | 1387 | Remove | 2025-05-19 | 21:51 | US | GS | - | 91.5 | g | 0 | 113.8 | 11.39 | 1124.8 | 63827 | 11:34 | 28.8 | 2.15 m/s | 24.7 | 30 | 3.98 m/s | 20.2 |  | 2.15 | m/s |  | 3.98 | m/s | 11.5747 | 0.0093733 | 13.4451 |  | -2 | 91.5 | 0.0915 | 146.9407 | 7.0231 | 6.1315 | 0.022211 | 34.8388 | 0.26264
2025-05-19 21:52 | 1388 | Remove | 2025-05-19 | 21:52 | US | GS | - | 96.5 | g | 0 | 113.7 | 11.435 | 1129.5 | 63836 | 11:35 | 28.8 | 2.41 m/s | 23.6 | 30 | 3.98 m/s | 18.1 |  | 2.41 | m/s |  | 3.98 | m/s | 11.5831 | 0.0094125 | 13.4545 |  | 5 | 96.5 | 0.0965 | 139.4248 | 6.7103 | 5.4941 | 0.023788 | 34.8626 | 0.2768
2025-05-19 21:52 | 1389 | Remove | 2025-05-19 | 21:52 | ST | GS | - | 90.5 | g | 0 | 113.7 | 11.373 | 1122.5 | 63845 | 11:35 | 28.7 | 2.13 m/s | 25.5 | 30 | 4.0 m/s | 19.1 |  | 2.13 | m/s |  | 4 | m/s | 11.5914 | 0.0093542 | 13.4638 |  | -6 | 90.5 | 0.0905 | 148.7717 | 7.211 | 5.7976 | 0.022593 | 34.8852 | 0.25942
2025-05-19 21:53 | 1390 | Remove | 2025-05-19 | 21:53 | ST | GS | - | 95 | g | 0 | 113.8 | 11.41 | 1126.3 | 63855 | 11:36 | 28.8 | 2.2 m/s | 26.7 | 30 | 4.0 m/s | 18.4 |  | 2.2 | m/s |  | 4 | m/s | 11.5997 | 0.0093858 | 13.4732 |  | 4.5 | 95 | 0.095 | 141.8235 | 7.5918 | 5.5852 | 0.024568 | 34.9097 | 0.27213
2025-05-19 21:53 | 1391 | Remove | 2025-05-19 | 21:53 | US | GS | - | 90.5 | g | 0 | 113.6 | 11.415 | 1127.6 | 63864 | 11:36 | 28.8 | 2.7 m/s | 23.9 | 30 | 3.94 m/s | 18.4 |  | 2.7 | m/s |  | 3.94 | m/s | 11.6081 | 0.0093967 | 13.4826 |  | -4.5 | 90.5 | 0.0905 | 148.9793 | 6.7956 | 5.5852 | 0.02699 | 34.9367 | 0.25904
2025-05-19 21:54 | 1392 | Remove | 2025-05-19 | 21:54 | ST | GS | - | 94.5 | g | 0 | 113.8 | 11.41 | 1126.6 | 63874 | 11:37 | 28.8 | 2.16 m/s | 24.7 | 30 | 3.96 m/s | 19.5 |  | 2.16 | m/s |  | 3.96 | m/s | 11.6164 | 0.0093883 | 13.492 |  | 4 | 94.5 | 0.0945 | 142.7726 | 7.0231 | 5.9191 | 0.022314 | 34.959 | 0.27032
2025-05-19 21:54 | 1393 | Remove | 2025-05-19 | 21:54 | ST | GS | - | 90.5 | g | 0 | 113.8 | 11.41 | 1126.7 | 63883 | 11:37 | 28.8 | 2.27 m/s | 23.4 | 30 | 3.96 m/s | 18.9 |  | 2.27 | m/s |  | 3.96 | m/s | 11.6247 | 0.0093892 | 13.5014 |  | -4 | 90.5 | 0.0905 | 149.1868 | 6.6535 | 5.7369 | 0.022216 | 34.9813 | 0.25871
2025-05-19 21:55 | 1394 | Remove | 2025-05-19 | 21:55 | US | GS | - | 93.5 | g | 0 | 113.8 | 11.406 | 1126.3 | 63893 | 11:38 | 28.8 | 2.27 m/s | 25 | 30 | 4.03 m/s | 18.7 |  | 2.27 | m/s |  | 4.03 | m/s | 11.6331 | 0.0093858 | 13.5108 |  | 3 | 93.5 | 0.0935 | 144.5004 | 7.1084 | 5.6762 | 0.023736 | 35.005 | 0.2671
2025-05-19 21:55 | 1395 | Remove | 2025-05-19 | 21:55 | ST | GS | - | 92 | g | 0 | 113.8 | 11.365 | 1121.8 | 63902 | 11:38 | 28.7 | 2.11 m/s | 26.3 | 30 | 4.06 m/s | 19.5 |  | 2.11 | m/s |  | 4.06 | m/s | 11.6417 | 0.0093483 | 13.5201 |  | -1.5 | 92 | 0.092 | 146.958 | 7.4372 | 5.9191 | 0.023083 | 35.0281 | 0.26265
2025-05-19 21:56 | 1396 | Remove | 2025-05-19 | 21:56 | US | GS | - | 91 | g | 0 | 113.8 | 11.402 | 1126.3 | 63911 | 11:39 | 28.7 | 2.5 m/s | 24.4 | 30 | 3.94 m/s | 19.1 |  | 2.5 | m/s |  | 3.94 | m/s | 11.65 | 0.0093858 | 13.5295 |  | -1 | 91 | 0.091 | 148.6761 | 6.8999 | 5.7976 | 0.025374 | 35.0535 | 0.2596
2025-05-19 21:56 | 1397 | Remove | 2025-05-19 | 21:56 | US | GS | - | 94 | g | 0 | 113.9 | 11.396 | 1124.9 | 63921 | 11:40 | 28.7 | 2.33 m/s | 23.9 | 30 | 4.09 m/s | 17.7 |  | 2.33 | m/s |  | 4.09 | m/s | 11.6583 | 0.0093742 | 13.5389 |  | 3 | 94 | 0.094 | 144.0308 | 6.7585 | 5.3727 | 0.023164 | 35.0766 | 0.26798
2025-05-19 21:57 | 1398 | Remove | 2025-05-19 | 21:57 | ST | GS | - | 90.5 | g | 0 | 113.8 | 11.42 | 1127.3 | 63930 | 11:40 | 28.8 | 2.27 m/s | 23.4 | 30 | 3.93 m/s | 18 |  | 2.27 | m/s |  | 3.93 | m/s | 11.6667 | 0.0093942 | 13.5483 |  | -3.5 | 90.5 | 0.0905 | 149.7049 | 6.6535 | 5.4637 | 0.022216 | 35.0988 | 0.25784
2025-05-19 21:57 | 1399 | Remove | 2025-05-19 | 21:57 | US | GS | - | 97.5 | g | 0 | 113.9 | 11.385 | 1123.7 | 63940 | 11:40 | 28.8 | 2.35 m/s | 26 | 30 | 4.09 m/s | 18.2 |  | 2.35 | m/s |  | 4.09 | m/s | 11.675 | 0.0093642 | 13.5577 |  | 7 | 97.5 | 0.0975 | 139.0529 | 7.3927 | 5.5245 | 0.025555 | 35.1244 | 0.27758
2025-05-19 21:58 | 1400 | Remove | 2025-05-19 | 21:58 | ST | GS | - | 90 | g | 0 | 113.9 | 11.356 | 1119.5 | 63949 | 11:41 | 28.7 | 2.2 m/s | 25.5 | 30 | 4.09 m/s | 19.5 |  | 2.2 | m/s |  | 4.09 | m/s | 11.6833 | 0.0093292 | 13.567 |  | -7.5 | 90 | 0.09 | 150.7443 | 7.211 | 5.9191 | 0.023336 | 35.1477 | 0.25606
2025-05-19 21:58 | 1401 | Remove | 2025-05-19 | 21:58 | ST | GS | - | 90 | g | 0 | 113.9 | 11.376 | 1122.3 | 63958 | 11:42 | 28.7 | 2.37 m/s | 24.7 | 30 | 3.9 m/s | 19.1 |  | 2.37 | m/s |  | 3.9 | m/s | 11.6917 | 0.0093525 | 13.5763 |  | 0 | 90 | 0.09 | 150.8482 | 6.9848 | 5.7976 | 0.02435 | 35.1721 | 0.25588
2025-05-19 21:59 | 1402 | Remove | 2025-05-19 | 21:59 | ST | GS | - | 91 | g | 0 | 114 | 11.399 | 1125.4 | 63968 | 11:42 | 28.7 | 2.31 m/s | 24.7 | 30 | 3.98 m/s | 18.9 |  | 2.31 | m/s |  | 3.98 | m/s | 11.7 | 0.0093783 | 13.5857 |  | 1 | 91 | 0.091 | 149.2936 | 6.9848 | 5.7369 | 0.023734 | 35.1958 | 0.25855
2025-05-19 21:59 | 1403 | Remove | 2025-05-19 | 21:59 | ST | GS | - | 92.5 | g | 0 | 113.9 | 11.401 | 1125.5 | 63977 | 11:42 | 28.7 | 2.45 m/s | 24.3 | 30 | 4.18 m/s | 19.5 |  | 2.45 | m/s |  | 4.18 | m/s | 11.7083 | 0.0093792 | 13.5951 |  | 1.5 | 92.5 | 0.0925 | 146.974 | 6.8716 | 5.9191 | 0.024764 | 35.2206 | 0.26263
2025-05-19 22:00 | 1404 | Remove | 2025-05-19 | 22:00 | US | GS | - | 94.5 | g | 0 | 113.9 | 11.392 | 1124 | 63987 | 11:43 | 28.7 | 2.3 m/s | 24.1 | 30 | 4.09 m/s | 18.6 |  | 2.3 | m/s |  | 4.09 | m/s | 11.7167 | 0.0093667 | 13.6045 |  | 2 | 94.5 | 0.0945 | 143.9626 | 6.8151 | 5.6459 | 0.023057 | 35.2436 | 0.26813
2025-05-19 22:00 | 1405 | Remove | 2025-05-19 | 22:00 | ST | GS | - | 91 | g | 0 | 113.9 | 11.385 | 1123 | 63996 | 11:44 | 28.7 | 2.23 m/s | 25.1 | 30 | 3.9 m/s | 19.7 |  | 2.23 | m/s |  | 3.9 | m/s | 11.725 | 0.0093583 | 13.6138 |  | -3.5 | 91 | 0.091 | 149.6024 | 7.0979 | 5.9798 | 0.023283 | 35.2669 | 0.25803
2025-05-19 22:01 | 1406 | Remove | 2025-05-19 | 22:01 | ST | GS | - | 91 | g | 0 | 113.9 | 11.37 | 1121.1 | 64005 | 11:44 | 28.7 | 2.16 m/s | 25.5 | 30 | 4.07 m/s | 18.9 |  | 2.16 | m/s |  | 4.07 | m/s | 11.7333 | 0.0093425 | 13.6232 |  | 0 | 91 | 0.091 | 149.7051 | 7.211 | 5.7369 | 0.022911 | 35.2898 | 0.25786
2025-05-19 22:01 | 1407 | Remove | 2025-05-19 | 22:01 | ST | GS | - | 92 | g | 0 | 113.9 | 11.373 | 1122.4 | 64015 | 11:44 | 28.7 | 2.27 m/s | 23.9 | 30 | 4.09 m/s | 19 |  | 2.27 | m/s |  | 4.09 | m/s | 11.7417 | 0.0093533 | 13.6325 |  | 1 | 92 | 0.092 | 148.1795 | 6.7585 | 5.7673 | 0.022567 | 35.3124 | 0.26053
2025-05-19 22:02 | 1408 | Remove | 2025-05-19 | 22:02 | ST | GS | - | 91 | g | 0 | 113.9 | 11.389 | 1123.4 | 64024 | 11:45 | 28.7 | 2.37 m/s | 25 | 30 | 4.07 m/s | 19.4 |  | 2.37 | m/s |  | 4.07 | m/s | 11.75 | 0.0093617 | 13.6419 |  | -1 | 91 | 0.091 | 149.9107 | 7.0696 | 5.8887 | 0.024646 | 35.337 | 0.25752
2025-05-19 22:02 | 1409 | Remove | 2025-05-19 | 22:02 | ST | GS | - | 92.5 | g | 0 | 113.8 | 11.37 | 1122.1 | 64034 | 11:46 | 28.7 | 2.06 m/s | 25.4 | 30 | 4.04 m/s | 18.6 |  | 2.06 | m/s |  | 4.04 | m/s | 11.7583 | 0.0093508 | 13.6512 |  | 1.5 | 92.5 | 0.0925 | 147.5808 | 7.1827 | 5.6459 | 0.021765 | 35.3588 | 0.2616
2025-05-19 22:03 | 1410 | Remove | 2025-05-19 | 22:03 | US | GS | - | 96.5 | g | 0 | 114 | 11.379 | 1123.5 | 64043 | 11:46 | 28.7 | 2.37 m/s | 24.4 | 30 | 3.93 m/s | 20.3 |  | 2.37 | m/s |  | 3.93 | m/s | 11.7667 | 0.0093625 | 13.6606 |  | 4 | 96.5 | 0.0965 | 141.5605 | 6.8999 | 6.1619 | 0.024054 | 35.3829 | 0.27273
2025-05-19 22:03 | 1411 | Keep | 2025-05-19 | 22:03 | US | GS | - | 92 | g | 0 | 114 | 11.365 | 1121.3 | 64052 | 11:46 | 28.7 | 2.22 m/s | 25.2 | 30 | 4.26 m/s | 19.5 |  | 2.22 | m/s |  | 4.26 | m/s | 11.775 | 0.0093442 | 13.6699 |  | -4.5 | 92 | 0.092 | 148.5863 | 7.1261 | 5.9191 | 0.023271 | 35.4061 | 0.25984
2025-05-19 22:04 | 1412 | Remove | 2025-05-19 | 22:04 | ST | GS | - | 90.5 | g | 0 | 114 | 11.402 | 1126.1 | 64062 | 11:47 | 28.7 | 2.12 m/s | 23.8 | 30 | 4.12 m/s | 17.2 |  | 2.12 | m/s |  | 4.12 | m/s | 11.7833 | 0.0093842 | 13.6793 |  | -1.5 | 90.5 | 0.0905 | 151.1527 | 6.7303 | 5.2209 | 0.020988 | 35.4271 | 0.25545
2025-05-19 22:04 | 1413 | Remove | 2025-05-19 | 22:04 | ST | GS | - | 95 | g | 0 | 114 | 11.377 | 1122.5 | 64071 | 11:48 | 28.7 | 2.23 m/s | 24.3 | 30 | 3.96 m/s | 18.9 |  | 2.23 | m/s |  | 3.96 | m/s | 11.7919 | 0.0093542 | 13.6887 |  | 4.5 | 95 | 0.095 | 144.0913 | 6.8716 | 5.7369 | 0.022541 | 35.4497 | 0.26799
2025-05-19 22:05 | 1414 | Remove | 2025-05-19 | 22:05 | ST | GS | - | 92 | g | 0 | 114 | 11.373 | 1123 | 64080 | 11:48 | 28.7 | 2.08 m/s | 24.8 | 30 | 4.07 m/s | 18 |  | 2.08 | m/s |  | 4.07 | m/s | 11.8003 | 0.0093583 | 13.698 |  | -3 | 92 | 0.092 | 148.8916 | 7.013 | 5.4637 | 0.021457 | 35.4711 | 0.25937
2025-05-19 22:05 | 1415 | Remove | 2025-05-19 | 22:05 | US | GS | - | 93 | g | 0 | 113.9 | 11.368 | 1121.8 | 64090 | 11:49 | 28.7 | 2.22 m/s | 24.2 | 30 | 3.92 m/s | 18.7 |  | 2.22 | m/s |  | 3.92 | m/s | 11.8086 | 0.0093483 | 13.7074 |  | 1 | 93 | 0.093 | 147.3912 | 6.8434 | 5.6762 | 0.022347 | 35.4935 | 0.26202
2025-05-19 22:06 | 1416 | Remove | 2025-05-19 | 22:06 | ST | GS | - | 93 | g | 0 | 113.9 | 11.377 | 1123 | 64099 | 11:49 | 28.7 | 2.37 m/s | 24.6 | 29.9 | 3.9 m/s | 19.4 |  | 2.37 | m/s |  | 3.9 | m/s | 11.8169 | 0.0093583 | 13.7167 |  | 0 | 93 | 0.093 | 147.4918 | 6.9565 | 5.8568 | 0.024252 | 35.5177 | 0.26184
2025-05-19 22:06 | 1417 | Remove | 2025-05-19 | 22:06 | US | GS | - | 94.5 | g | 0 | 113.9 | 11.355 | 1119.6 | 64109 | 11:50 | 28.7 | 2.31 m/s | 26.4 | 29.9 | 3.99 m/s | 19.5 |  | 2.31 | m/s |  | 3.99 | m/s | 11.8253 | 0.00933 | 13.7261 |  | 1.5 | 94.5 | 0.0945 | 145.2494 | 7.4655 | 5.887 | 0.025367 | 35.5431 | 0.26587
2025-05-19 22:07 | 1418 | Remove | 2025-05-19 | 22:07 | US | GS | - | 92 | g | 0 | 114 | 11.356 | 1119.7 | 64118 | 11:50 | 28.7 | 2.61 m/s | 26.6 | 29.9 | 3.97 m/s | 21.7 |  | 2.61 | m/s |  | 3.97 | m/s | 11.8336 | 0.0093308 | 13.7354 |  | -2.5 | 92 | 0.092 | 149.2978 | 7.522 | 6.5512 | 0.028879 | 35.572 | 0.25863
2025-05-19 22:07 | 1419 | Remove | 2025-05-19 | 22:07 | US | GS | - | 94.5 | g | 0 | 114 | 11.383 | 1123.6 | 64127 | 11:51 | 28.7 | 2.27 m/s | 23.2 | 29.9 | 4.03 m/s | 17.6 |  | 2.27 | m/s |  | 4.03 | m/s | 11.8419 | 0.0093633 | 13.7448 |  | 2.5 | 94.5 | 0.0945 | 145.4472 | 6.5606 | 5.3134 | 0.021906 | 35.5939 | 0.2655
2025-05-19 22:08 | 1420 | Remove | 2025-05-19 | 22:08 | ST | GS | - | 90.5 | g | 0 | 114 | 11.358 | 1120.2 | 64137 | 11:51 | 28.7 | 2.23 m/s | 24.7 | 29.9 | 4.16 m/s | 18.3 |  | 2.23 | m/s |  | 4.16 | m/s | 11.8503 | 0.009335 | 13.7541 |  | -4 | 90.5 | 0.0905 | 151.979 | 6.9848 | 5.5248 | 0.022912 | 35.6168 | 0.25409
2025-05-19 22:08 | 1421 | Remove | 2025-05-19 | 22:08 | ST | GS | - | 95.5 | g | 0 | 114 | 11.359 | 1120.8 | 64146 | 11:52 | 28.7 | 2.31 m/s | 27.4 | 29.9 | 4.13 m/s | 19.4 |  | 2.31 | m/s |  | 4.13 | m/s | 11.8586 | 0.00934 | 13.7634 |  | 5 | 95.5 | 0.0955 | 144.1198 | 7.7483 | 5.8568 | 0.026328 | 35.6431 | 0.26793
2025-05-19 22:09 | 1422 | Remove | 2025-05-19 | 22:09 | ST | GS | - | 93 | g | 0 | 114 | 11.385 | 1124 | 64156 | 11:52 | 28.7 | 2.41 m/s | 25.1 | 29.9 | 4.07 m/s | 18.1 |  | 2.41 | m/s |  | 4.07 | m/s | 11.8669 | 0.0093667 | 13.7728 |  | -2.5 | 93 | 0.093 | 148.0947 | 7.0979 | 5.4644 | 0.025162 | 35.6683 | 0.26074
2025-05-19 22:09 | 1423 | Remove | 2025-05-19 | 22:09 | ST | GS | - | 92 | g | 0 | 114 | 11.36 | 1120.5 | 64165 | 11:53 | 28.7 | 2.23 m/s | 24.8 | 29.9 | 4.01 m/s | 19.3 |  | 2.23 | m/s |  | 4.01 | m/s | 11.8753 | 0.0093375 | 13.7821 |  | -1 | 92 | 0.092 | 149.8059 | 7.013 | 5.8267 | 0.023005 | 35.6913 | 0.25777
2025-05-19 22:10 | 1424 | Remove | 2025-05-19 | 22:10 | ST | GS | - | 91 | g | 0 | 113.9 | 11.379 | 1122.8 | 64174 | 11:53 | 28.7 | 2.26 m/s | 24.8 | 29.9 | 4.12 m/s | 17.8 |  | 2.26 | m/s |  | 4.12 | m/s | 11.8836 | 0.0093567 | 13.7915 |  | -1 | 91 | 0.091 | 151.5549 | 7.013 | 5.3738 | 0.023314 | 35.7146 | 0.2548
2025-05-19 22:10 | 1425 | Remove | 2025-05-19 | 22:10 | ST | GS | - | 93.5 | g | 0 | 114 | 11.393 | 1124.5 | 64184 | 11:54 | 28.7 | 2.26 m/s | 24.8 | 29.9 | 3.92 m/s | 17.5 |  | 2.26 | m/s |  | 3.92 | m/s | 11.8919 | 0.0093708 | 13.8009 |  | 2.5 | 93.5 | 0.0935 | 147.6029 | 7.013 | 5.2832 | 0.023314 | 35.7379 | 0.26163
2025-05-19 22:11 | 1426 | Remove | 2025-05-19 | 22:11 | ST | GS | - | 95.5 | g | 0 | 114 | 11.378 | 1123.1 | 64193 | 11:54 | 28.7 | 2.22 m/s | 23.3 | 29.9 | 3.94 m/s | 18.7 |  | 2.22 | m/s |  | 3.94 | m/s | 11.9003 | 0.0093592 | 13.8102 |  | 2 | 95.5 | 0.0955 | 144.6097 | 6.5889 | 5.6455 | 0.021516 | 35.7594 | 0.26706
2025-05-19 22:11 | 1427 | Remove | 2025-05-19 | 22:11 | ST | GS | - | 94.5 | g | 0 | 114 | 11.403 | 1125.7 | 64202 | 11:55 | 28.7 | 2.26 m/s | 23.9 | 29.9 | 3.9 m/s | 17.4 |  | 2.26 | m/s |  | 3.9 | m/s | 11.9086 | 0.0093808 | 13.8196 |  | -1 | 94.5 | 0.0945 | 146.2393 | 6.7585 | 5.2531 | 0.022468 | 35.7819 | 0.2641
2025-05-19 22:12 | 1428 | Remove | 2025-05-19 | 22:12 | US | GS | - | 97.5 | g | 0 | 114 | 11.389 | 1124.6 | 64212 | 11:55 | 28.7 | 2.23 m/s | 23.4 | 29.9 | 3.94 m/s | 18.2 |  | 2.23 | m/s |  | 3.94 | m/s | 11.9169 | 0.0093717 | 13.829 |  | 3 | 97.5 | 0.0975 | 141.8357 | 6.6171 | 5.4946 | 0.021706 | 35.8036 | 0.27232
2025-05-19 22:12 | 1429 | Remove | 2025-05-19 | 22:12 | ST | GS | - | 93.5 | g | 0 | 114.1 | 11.351 | 1119.7 | 64221 | 11:56 | 28.7 | 2.25 m/s | 24.1 | 29.9 | 3.92 m/s | 19.3 |  | 2.25 | m/s |  | 3.92 | m/s | 11.9253 | 0.0093308 | 13.8383 |  | -4 | 93.5 | 0.0935 | 148.0033 | 6.8151 | 5.8267 | 0.022556 | 35.8261 | 0.26098
2025-05-19 22:13 | 1430 | Remove | 2025-05-19 | 22:13 | ST | GS | - | 91 | g | 0 | 114 | 11.385 | 1123.9 | 64231 | 11:56 | 28.7 | 2.13 m/s | 23.8 | 29.9 | 4.04 m/s | 17.9 |  | 2.13 | m/s |  | 4.04 | m/s | 11.9339 | 0.0093658 | 13.8477 |  | -2.5 | 91 | 0.091 | 152.1723 | 6.7303 | 5.404 | 0.021087 | 35.8472 | 0.25385
2025-05-19 22:13 | 1431 | Remove | 2025-05-19 | 22:13 | US | GS | - | 96.5 | g | 0 | 114.1 | 11.388 | 1124 | 64240 | 11:57 | 28.7 | 2.5 m/s | 23.5 | 29.9 | 4.1 m/s | 18.1 |  | 2.5 | m/s |  | 4.1 | m/s | 11.9422 | 0.0093667 | 13.857 |  | 5.5 | 96.5 | 0.0965 | 143.5963 | 6.6454 | 5.4644 | 0.024438 | 35.8717 | 0.26901
2025-05-19 22:14 | 1432 | Remove | 2025-05-19 | 22:14 | ST | GS | - | 92 | g | 0 | 114 | 11.404 | 1126.1 | 64249 | 11:57 | 28.7 | 2.37 m/s | 24.1 | 29.9 | 4.0 m/s | 16.9 |  | 2.37 | m/s |  | 4 | m/s | 11.9506 | 0.0093842 | 13.8664 |  | -4.5 | 92 | 0.092 | 150.722 | 6.8151 | 5.1021 | 0.023759 | 35.8954 | 0.2563
2025-05-19 22:14 | 1433 | Remove | 2025-05-19 | 22:14 | ST | GS | - | 91.5 | g | 0 | 114.1 | 11.374 | 1123.1 | 64259 | 11:58 | 28.7 | 2.37 m/s | 24.1 | 29.9 | 4.18 m/s | 17.4 |  | 2.37 | m/s |  | 4.18 | m/s | 11.9589 | 0.0093592 | 13.8758 |  | -0.5 | 91.5 | 0.0915 | 151.648 | 6.8151 | 5.2531 | 0.023759 | 35.9192 | 0.25474
2025-05-19 22:15 | 1434 | Remove | 2025-05-19 | 22:15 | ST | GS | - | 94 | g | 0 | 114.1 | 11.388 | 1124.7 | 64268 | 11:58 | 28.7 | 2.34 m/s | 24.2 | 29.9 | 4.03 m/s | 17.6 |  | 2.34 | m/s |  | 4.03 | m/s | 11.9672 | 0.0093725 | 13.8852 |  | 2.5 | 94 | 0.094 | 147.7145 | 6.8434 | 5.3134 | 0.023555 | 35.9427 | 0.26153
2025-05-19 22:15 | 1435 | Remove | 2025-05-19 | 22:15 | ST | GS | - | 95.5 | g | 0 | 114.1 | 11.412 | 1128.2 | 64278 | 11:59 | 28.7 | 2.35 m/s | 23.7 | 29.9 | 3.9 m/s | 17 |  | 2.35 | m/s |  | 3.9 | m/s | 11.9756 | 0.0094017 | 13.8946 |  | 1.5 | 95.5 | 0.0955 | 145.4928 | 6.702 | 5.1323 | 0.023167 | 35.9659 | 0.26553
2025-05-19 22:16 | 1436 | Remove | 2025-05-19 | 22:16 | ST | GS | - | 91.5 | g | 0 | 114 | 11.377 | 1123.2 | 64287 | 11:59 | 28.7 | 2.18 m/s | 23.1 | 29.9 | 4.1 m/s | 18.3 |  | 2.18 | m/s |  | 4.1 | m/s | 11.9839 | 0.00936 | 13.9039 |  | -4 | 91.5 | 0.0915 | 151.9554 | 6.5323 | 5.5248 | 0.020947 | 35.9869 | 0.25426
2025-05-19 22:16 | 1437 | Remove | 2025-05-19 | 22:16 | US | GS | - | 94.5 | g | 0 | 114.1 | 11.392 | 1124.5 | 64296 | 12:00 | 28.7 | 2.33 m/s | 24 | 29.9 | 4.06 m/s | 18.1 |  | 2.33 | m/s |  | 4.06 | m/s | 11.9922 | 0.0093708 | 13.9133 |  | 3 | 94.5 | 0.0945 | 147.2306 | 6.7868 | 5.4644 | 0.023261 | 36.0101 | 0.26243
2025-05-19 22:17 | 1438 | Remove | 2025-05-19 | 22:17 | ST | GS | - | 92.5 | g | 0 | 114 | 11.414 | 1128 | 64306 | 12:00 | 28.7 | 2.19 m/s | 23.5 | 29.9 | 3.96 m/s | 17.8 |  | 2.19 | m/s |  | 3.96 | m/s | 12.0006 | 0.0094 | 13.9227 |  | -2 | 92.5 | 0.0925 | 150.5156 | 6.6454 | 5.3738 | 0.021408 | 36.0315 | 0.25672
2025-05-19 22:17 | 1439 | Remove | 2025-05-19 | 22:17 | ST | GS | - | 95.5 | g | 0 | 114.1 | 11.412 | 1127 | 64315 | 12:01 | 28.7 | 2.35 m/s | 22.5 | 30 | 3.92 m/s | 18.3 |  | 2.35 | m/s |  | 3.92 | m/s | 12.0089 | 0.0093917 | 13.9321 |  | 3 | 95.5 | 0.0955 | 145.8857 | 6.3626 | 5.5548 | 0.021994 | 36.0535 | 0.26488
2025-05-19 22:18 | 1440 | Remove | 2025-05-19 | 22:18 | ST | GS | - | 93 | g | 0 | 114.1 | 11.376 | 1123 | 64325 | 12:01 | 28.7 | 2.3 m/s | 23.4 | 30 | 4.12 m/s | 19.4 |  | 2.3 | m/s |  | 4.12 | m/s | 12.0172 | 0.0093583 | 13.9414 |  | -2.5 | 93 | 0.093 | 149.908 | 6.6171 | 5.8887 | 0.022387 | 36.0759 | 0.25779
2025-05-19 22:18 | 1441 | Keep | 2025-05-19 | 22:18 | US | GS | - | 96 | g | 0 | 114 | 11.403 | 1127 | 64334 | 12:02 | 28.7 | 2.42 m/s | 23.3 | 29.9 | 3.9 m/s | 17.8 |  | 2.42 | m/s |  | 3.9 | m/s | 12.0256 | 0.0093917 | 13.9508 |  | 3 | 96 | 0.096 | 145.3212 | 6.5889 | 5.3738 | 0.023455 | 36.0994 | 0.26593
2025-05-19 22:19 | 1442 | Remove | 2025-05-19 | 22:19 | ST | GS | - | 93 | g | 0 | 114.1 | 11.353 | 1120.8 | 64343 | 12:02 | 28.7 | 2.34 m/s | 24.4 | 29.9 | 4.09 m/s | 19 |  | 2.34 | m/s |  | 4.09 | m/s | 12.0339 | 0.00934 | 13.9602 |  | -3 | 93 | 0.093 | 150.1094 | 6.8999 | 5.7361 | 0.02375 | 36.1231 | 0.25745
2025-05-19 22:19 | 1443 | Remove | 2025-05-19 | 22:19 | ST | GS | - | 96 | g | 0 | 114.2 | 11.381 | 1123.8 | 64353 | 12:03 | 28.7 | 2.34 m/s | 25.9 | 29.9 | 4.0 m/s | 19.2 |  | 2.34 | m/s |  | 4 | m/s | 12.0422 | 0.009365 | 13.9695 |  | 3 | 96 | 0.096 | 145.516 | 7.3241 | 5.7965 | 0.02521 | 36.1483 | 0.26557
2025-05-19 22:20 | 1444 | Remove | 2025-05-19 | 22:20 | US | GS | - | 92.5 | g | 0 | 114.1 | 11.402 | 1126.7 | 64362 | 12:03 | 28.7 | 2.15 m/s | 24.4 | 29.9 | 3.97 m/s | 18.3 |  | 2.15 | m/s |  | 3.97 | m/s | 12.0506 | 0.0093892 | 13.9789 |  | -3.5 | 92.5 | 0.0925 | 151.1235 | 6.8999 | 5.5248 | 0.021822 | 36.1701 | 0.25574
2025-05-19 22:20 | 1445 | Remove | 2025-05-19 | 22:20 | ST | GS | - | 96 | g | 0 | 114 | 11.398 | 1125.8 | 64372 | 12:04 | 28.7 | 2.26 m/s | 23.1 | 29.9 | 3.88 m/s | 19.1 |  | 2.26 | m/s |  | 3.88 | m/s | 12.0589 | 0.0093817 | 13.9883 |  | 3.5 | 96 | 0.096 | 145.7116 | 6.5323 | 5.7663 | 0.021716 | 36.1919 | 0.26525
2025-05-19 22:21 | 1446 | Remove | 2025-05-19 | 22:21 | US | GS | - | 94.5 | g | 0 | 114.1 | 11.397 | 1125.3 | 64381 | 12:04 | 28.7 | 2.38 m/s | 23.5 | 29.9 | 4.03 m/s | 17.5 |  | 2.38 | m/s |  | 4.03 | m/s | 12.0672 | 0.0093775 | 13.9977 |  | -1.5 | 94.5 | 0.0945 | 148.1237 | 6.6454 | 5.2832 | 0.023265 | 36.2151 | 0.26094
2025-05-19 22:21 | 1447 | Remove | 2025-05-19 | 22:21 | ST | GS | - | 97.5 | g | 0 | 114 | 11.386 | 1124.5 | 64390 | 12:05 | 28.7 | 2.3 m/s | 24.2 | 29.9 | 4.01 m/s | 17.8 |  | 2.3 | m/s |  | 4.01 | m/s | 12.0758 | 0.0093708 | 14.0071 |  | 3 | 97.5 | 0.0975 | 143.6621 | 6.8434 | 5.3738 | 0.023153 | 36.2383 | 0.26905
2025-05-19 22:22 | 1448 | Remove | 2025-05-19 | 22:22 | ST | GS | - | 95.5 | g | 0 | 114.1 | 11.392 | 1125.9 | 64400 | 12:05 | 28.7 | 2.19 m/s | 24.2 | 29.9 | 3.96 m/s | 17.7 |  | 2.19 | m/s |  | 3.96 | m/s | 12.0842 | 0.0093825 | 14.0164 |  | -2 | 95.5 | 0.0955 | 146.769 | 6.8434 | 5.3436 | 0.022045 | 36.2603 | 0.26337
2025-05-19 22:22 | 1449 | Remove | 2025-05-19 | 22:22 | ST | GS | - | 95 | g | 0 | 114 | 11.42 | 1128.5 | 64409 | 12:06 | 28.7 | 2.27 m/s | 23.4 | 29.9 | 3.93 m/s | 17.5 |  | 2.27 | m/s |  | 3.93 | m/s | 12.0925 | 0.0094042 | 14.0258 |  | -0.5 | 95 | 0.095 | 147.6405 | 6.6171 | 5.2832 | 0.022095 | 36.2824 | 0.26183
2025-05-19 22:23 | 1450 | Remove | 2025-05-19 | 22:23 | US | GS | - | 95 | g | 0 | 114.1 | 11.379 | 1123.6 | 64419 | 12:06 | 28.7 | 2.23 m/s | 22.3 | 29.9 | 3.98 m/s | 18.5 |  | 2.23 | m/s |  | 3.98 | m/s | 12.1011 | 0.0093633 | 14.0352 |  | 0 | 95 | 0.095 | 147.739 | 6.3061 | 5.5851 | 0.020686 | 36.3031 | 0.26169
2025-05-19 22:23 | 1451 | Remove | 2025-05-19 | 22:23 | US | GS | - | 98 | g | 0 | 114.1 | 11.392 | 1125.2 | 64428 | 12:07 | 28.7 | 2.18 m/s | 24.5 | 29.9 | 4.04 m/s | 18.7 |  | 2.18 | m/s |  | 4.04 | m/s | 12.1094 | 0.0093767 | 14.0446 |  | 3 | 98 | 0.098 | 143.3121 | 6.9282 | 5.6455 | 0.022217 | 36.3253 | 0.26978
2025-05-19 22:24 | 1452 | Remove | 2025-05-19 | 22:24 | ST | GS | - | 96.5 | g | 0 | 114.1 | 11.403 | 1126.8 | 64438 | 12:07 | 28.7 | 2.42 m/s | 23.9 | 29.9 | 3.88 m/s | 18.1 |  | 2.42 | m/s |  | 3.88 | m/s | 12.1178 | 0.00939 | 14.054 |  | -1.5 | 96.5 | 0.0965 | 145.637 | 6.7585 | 5.4644 | 0.024059 | 36.3494 | 0.26548
2025-05-19 22:24 | 1453 | Remove | 2025-05-19 | 22:24 | ST | GS | - | 92.5 | g | 0 | 114.2 | 11.357 | 1120.8 | 64447 | 12:08 | 28.7 | 2.25 m/s | 23.1 | 29.9 | 4.16 m/s | 20.1 |  | 2.25 | m/s |  | 4.16 | m/s | 12.1261 | 0.00934 | 14.0633 |  | -4 | 92.5 | 0.0925 | 152.0358 | 6.5323 | 6.0682 | 0.02162 | 36.371 | 0.25432
2025-05-19 22:25 | 1454 | Remove | 2025-05-19 | 22:25 | ST | GS | - | 93 | g | 0 | 114.1 | 11.383 | 1124.2 | 64456 | 12:08 | 28.7 | 2.25 m/s | 25.3 | 29.9 | 4.06 m/s | 17.7 |  | 2.25 | m/s |  | 4.06 | m/s | 12.1344 | 0.0093683 | 14.0727 |  | 0.5 | 93 | 0.093 | 151.3192 | 7.1544 | 5.3436 | 0.023679 | 36.3947 | 0.25553
2025-05-19 22:25 | 1455 | Remove | 2025-05-19 | 22:25 | ST | GS | - | 96 | g | 0 | 114.2 | 11.381 | 1123.4 | 64466 | 12:09 | 28.7 | 2.15 m/s | 25.2 | 29.9 | 3.89 m/s | 19.5 |  | 2.15 | m/s |  | 3.89 | m/s | 12.1428 | 0.0093617 | 14.082 |  | 3 | 96 | 0.096 | 146.688 | 7.1261 | 5.887 | 0.022537 | 36.4172 | 0.26361
2025-05-19 22:26 | 1456 | Remove | 2025-05-19 | 22:26 | US | GS | - | 94 | g | 0 | 114.2 | 11.394 | 1125.4 | 64475 | 12:09 | 28.7 | 2.12 m/s | 23.3 | 29.9 | 4.03 m/s | 17.7 |  | 2.12 | m/s |  | 4.03 | m/s | 12.1511 | 0.0093783 | 14.0914 |  | -2 | 94 | 0.094 | 149.9088 | 6.5889 | 5.3436 | 0.020547 | 36.4378 | 0.25797
2025-05-19 22:26 | 1457 | Remove | 2025-05-19 | 22:26 | ST | GS | - | 92.5 | g | 0 | 114.2 | 11.373 | 1122.3 | 64485 | 12:10 | 28.7 | 2.16 m/s | 23.9 | 29.9 | 4.13 m/s | 19.3 |  | 2.16 | m/s |  | 4.13 | m/s | 12.1594 | 0.0093525 | 14.1008 |  | -1.5 | 92.5 | 0.0925 | 152.4408 | 6.7585 | 5.8267 | 0.021474 | 36.4592 | 0.25371
2025-05-19 22:27 | 1458 | Remove | 2025-05-19 | 22:27 | ST | GS | - | 96.5 | g | 0 | 114.1 | 11.407 | 1126.9 | 64494 | 12:10 | 28.7 | 2.31 m/s | 24.1 | 29.9 | 3.9 m/s | 17.3 |  | 2.31 | m/s |  | 3.9 | m/s | 12.1678 | 0.0093908 | 14.1102 |  | 4 | 96.5 | 0.0965 | 146.2193 | 6.8151 | 5.2229 | 0.023157 | 36.4824 | 0.26451
2025-05-19 22:27 | 1459 | Remove | 2025-05-19 | 22:27 | ST | GS | - | 96.5 | g | 0 | 114.2 | 11.385 | 1124.5 | 64503 | 12:11 | 28.7 | 2.38 m/s | 23.5 | 29.9 | 4.03 m/s | 17.3 |  | 2.38 | m/s |  | 4.03 | m/s | 12.1761 | 0.0093708 | 14.1195 |  | 0 | 96.5 | 0.0965 | 146.3165 | 6.6454 | 5.2229 | 0.023265 | 36.5057 | 0.26434
2025-05-19 22:28 | 1460 | Remove | 2025-05-19 | 22:28 | ST | GS | - | 95 | g | 0 | 114.2 | 11.369 | 1121.9 | 64513 | 12:11 | 28.7 | 2.16 m/s | 24.1 | 29.9 | 3.97 m/s | 19.4 |  | 2.16 | m/s |  | 3.97 | m/s | 12.1844 | 0.0093492 | 14.1289 |  | -1.5 | 95 | 0.095 | 148.7251 | 6.8151 | 5.8568 | 0.021653 | 36.5273 | 0.26008
2025-05-19 22:28 | 1461 | Remove | 2025-05-19 | 22:28 | US | GS | - | 94.5 | g | 0 | 114.2 | 11.385 | 1124.6 | 64522 | 12:12 | 28.7 | 2.2 m/s | 24.7 | 29.9 | 3.96 m/s | 18 |  | 2.2 | m/s |  | 3.96 | m/s | 12.1928 | 0.0093717 | 14.1383 |  | -0.5 | 94.5 | 0.0945 | 149.6112 | 6.9848 | 5.4342 | 0.022604 | 36.5499 | 0.25855
2025-05-19 22:29 | 1462 | Remove | 2025-05-19 | 22:29 | US | GS | - | 97 | g | 0 | 114.2 | 11.363 | 1121.1 | 64531 | 12:12 | 28.7 | 2.33 m/s | 23.3 | 29.9 | 3.93 m/s | 20.9 |  | 2.33 | m/s |  | 3.93 | m/s | 12.2011 | 0.0093425 | 14.1476 |  | 2.5 | 97 | 0.097 | 145.8516 | 6.5889 | 6.3097 | 0.022582 | 36.5725 | 0.26523
2025-05-19 22:29 | 1463 | Remove | 2025-05-19 | 22:29 | ST | GS | - | 94.5 | g | 0 | 114.3 | 11.336 | 1118.5 | 64541 | 12:13 | 28.7 | 2.44 m/s | 24.3 | 29.9 | 4.0 m/s | 19.1 |  | 2.44 | m/s |  | 4 | m/s | 12.2094 | 0.0093208 | 14.1569 |  | -2.5 | 94.5 | 0.0945 | 149.8087 | 6.8716 | 5.7663 | 0.024663 | 36.5972 | 0.25822
2025-05-19 22:30 | 1464 | Remove | 2025-05-19 | 22:30 | ST | GS | - | 93 | g | 0 | 114.2 | 11.364 | 1121.6 | 64550 | 12:13 | 28.7 | 2.31 m/s | 25.2 | 29.9 | 4.15 m/s | 17.6 |  | 2.31 | m/s |  | 4.15 | m/s | 12.2181 | 0.0093467 | 14.1663 |  | -1.5 | 93 | 0.093 | 152.3255 | 7.1261 | 5.3134 | 0.024214 | 36.6214 | 0.25395
2025-05-19 22:30 | 1465 | Remove | 2025-05-19 | 22:30 | ST | GS | - | 96 | g | 0 | 114.2 | 11.363 | 1122.5 | 64560 | 12:14 | 28.7 | 2.34 m/s | 25.1 | 29.9 | 3.94 m/s | 17.8 |  | 2.34 | m/s |  | 3.94 | m/s | 12.2264 | 0.0093542 | 14.1756 |  | 3 | 96 | 0.096 | 147.6627 | 7.0979 | 5.3738 | 0.024431 | 36.6458 | 0.26197
2025-05-19 22:31 | 1466 | Remove | 2025-05-19 | 22:31 | ST | GS | - | 96 | g | 0 | 114.3 | 11.353 | 1120.1 | 64569 | 12:14 | 28.7 | 2.34 m/s | 23.5 | 29.9 | 4.0 m/s | 18.7 |  | 2.34 | m/s |  | 4 | m/s | 12.2347 | 0.0093342 | 14.185 |  | 0 | 96 | 0.096 | 147.76 | 6.6454 | 5.6455 | 0.022874 | 36.6687 | 0.2618
2025-05-19 22:31 | 1467 | Remove | 2025-05-19 | 22:31 | ST | GS | - | 96.5 | g | 0 | 114.2 | 11.343 | 1119.6 | 64578 | 12:15 | 28.7 | 2.18 m/s | 24.6 | 29.9 | 4.04 m/s | 18.6 |  | 2.18 | m/s |  | 4.04 | m/s | 12.2431 | 0.00933 | 14.1943 |  | 0.5 | 96.5 | 0.0965 | 147.0911 | 6.9565 | 5.6153 | 0.022307 | 36.691 | 0.26301
2025-05-19 22:32 | 1468 | Remove | 2025-05-19 | 22:32 | ST | GS | - | 96.5 | g | 0 | 114.3 | 11.374 | 1123 | 64588 | 12:15 | 28.7 | 2.27 m/s | 25.9 | 29.9 | 3.98 m/s | 17.5 |  | 2.27 | m/s |  | 3.98 | m/s | 12.2514 | 0.0093583 | 14.2036 |  | 0 | 96.5 | 0.0965 | 147.188 | 7.3241 | 5.2832 | 0.024456 | 36.7154 | 0.26283
2025-05-19 22:32 | 1469 | Remove | 2025-05-19 | 22:32 | ST | GS | - | 95.5 | g | 0 | 114.3 | 11.349 | 1120.2 | 64597 | 12:16 | 28.7 | 2.45 m/s | 24.3 | 29.9 | 3.96 m/s | 18.8 |  | 2.45 | m/s |  | 3.96 | m/s | 12.2597 | 0.009335 | 14.213 |  | -1 | 95.5 | 0.0955 | 148.827 | 6.8716 | 5.6757 | 0.024764 | 36.7402 | 0.25993
2025-05-19 22:33 | 1470 | Remove | 2025-05-19 | 22:33 | ST | GS | - | 98.5 | g | 0 | 114.1 | 11.335 | 1117.9 | 64606 | 12:16 | 28.7 | 2.15 m/s | 24.8 | 29.9 | 3.96 m/s | 18.6 |  | 2.15 | m/s |  | 3.96 | m/s | 12.2681 | 0.0093158 | 14.2223 |  | 3 | 98.5 | 0.0985 | 144.3888 | 7.013 | 5.6153 | 0.022179 | 36.7624 | 0.26794
2025-05-19 22:33 | 1471 | Keep | 2025-05-19 | 22:33 | US | GS | - | 98 | g | 0 | 114.2 | 11.348 | 1119.8 | 64616 | 12:17 | 28.7 | 2.35 m/s | 24.5 | 29.9 | 3.85 m/s | 18.7 |  | 2.35 | m/s |  | 3.85 | m/s | 12.2764 | 0.0093317 | 14.2316 |  | -0.5 | 98 | 0.098 | 145.2207 | 6.9282 | 5.6455 | 0.023949 | 36.7863 | 0.2664
2025-05-19 22:34 | 1472 | Remove | 2025-05-19 | 22:34 | ST | GS | - | 98.5 | g | 0 | 114.2 | 11.343 | 1118.9 | 64625 | 12:17 | 28.7 | 2.09 m/s | 23.6 | 29.8 | 3.9 m/s | 19 |  | 2.09 | m/s |  | 3.9 | m/s | 12.2847 | 0.0093242 | 14.241 |  | 0.5 | 98.5 | 0.0985 | 144.5782 | 6.6737 | 5.705 | 0.020517 | 36.8069 | 0.26761
2025-05-19 22:34 | 1473 | Remove | 2025-05-19 | 22:34 | ST | GS | - | 96 | g | 0 | 114.3 | 11.329 | 1117.6 | 64634 | 12:18 | 28.7 | 2.3 m/s | 24.4 | 29.8 | 3.96 m/s | 18.6 |  | 2.3 | m/s |  | 3.96 | m/s | 12.2931 | 0.0093133 | 14.2503 |  | -2.5 | 96 | 0.096 | 148.4403 | 6.8999 | 5.5849 | 0.023344 | 36.8302 | 0.26066
2025-05-19 22:35 | 1474 | Remove | 2025-05-19 | 22:35 | ST | GS | - | 94 | g | 0 | 114.1 | 11.317 | 1115.4 | 64644 | 12:18 | 28.6 | 2.23 m/s | 26.5 | 29.8 | 4.1 m/s | 19 |  | 2.23 | m/s |  | 4.1 | m/s | 12.3014 | 0.009295 | 14.2596 |  | -2 | 94 | 0.094 | 151.6974 | 7.4528 | 5.705 | 0.024447 | 36.8546 | 0.25506
2025-05-19 22:35 | 1475 | Remove | 2025-05-19 | 22:35 | ST | GS | - | 96.5 | g | 0 | 114.3 | 11.332 | 1118.1 | 64653 | 12:19 | 28.6 | 2.25 m/s | 25.1 | 29.8 | 3.96 m/s | 18.5 |  | 2.25 | m/s |  | 3.96 | m/s | 12.3097 | 0.0093175 | 14.2689 |  | 2.5 | 96.5 | 0.0965 | 147.864 | 7.0591 | 5.5549 | 0.023363 | 36.878 | 0.26167
2025-05-19 22:36 | 1476 | Remove | 2025-05-19 | 22:36 | US | GS | - | 94.5 | g | 0 | 114.2 | 11.305 | 1113.7 | 64662 | 12:19 | 28.6 | 2.37 m/s | 24.8 | 29.8 | 4.03 m/s | 19 |  | 2.37 | m/s |  | 4.03 | m/s | 12.3181 | 0.0092808 | 14.2782 |  | -2 | 94.5 | 0.0945 | 151.0916 | 6.9747 | 5.705 | 0.024315 | 36.9023 | 0.25608
2025-05-19 22:36 | 1477 | Remove | 2025-05-19 | 22:36 | ST | GS | - | 96 | g | 0 | 114.3 | 11.325 | 1116.1 | 64672 | 12:20 | 28.6 | 2.09 m/s | 26.2 | 29.8 | 4.06 m/s | 19 |  | 2.09 | m/s |  | 4.06 | m/s | 12.3264 | 0.0093008 | 14.2875 |  | 1.5 | 96 | 0.096 | 148.8277 | 7.3685 | 5.705 | 0.022653 | 36.925 | 0.25999
2025-05-19 22:37 | 1478 | Remove | 2025-05-19 | 22:37 | US | GS | - | 96.5 | g | 0 | 114.3 | 11.338 | 1118.2 | 64681 | 12:20 | 28.6 | 2.26 m/s | 24.4 | 29.8 | 3.92 m/s | 18.7 |  | 2.26 | m/s |  | 3.92 | m/s | 12.3347 | 0.0093183 | 14.2968 |  | 0.5 | 96.5 | 0.0965 | 148.1531 | 6.8622 | 5.615 | 0.022813 | 36.9478 | 0.26118
2025-05-19 22:37 | 1479 | Remove | 2025-05-19 | 22:37 | ST | GS | - | 94 | g | 0 | 114.3 | 11.327 | 1117.1 | 64690 | 12:21 | 28.6 | 2.23 m/s | 24.7 | 29.8 | 4.13 m/s | 18.2 |  | 2.23 | m/s |  | 4.13 | m/s | 12.3431 | 0.0093092 | 14.3061 |  | -2.5 | 94 | 0.094 | 152.1924 | 6.9466 | 5.4648 | 0.022787 | 36.9706 | 0.25426
2025-05-19 22:38 | 1480 | Remove | 2025-05-19 | 22:38 | ST | GS | - | 95 | g | 0 | 114.4 | 11.312 | 1114.7 | 64700 | 12:21 | 28.6 | 2.26 m/s | 26.1 | 29.8 | 4.03 m/s | 20.3 |  | 2.26 | m/s |  | 4.03 | m/s | 12.3514 | 0.0092892 | 14.3154 |  | 1 | 95 | 0.095 | 150.6882 | 7.3403 | 6.0954 | 0.024402 | 36.995 | 0.25679
2025-05-19 22:38 | 1481 | Remove | 2025-05-19 | 22:38 | US | GS | - | 98.5 | g | 0 | 114.4 | 11.32 | 1115.7 | 64709 | 12:22 | 28.6 | 2.22 m/s | 24.4 | 29.8 | 3.95 m/s | 19.6 |  | 2.22 | m/s |  | 3.95 | m/s | 12.36 | 0.0092975 | 14.3247 |  | 3.5 | 98.5 | 0.0985 | 145.4282 | 6.8622 | 5.8852 | 0.022409 | 37.0174 | 0.26609
2025-05-19 22:39 | 1482 | Remove | 2025-05-19 | 22:39 | ST | GS | - | 96 | g | 0 | 114.4 | 11.338 | 1117.9 | 64718 | 12:22 | 28.6 | 2.3 m/s | 24.8 | 29.8 | 3.98 m/s | 18.1 |  | 2.3 | m/s |  | 3.98 | m/s | 12.3683 | 0.0093158 | 14.334 |  | -2.5 | 96 | 0.096 | 149.3124 | 6.9747 | 5.4348 | 0.023597 | 37.041 | 0.25917
2025-05-19 22:39 | 1483 | Remove | 2025-05-19 | 22:39 | ST | GS | - | 100 | g | 0 | 114.4 | 11.331 | 1118.3 | 64728 | 12:23 | 28.6 | 2.19 m/s | 24.3 | 29.8 | 3.98 m/s | 18.3 |  | 2.19 | m/s |  | 3.98 | m/s | 12.3767 | 0.0093192 | 14.3433 |  | 4 | 100 | 0.1 | 143.4331 | 6.8341 | 5.4949 | 0.022015 | 37.063 | 0.26981
2025-05-19 22:40 | 1484 | Remove | 2025-05-19 | 22:40 | ST | GS | - | 99.5 | g | 0 | 114.4 | 11.309 | 1114.6 | 64737 | 12:23 | 28.6 | 2.38 m/s | 24.1 | 29.8 | 3.98 m/s | 20.3 |  | 2.38 | m/s |  | 3.98 | m/s | 12.385 | 0.0092883 | 14.3526 |  | -0.5 | 99.5 | 0.0995 | 144.2472 | 6.7779 | 6.0954 | 0.023729 | 37.0867 | 0.26829
2025-05-19 22:40 | 1485 | Remove | 2025-05-19 | 22:40 | ST | GS | - | 97.5 | g | 0 | 114.4 | 11.313 | 1114.8 | 64746 | 12:24 | 28.6 | 2.42 m/s | 24.8 | 29.8 | 4.03 m/s | 19.6 |  | 2.42 | m/s |  | 4.03 | m/s | 12.3933 | 0.00929 | 14.3619 |  | -2 | 97.5 | 0.0975 | 147.3014 | 6.9747 | 5.8852 | 0.024828 | 37.1116 | 0.26272
2025-05-19 22:41 | 1486 | Remove | 2025-05-19 | 22:41 | ST | GS | - | 97 | g | 0 | 114.4 | 11.325 | 1116.9 | 64756 | 12:24 | 28.6 | 2.22 m/s | 24.4 | 29.8 | 4.01 m/s | 18.3 |  | 2.22 | m/s |  | 4.01 | m/s | 12.4017 | 0.0093075 | 14.3712 |  | -0.5 | 97 | 0.097 | 148.1566 | 6.8622 | 5.4949 | 0.022409 | 37.134 | 0.26122
2025-05-19 22:41 | 1487 | Remove | 2025-05-19 | 22:41 | ST | GS | - | 98.5 | g | 0 | 114.4 | 11.325 | 1116.9 | 64765 | 12:25 | 28.6 | 2.26 m/s | 25.2 | 29.8 | 3.97 m/s | 19.1 |  | 2.26 | m/s |  | 3.97 | m/s | 12.41 | 0.0093075 | 14.3805 |  | 1.5 | 98.5 | 0.0985 | 145.9949 | 7.0872 | 5.7351 | 0.023561 | 37.1575 | 0.26509
2025-05-19 22:42 | 1488 | Remove | 2025-05-19 | 22:42 | ST | GS | - | 96.5 | g | 0 | 114.4 | 11.299 | 1113 | 64774 | 12:25 | 28.6 | 2.08 m/s | 24.3 | 29.8 | 4.07 m/s | 18.6 |  | 2.08 | m/s |  | 4.07 | m/s | 12.4183 | 0.009275 | 14.3898 |  | -2 | 96.5 | 0.0965 | 149.1169 | 6.8341 | 5.5849 | 0.02091 | 37.1784 | 0.25956
2025-05-19 22:42 | 1489 | Remove | 2025-05-19 | 22:42 | US | GS | - | 98.5 | g | 0 | 114.4 | 11.306 | 1114.5 | 64784 | 12:26 | 28.6 | 2.3 m/s | 24.7 | 29.8 | 3.93 m/s | 18.7 |  | 2.3 | m/s |  | 3.93 | m/s | 12.4267 | 0.0092875 | 14.3991 |  | 2 | 98.5 | 0.0985 | 146.1834 | 6.9466 | 5.615 | 0.023502 | 37.2019 | 0.26477
2025-05-19 22:43 | 1490 | Remove | 2025-05-19 | 22:43 | ST | GS | - | 97 | g | 0 | 114.4 | 11.329 | 1117.1 | 64793 | 12:26 | 28.6 | 2.16 m/s | 24.2 | 29.8 | 3.97 m/s | 18.3 |  | 2.16 | m/s |  | 3.97 | m/s | 12.435 | 0.0093092 | 14.4084 |  | -1.5 | 97 | 0.097 | 148.5399 | 6.806 | 5.4949 | 0.021625 | 37.2236 | 0.26059
2025-05-19 22:43 | 1491 | Remove | 2025-05-19 | 22:43 | ST | GS | - | 101 | g | 0 | 114.4 | 11.335 | 1117.6 | 64802 | 12:27 | 28.6 | 2.3 m/s | 23.8 | 29.8 | 3.97 m/s | 18.2 |  | 2.3 | m/s |  | 3.97 | m/s | 12.4433 | 0.0093133 | 14.4177 |  | 4 | 101 | 0.101 | 142.7494 | 6.6935 | 5.4648 | 0.022646 | 37.2462 | 0.27117
2025-05-19 22:44 | 1492 | Remove | 2025-05-19 | 22:44 | ST | GS | - | 98 | g | 0 | 114.3 | 11.33 | 1117.3 | 64812 | 12:27 | 28.6 | 2.26 m/s | 24.4 | 29.8 | 3.98 m/s | 18.6 |  | 2.26 | m/s |  | 3.98 | m/s | 12.4517 | 0.0093108 | 14.427 |  | -3 | 98 | 0.098 | 147.2143 | 6.8622 | 5.5849 | 0.022813 | 37.269 | 0.26295
2025-05-19 22:44 | 1493 | Remove | 2025-05-19 | 22:44 | ST | GS | - | 100.5 | g | 0 | 114.4 | 11.321 | 1116.6 | 64821 | 12:28 | 28.6 | 2.25 m/s | 24.8 | 29.8 | 3.94 m/s | 18.8 |  | 2.25 | m/s |  | 3.94 | m/s | 12.46 | 0.009305 | 14.4363 |  | 2.5 | 100.5 | 0.1005 | 143.6448 | 6.9747 | 5.645 | 0.023084 | 37.2921 | 0.26949
2025-05-19 22:45 | 1494 | Remove | 2025-05-19 | 22:45 | US | GS | - | 97.5 | g | 0 | 114.3 | 11.329 | 1117 | 64830 | 12:28 | 28.6 | 2.26 m/s | 24.1 | 29.8 | 3.93 m/s | 18.1 |  | 2.26 | m/s |  | 3.93 | m/s | 12.4683 | 0.0093083 | 14.4456 |  | -3 | 97.5 | 0.0975 | 148.1601 | 6.7779 | 5.4348 | 0.022532 | 37.3146 | 0.26129
2025-05-19 22:45 | 1495 | Remove | 2025-05-19 | 22:45 | US | GS | - | 96.5 | g | 0 | 114.4 | 11.319 | 1115.4 | 64840 | 12:29 | 28.6 | 2.25 m/s | 23.7 | 29.8 | 3.96 m/s | 18.4 |  | 2.25 | m/s |  | 3.96 | m/s | 12.4767 | 0.009295 | 14.4549 |  | -1 | 96.5 | 0.0965 | 149.7918 | 6.6654 | 5.5249 | 0.02206 | 37.3367 | 0.25846
2025-05-19 22:46 | 1496 | Remove | 2025-05-19 | 22:46 | US | GS | - | 99 | g | 0 | 114.3 | 11.33 | 1117.2 | 64849 | 12:29 | 28.6 | 2.27 m/s | 25 | 29.8 | 3.94 m/s | 18.8 |  | 2.27 | m/s |  | 3.94 | m/s | 12.485 | 0.00931 | 14.4642 |  | 2.5 | 99 | 0.099 | 146.1032 | 7.031 | 5.645 | 0.023477 | 37.3602 | 0.26499
2025-05-19 22:46 | 1497 | Remove | 2025-05-19 | 22:46 | US | GS | - | 100 | g | 0 | 114.4 | 11.33 | 1117.7 | 64858 | 12:30 | 28.6 | 2.25 m/s | 25.2 | 29.8 | 4.0 m/s | 18.6 |  | 2.25 | m/s |  | 4 | m/s | 12.4933 | 0.0093142 | 14.4735 |  | 1 | 100 | 0.1 | 144.7353 | 7.0872 | 5.5849 | 0.023456 | 37.3836 | 0.2675
2025-05-19 22:47 | 1498 | Remove | 2025-05-19 | 22:47 | ST | GS | - | 95.5 | g | 0 | 114.4 | 11.306 | 1113.7 | 64868 | 12:30 | 28.6 | 2.23 m/s | 26.2 | 29.8 | 4.07 m/s | 19.2 |  | 2.23 | m/s |  | 4.07 | m/s | 12.5019 | 0.0092808 | 14.4828 |  | -4.5 | 95.5 | 0.0955 | 151.6525 | 7.3685 | 5.7651 | 0.02417 | 37.4078 | 0.25529
2025-05-19 22:47 | 1499 | Remove | 2025-05-19 | 22:47 | ST | GS | - | 98.5 | g | 0 | 114.3 | 11.327 | 1117.1 | 64877 | 12:31 | 28.6 | 2.27 m/s | 24.5 | 29.8 | 3.98 m/s | 18 |  | 2.27 | m/s |  | 3.98 | m/s | 12.5103 | 0.0093092 | 14.4921 |  | 3 | 98.5 | 0.0985 | 147.1281 | 6.8904 | 5.4048 | 0.023008 | 37.4308 | 0.26315
2025-05-19 22:48 | 1500 | Remove | 2025-05-19 | 22:48 | ST | GS | - | 97 | g | 0 | 114.3 | 11.342 | 1119.3 | 64886 | 12:31 | 28.6 | 2.16 m/s | 23.7 | 29.8 | 4.0 m/s | 18.2 |  | 2.16 | m/s |  | 4 | m/s | 12.5186 | 0.0093275 | 14.5014 |  | -1.5 | 97 | 0.097 | 149.4995 | 6.6654 | 5.4648 | 0.021178 | 37.452 | 0.259
2025-05-19 22:48 | 1501 | Keep | 2025-05-19 | 22:48 | ST | GS | - | 97 | g | 0 | 114.2 | 11.325 | 1116.5 | 64896 | 12:32 | 28.6 | 2.41 m/s | 23.6 | 29.8 | 3.98 m/s | 18.7 |  | 2.41 | m/s |  | 3.98 | m/s | 12.5269 | 0.0093042 | 14.5108 |  | 0 | 97 | 0.097 | 149.5954 | 6.6372 | 5.615 | 0.023529 | 37.4755 | 0.25884
2025-05-19 22:49 | 1502 | Remove | 2025-05-19 | 22:49 | ST | GS | - | 95.5 | g | 0 | 114.3 | 11.321 | 1116.3 | 64905 | 12:32 | 28.6 | 2.12 m/s | 23.4 | 29.8 | 3.96 m/s | 18.4 |  | 2.12 | m/s |  | 3.96 | m/s | 12.5353 | 0.0093025 | 14.5201 |  | -1.5 | 95.5 | 0.0955 | 152.0425 | 6.581 | 5.5249 | 0.020522 | 37.496 | 0.25469
2025-05-19 22:49 | 1503 | Remove | 2025-05-19 | 22:49 | ST | GS | - | 97.5 | g | 0 | 114.4 | 11.309 | 1114.4 | 64914 | 12:33 | 28.6 | 2.31 m/s | 23.8 | 29.8 | 4.0 m/s | 19.6 |  | 2.31 | m/s |  | 4 | m/s | 12.5436 | 0.0092867 | 14.5293 |  | 2 | 97.5 | 0.0975 | 149.0189 | 6.6935 | 5.8852 | 0.022744 | 37.5188 | 0.25987
2025-05-19 22:50 | 1504 | Remove | 2025-05-19 | 22:50 | ST | GS | - | 96 | g | 0 | 114.3 | 11.283 | 1111.7 | 64924 | 12:33 | 28.6 | 2.4 m/s | 25.3 | 29.8 | 4.12 m/s | 20.6 |  | 2.4 | m/s |  | 4.12 | m/s | 12.5519 | 0.0092642 | 14.5386 |  | -1.5 | 96 | 0.096 | 151.4438 | 7.1153 | 6.1855 | 0.025119 | 37.5439 | 0.2557
2025-05-19 22:50 | 1505 | Remove | 2025-05-19 | 22:50 | ST | GS | - | 98 | g | 0 | 114.3 | 11.318 | 1115.6 | 64933 | 12:34 | 28.6 | 2.31 m/s | 25.2 | 29.8 | 3.97 m/s | 18.8 |  | 2.31 | m/s |  | 3.97 | m/s | 12.5603 | 0.0092967 | 14.5479 |  | 2 | 98 | 0.098 | 148.448 | 7.0872 | 5.645 | 0.024082 | 37.568 | 0.26086
2025-05-19 22:51 | 1506 | Remove | 2025-05-19 | 22:51 | ST | GS | - | 101 | g | 0 | 114.3 | 11.317 | 1116.3 | 64942 | 12:34 | 28.6 | 2.15 m/s | 24.4 | 29.8 | 4.01 m/s | 18.9 |  | 2.15 | m/s |  | 4.01 | m/s | 12.5686 | 0.0093025 | 14.5572 |  | 3 | 101 | 0.101 | 144.1307 | 6.8622 | 5.675 | 0.021702 | 37.5897 | 0.26869
2025-05-19 22:51 | 1507 | Remove | 2025-05-19 | 22:51 | ST | GS | - | 96 | g | 0 | 114.1 | 11.322 | 1114.7 | 64952 | 12:35 | 28.6 | 2.31 m/s | 23.8 | 29.8 | 3.98 m/s | 18.2 |  | 2.31 | m/s |  | 3.98 | m/s | 12.5769 | 0.0092892 | 14.5665 |  | -5 | 96 | 0.096 | 151.7343 | 6.6935 | 5.4648 | 0.022744 | 37.6124 | 0.25523
2025-05-19 22:52 | 1508 | Remove | 2025-05-19 | 22:52 | ST | GS | - | 102 | g | 0 | 114.2 | 11.336 | 1116.6 | 64961 | 12:35 | 28.6 | 2.37 m/s | 24.3 | 29.8 | 3.8 m/s | 18.3 |  | 2.37 | m/s |  | 3.8 | m/s | 12.5853 | 0.009305 | 14.5758 |  | 6 | 102 | 0.102 | 142.9 | 6.8341 | 5.4949 | 0.023825 | 37.6363 | 0.27102
2025-05-19 22:52 | 1509 | Remove | 2025-05-19 | 22:52 | US | GS | - | 97.5 | g | 0 | 114.2 | 11.337 | 1117.6 | 64970 | 12:36 | 28.6 | 2.7 m/s | 23.3 | 29.8 | 4.04 m/s | 18.6 |  | 2.7 | m/s |  | 4.04 | m/s | 12.5936 | 0.0093133 | 14.5851 |  | -4.5 | 97.5 | 0.0975 | 149.5909 | 6.5529 | 5.5849 | 0.026025 | 37.6623 | 0.25888
2025-05-19 22:53 | 1510 | Remove | 2025-05-19 | 22:53 | US | GS | - | 98.5 | g | 0 | 114.2 | 11.316 | 1114.7 | 64980 | 12:36 | 28.6 | 2.35 m/s | 23.8 | 29.8 | 3.9 m/s | 19.4 |  | 2.35 | m/s |  | 3.9 | m/s | 12.6019 | 0.0092892 | 14.5944 |  | 1 | 98.5 | 0.0985 | 148.1665 | 6.6935 | 5.8251 | 0.023138 | 37.6854 | 0.26137
2025-05-19 22:53 | 1511 | Remove | 2025-05-19 | 22:53 | US | GS | - | 99.5 | g | 0 | 114.2 | 11.322 | 1115.1 | 64989 | 12:37 | 28.6 | 2.2 m/s | 25 | 29.8 | 3.89 m/s | 18.6 |  | 2.2 | m/s |  | 3.89 | m/s | 12.6103 | 0.0092925 | 14.6037 |  | 1 | 99.5 | 0.0995 | 146.7708 | 7.031 | 5.5849 | 0.022753 | 37.7082 | 0.26387
2025-05-19 22:54 | 1512 | Remove | 2025-05-19 | 22:54 | ST | GS | - | 102.5 | g | 0 | 114.2 | 11.325 | 1116.1 | 64998 | 12:37 | 28.6 | 2.31 m/s | 23.8 | 29.8 | 4.04 m/s | 18.8 |  | 2.31 | m/s |  | 4.04 | m/s | 12.6186 | 0.0093008 | 14.613 |  | 3 | 102.5 | 0.1025 | 142.5658 | 6.6935 | 5.645 | 0.022744 | 37.7309 | 0.27166
2025-05-19 22:54 | 1513 | Remove | 2025-05-19 | 22:54 | ST | GS | - | 97 | g | 0 | 114.3 | 11.305 | 1113 | 65008 | 12:38 | 28.6 | 2.11 m/s | 24.2 | 29.8 | 4.16 m/s | 18.9 |  | 2.11 | m/s |  | 4.16 | m/s | 12.6269 | 0.009275 | 14.6223 |  | -5.5 | 97 | 0.097 | 150.745 | 6.806 | 5.675 | 0.021124 | 37.752 | 0.25694
2025-05-19 22:55 | 1514 | Remove | 2025-05-19 | 22:55 | ST | GS | - | 96 | g | 0 | 114.3 | 11.286 | 1110.5 | 65017 | 12:38 | 28.6 | 2.45 m/s | 25.5 | 29.8 | 4.15 m/s | 19.6 |  | 2.45 | m/s |  | 4.15 | m/s | 12.6353 | 0.0092542 | 14.6315 |  | -1 | 96 | 0.096 | 152.4117 | 7.1716 | 5.8852 | 0.025845 | 37.7779 | 0.25412
2025-05-19 22:55 | 1515 | Remove | 2025-05-19 | 22:55 | ST | GS | - | 100.5 | g | 0 | 114.2 | 11.301 | 1113.1 | 65026 | 12:39 | 28.6 | 2.3 m/s | 26.1 | 29.8 | 3.93 m/s | 20.2 |  | 2.3 | m/s |  | 3.93 | m/s | 12.6439 | 0.0092758 | 14.6408 |  | 4.5 | 100.5 | 0.1005 | 145.6796 | 7.3403 | 6.0654 | 0.024834 | 37.8027 | 0.26585
2025-05-19 22:56 | 1516 | Remove | 2025-05-19 | 22:56 | ST | GS | - | 97.5 | g | 0 | 114.3 | 11.303 | 1112.5 | 65035 | 12:39 | 28.6 | 2.31 m/s | 27.5 | 29.8 | 4.12 m/s | 19.7 |  | 2.31 | m/s |  | 4.12 | m/s | 12.6522 | 0.0092708 | 14.6501 |  | -3 | 97.5 | 0.0975 | 150.2571 | 7.7341 | 5.9152 | 0.02628 | 37.829 | 0.25774
2025-05-19 22:56 | 1517 | Remove | 2025-05-19 | 22:56 | ST | GS | - | 98 | g | 0 | 114.3 | 11.297 | 1112.6 | 65045 | 12:40 | 28.6 | 2.2 m/s | 28 | 29.8 | 4.0 m/s | 19.4 |  | 2.2 | m/s |  | 4 | m/s | 12.6606 | 0.0092717 | 14.6593 |  | 0.5 | 98 | 0.098 | 149.5851 | 7.8747 | 5.8251 | 0.025483 | 37.8545 | 0.25889
2025-05-19 22:57 | 1518 | Remove | 2025-05-19 | 22:57 | ST | GS | - | 96 | g | 0 | 114.2 | 11.317 | 1114.6 | 65054 | 12:40 | 28.6 | 2.06 m/s | 25.6 | 29.8 | 3.98 m/s | 18.7 |  | 2.06 | m/s |  | 3.98 | m/s | 12.6689 | 0.0092883 | 14.6686 |  | -2 | 96 | 0.096 | 152.7982 | 7.1997 | 5.615 | 0.021816 | 37.8763 | 0.25346
2025-05-19 22:57 | 1519 | Remove | 2025-05-19 | 22:57 | ST | GS | - | 95.5 | g | 0 | 114.2 | 11.318 | 1114.5 | 65063 | 12:41 | 28.6 | 2.35 m/s | 25.2 | 29.8 | 4.24 m/s | 18.7 |  | 2.35 | m/s |  | 4.24 | m/s | 12.6772 | 0.0092875 | 14.6779 |  | -0.5 | 95.5 | 0.0955 | 153.6955 | 7.0872 | 5.615 | 0.024499 | 37.9008 | 0.25197
2025-05-19 22:58 | 1520 | Remove | 2025-05-19 | 22:58 | ST | GS | - | 95.5 | g | 0 | 114.3 | 11.313 | 1114.1 | 65073 | 12:41 | 28.6 | 2.25 m/s | 24.5 | 29.8 | 4.1 m/s | 18.7 |  | 2.25 | m/s |  | 4.1 | m/s | 12.6856 | 0.0092842 | 14.6872 |  | 0 | 95.5 | 0.0955 | 153.7927 | 6.8904 | 5.615 | 0.022805 | 37.9236 | 0.25182
2025-05-19 22:58 | 1521 | Remove | 2025-05-19 | 22:58 | ST | GS | - | 100.5 | g | 0 | 114.3 | 11.311 | 1114.4 | 65082 | 12:42 | 28.6 | 2.12 m/s | 25.2 | 29.8 | 4.04 m/s | 19.6 |  | 2.12 | m/s |  | 4.04 | m/s | 12.6939 | 0.0092867 | 14.6965 |  | 5 | 100.5 | 0.1005 | 146.2337 | 7.0872 | 5.8852 | 0.022101 | 37.9457 | 0.26485
2025-05-19 22:59 | 1522 | Remove | 2025-05-19 | 22:59 | ST | GS | - | 101.5 | g | 0 | 114.3 | 11.324 | 1116.3 | 65091 | 12:42 | 28.6 | 2.16 m/s | 24.7 | 29.8 | 4.03 m/s | 17.7 |  | 2.16 | m/s |  | 4.03 | m/s | 12.7022 | 0.0093025 | 14.7058 |  | 1 | 101.5 | 0.1015 | 144.8846 | 6.9466 | 5.3147 | 0.022071 | 37.9678 | 0.26733
2025-05-19 22:59 | 1523 | Remove | 2025-05-19 | 22:59 | ST | GS | - | 103 | g | 0 | 114.3 | 11.329 | 1117.1 | 65101 | 12:43 | 28.6 | 2.19 m/s | 23.7 | 29.8 | 3.89 m/s | 19.8 |  | 2.19 | m/s |  | 3.89 | m/s | 12.7106 | 0.0093092 | 14.7151 |  | 1.5 | 103 | 0.103 | 142.865 | 6.6654 | 5.9452 | 0.021472 | 37.9892 | 0.27113
2025-05-19 23:00 | 1524 | Remove | 2025-05-19 | 23:00 | ST | GS | - | 99 | g | 0 | 114.4 | 11.325 | 1117.1 | 65110 | 12:43 | 28.6 | 2.31 m/s | 25.5 | 29.8 | 3.97 m/s | 18.3 |  | 2.31 | m/s |  | 3.97 | m/s | 12.7189 | 0.0093092 | 14.7244 |  | -4 | 99 | 0.099 | 148.7314 | 7.1716 | 5.4949 | 0.024369 | 38.0136 | 0.26043
2025-05-19 23:00 | 1525 | Remove | 2025-05-19 | 23:00 | ST | GS | - | 100 | g | 0 | 114.3 | 11.307 | 1114.1 | 65119 | 12:44 | 28.6 | 2.3 m/s | 23.8 | 29.8 | 3.98 m/s | 20.2 |  | 2.3 | m/s |  | 3.98 | m/s | 12.7272 | 0.0092842 | 14.7337 |  | 1 | 100 | 0.1 | 147.3369 | 6.6935 | 6.0654 | 0.022646 | 38.0363 | 0.26291
2025-05-19 23:01 | 1526 | Remove | 2025-05-19 | 23:01 | ST | GS | - | 98.5 | g | 0 | 114.4 | 11.338 | 1117.7 | 65129 | 12:44 | 28.6 | 2.26 m/s | 25.3 | 29.8 | 3.89 m/s | 17.8 |  | 2.26 | m/s |  | 3.89 | m/s | 12.7356 | 0.0093142 | 14.743 |  | -1.5 | 98.5 | 0.0985 | 149.6752 | 7.1153 | 5.3447 | 0.023654 | 38.0599 | 0.2588
2025-05-19 23:01 | 1527 | Remove | 2025-05-19 | 23:01 | ST | GS | - | 96 | g | 0 | 114.4 | 11.313 | 1114.8 | 65138 | 12:45 | 28.6 | 2.42 m/s | 24.3 | 29.8 | 3.89 m/s | 18.4 |  | 2.42 | m/s |  | 3.89 | m/s | 12.7439 | 0.00929 | 14.7523 |  | -2.5 | 96 | 0.096 | 153.6698 | 6.8341 | 5.5249 | 0.024328 | 38.0842 | 0.25207
2025-05-19 23:02 | 1528 | Remove | 2025-05-19 | 23:02 | US | GS | - | 103 | g | 0 | 114.4 | 11.327 | 1116.3 | 65147 | 12:45 | 28.6 | 2.38 m/s | 25.4 | 29.8 | 3.98 m/s | 19 |  | 2.38 | m/s |  | 3.98 | m/s | 12.7522 | 0.0093025 | 14.7616 |  | 7 | 103 | 0.103 | 143.3165 | 7.1435 | 5.705 | 0.025009 | 38.1093 | 0.27028
2025-05-19 23:02 | 1529 | Remove | 2025-05-19 | 23:02 | ST | GS | - | 98 | g | 0 | 114.5 | 11.31 | 1113.7 | 65156 | 12:46 | 28.6 | 2.13 m/s | 23.8 | 29.8 | 4.1 m/s | 18.9 |  | 2.13 | m/s |  | 4.1 | m/s | 12.7606 | 0.0092808 | 14.7709 |  | -5 | 98 | 0.098 | 150.7233 | 6.6935 | 5.675 | 0.020972 | 38.1302 | 0.25701
2025-05-19 23:03 | 1530 | Remove | 2025-05-19 | 23:03 | ST | GS | - | 97 | g | 0 | 114.4 | 11.307 | 1113.1 | 65166 | 12:46 | 28.6 | 2.3 m/s | 26.3 | 29.8 | 4.15 m/s | 19.2 |  | 2.3 | m/s |  | 4.15 | m/s | 12.7689 | 0.0092758 | 14.7802 |  | -1 | 97 | 0.097 | 152.3727 | 7.3966 | 5.7651 | 0.025024 | 38.1552 | 0.25422
2025-05-19 23:03 | 1531 | Keep | 2025-05-19 | 23:03 | US | GS | - | 101.5 | g | 0 | 114.4 | 11.302 | 1113.5 | 65175 | 12:47 | 28.6 | 2.51 m/s | 24.7 | 29.8 | 4.04 m/s | 19.7 |  | 2.51 | m/s |  | 4.04 | m/s | 12.7772 | 0.0092792 | 14.7894 |  | 4.5 | 101.5 | 0.1015 | 145.7087 | 6.9466 | 5.9152 | 0.025648 | 38.1809 | 0.26584
2025-05-19 23:04 | 1532 | Remove | 2025-05-19 | 23:04 | ST | GS | - | 96 | g | 0 | 114.4 | 11.304 | 1113.4 | 65185 | 12:47 | 28.6 | 2.27 m/s | 24.4 | 29.8 | 3.86 m/s | 19.6 |  | 2.27 | m/s |  | 3.86 | m/s | 12.7858 | 0.0092783 | 14.7987 |  | -5.5 | 96 | 0.096 | 154.1533 | 6.8622 | 5.8852 | 0.022914 | 38.2038 | 0.25128
2025-05-19 23:04 | 1533 | Remove | 2025-05-19 | 23:04 | ST | GS | - | 99 | g | 0 | 114.4 | 11.314 | 1114.5 | 65194 | 12:48 | 28.6 | 2.33 m/s | 24.8 | 29.8 | 3.98 m/s | 19.3 |  | 2.33 | m/s |  | 3.98 | m/s | 12.7942 | 0.0092875 | 14.808 |  | 3 | 99 | 0.099 | 149.5758 | 6.9747 | 5.7951 | 0.023905 | 38.2277 | 0.25897
2025-05-19 23:05 | 1534 | Remove | 2025-05-19 | 23:05 | ST | GS | - | 96.5 | g | 0 | 114.4 | 11.318 | 1114.9 | 65203 | 12:48 | 28.6 | 2.5 m/s | 25.1 | 29.8 | 3.94 m/s | 18.6 |  | 2.5 | m/s |  | 3.94 | m/s | 12.8025 | 0.0092908 | 14.8173 |  | -2.5 | 96.5 | 0.0965 | 153.5471 | 7.0591 | 5.5849 | 0.025959 | 38.2537 | 0.25226
2025-05-19 23:05 | 1535 | Remove | 2025-05-19 | 23:05 | ST | GS | - | 100 | g | 0 | 114.5 | 11.305 | 1113.8 | 65212 | 12:49 | 28.6 | 2.13 m/s | 23.9 | 29.8 | 4.0 m/s | 18.8 |  | 2.13 | m/s |  | 4 | m/s | 12.8108 | 0.0092817 | 14.8266 |  | 3.5 | 100 | 0.1 | 148.2657 | 6.7216 | 5.645 | 0.02106 | 38.2747 | 0.26127
2025-05-19 23:06 | 1536 | Remove | 2025-05-19 | 23:06 | ST | GS | - | 99 | g | 0 | 114.5 | 11.314 | 1115.1 | 65222 | 12:49 | 28.6 | 2.23 m/s | 25 | 29.8 | 4.01 m/s | 18.5 |  | 2.23 | m/s |  | 4.01 | m/s | 12.8192 | 0.0092925 | 14.8359 |  | -1 | 99 | 0.099 | 149.8572 | 7.031 | 5.5549 | 0.023063 | 38.2978 | 0.2585
2025-05-19 23:06 | 1537 | Remove | 2025-05-19 | 23:06 | US | GS | - | 98 | g | 0 | 114.5 | 11.309 | 1113.5 | 65231 | 12:50 | 28.6 | 2.16 m/s | 25.1 | 29.8 | 4.21 m/s | 18.7 |  | 2.16 | m/s |  | 4.21 | m/s | 12.8275 | 0.0092792 | 14.8451 |  | -1 | 98 | 0.098 | 151.4811 | 7.0591 | 5.615 | 0.022429 | 38.3202 | 0.25574
2025-05-19 23:07 | 1538 | Remove | 2025-05-19 | 23:07 | ST | GS | - | 97 | g | 0 | 114.5 | 11.28 | 1110.7 | 65240 | 12:50 | 28.6 | 2.23 m/s | 24 | 29.8 | 4.1 m/s | 20.5 |  | 2.23 | m/s |  | 4.1 | m/s | 12.8358 | 0.0092558 | 14.8544 |  | -1 | 97 | 0.097 | 153.1382 | 6.7497 | 6.1554 | 0.022141 | 38.3424 | 0.25298
2025-05-19 23:07 | 1539 | Remove | 2025-05-19 | 23:07 | US | GS | - | 100 | g | 0 | 114.5 | 11.288 | 1111.8 | 65250 | 12:51 | 28.6 | 2.19 m/s | 27.7 | 29.8 | 4.04 m/s | 18.9 |  | 2.19 | m/s |  | 4.04 | m/s | 12.8442 | 0.009265 | 14.8637 |  | 3 | 100 | 0.1 | 148.6367 | 7.7903 | 5.675 | 0.025096 | 38.3675 | 0.26064
2025-05-19 23:08 | 1540 | Remove | 2025-05-19 | 23:08 | ST | GS | - | 97.5 | g | 0 | 114.5 | 11.287 | 1110.7 | 65259 | 12:51 | 28.6 | 2.33 m/s | 24.2 | 29.8 | 3.93 m/s | 19.5 |  | 2.33 | m/s |  | 3.93 | m/s | 12.8525 | 0.0092558 | 14.8729 |  | -2.5 | 97.5 | 0.0975 | 152.5428 | 6.806 | 5.8552 | 0.023326 | 38.3908 | 0.25397
2025-05-19 23:08 | 1541 | Remove | 2025-05-19 | 23:08 | ST | GS | - | 97.5 | g | 0 | 114.6 | 11.283 | 1111.4 | 65268 | 12:52 | 28.6 | 2.25 m/s | 26.1 | 29.8 | 3.94 m/s | 20.2 |  | 2.25 | m/s |  | 3.94 | m/s | 12.8608 | 0.0092617 | 14.8822 |  | 0 | 97.5 | 0.0975 | 152.6378 | 7.3403 | 6.0654 | 0.024294 | 38.4151 | 0.25381
2025-05-19 23:09 | 1542 | Remove | 2025-05-19 | 23:09 | ST | GS | - | 98 | g | 0 | 114.5 | 11.313 | 1114.9 | 65277 | 12:52 | 28.6 | 2.27 m/s | 25.5 | 29.8 | 3.92 m/s | 18.8 |  | 2.27 | m/s |  | 3.92 | m/s | 12.8692 | 0.0092908 | 14.8915 |  | 0.5 | 98 | 0.098 | 151.9538 | 7.1716 | 5.645 | 0.023947 | 38.439 | 0.25495
2025-05-19 23:09 | 1543 | Remove | 2025-05-19 | 23:09 | ST | GS | - | 98 | g | 0 | 114.5 | 11.297 | 1112.6 | 65287 | 12:53 | 28.6 | 2.18 m/s | 25 | 29.8 | 4.03 m/s | 19.3 |  | 2.18 | m/s |  | 4.03 | m/s | 12.8775 | 0.0092717 | 14.9007 |  | 0 | 98 | 0.098 | 152.0484 | 7.031 | 5.7951 | 0.022546 | 38.4616 | 0.2548
2025-05-19 23:10 | 1544 | Remove | 2025-05-19 | 23:10 | US | GS | - | 98.5 | g | 0 | 114.5 | 11.29 | 1111.6 | 65296 | 12:53 | 28.6 | 2.37 m/s | 25.2 | 29.8 | 4.07 m/s | 19.7 |  | 2.37 | m/s |  | 4.07 | m/s | 12.8858 | 0.0092633 | 14.91 |  | 0.5 | 98.5 | 0.0985 | 151.3707 | 7.0872 | 5.9152 | 0.024707 | 38.4863 | 0.25594
2025-05-19 23:10 | 1545 | Remove | 2025-05-19 | 23:10 | ST | GS | - | 98.5 | g | 0 | 114.6 | 11.277 | 1110.7 | 65305 | 12:54 | 28.6 | 2.37 m/s | 25.7 | 29.7 | 4.12 m/s | 20.4 |  | 2.37 | m/s |  | 4.12 | m/s | 12.8942 | 0.0092558 | 14.9193 |  | 0 | 98.5 | 0.0985 | 151.4646 | 7.2278 | 6.0922 | 0.025198 | 38.5115 | 0.25577
2025-05-19 23:11 | 1546 | Remove | 2025-05-19 | 23:11 | ST | GS | - | 101 | g | 0 | 114.4 | 11.31 | 1114.9 | 65315 | 12:54 | 28.6 | 2.31 m/s | 25.6 | 29.7 | 4.2 m/s | 19.1 |  | 2.31 | m/s |  | 4.2 | m/s | 12.9025 | 0.0092908 | 14.9286 |  | 2.5 | 101 | 0.101 | 147.8075 | 7.1997 | 5.704 | 0.024464 | 38.5359 | 0.26209
2025-05-19 23:11 | 1547 | Remove | 2025-05-19 | 23:11 | ST | GS | - | 99.5 | g | 0 | 114.5 | 11.295 | 1112.7 | 65324 | 12:55 | 28.6 | 2.11 m/s | 27.1 | 29.8 | 3.98 m/s | 20.1 |  | 2.11 | m/s |  | 3.98 | m/s | 12.9108 | 0.0092725 | 14.9378 |  | -1.5 | 99.5 | 0.0995 | 150.1289 | 7.6216 | 6.0353 | 0.023655 | 38.5596 | 0.25804
2025-05-19 23:12 | 1548 | Remove | 2025-05-19 | 23:12 | ST | GS | - | 98.5 | g | 0 | 114.4 | 11.299 | 1113.6 | 65333 | 12:55 | 28.6 | 2.27 m/s | 26 | 29.8 | 4.0 m/s | 18.8 |  | 2.27 | m/s |  | 4 | m/s | 12.9194 | 0.00928 | 14.9471 |  | -1 | 98.5 | 0.0985 | 151.7473 | 7.3122 | 5.645 | 0.024416 | 38.584 | 0.25529
2025-05-19 23:12 | 1549 | Remove | 2025-05-19 | 23:12 | ST | GS | - | 100 | g | 0 | 114.5 | 11.283 | 1111.5 | 65343 | 12:56 | 28.6 | 2.4 m/s | 24.3 | 29.8 | 3.96 m/s | 19 |  | 2.4 | m/s |  | 3.96 | m/s | 12.9278 | 0.0092625 | 14.9564 |  | 1.5 | 100 | 0.1 | 149.5637 | 6.8341 | 5.705 | 0.024127 | 38.6081 | 0.25901
2025-05-19 23:13 | 1550 | Remove | 2025-05-19 | 23:13 | ST | GS | - | 97.5 | g | 0 | 114.5 | 11.31 | 1114.8 | 65352 | 12:56 | 28.6 | 2.48 m/s | 24.2 | 29.8 | 4.01 m/s | 19.1 |  | 2.48 | m/s |  | 4.01 | m/s | 12.9361 | 0.00929 | 14.9657 |  | -2.5 | 97.5 | 0.0975 | 153.494 | 6.806 | 5.7351 | 0.024828 | 38.633 | 0.25238
2025-05-19 23:13 | 1551 | Remove | 2025-05-19 | 23:13 | ST | GS | - | 99 | g | 0 | 114.5 | 11.288 | 1112.4 | 65361 | 12:57 | 28.6 | 2.22 m/s | 25.1 | 29.8 | 4.1 m/s | 19.2 |  | 2.22 | m/s |  | 4.1 | m/s | 12.9444 | 0.00927 | 14.9749 |  | 1.5 | 99 | 0.099 | 151.2619 | 7.0591 | 5.7651 | 0.023052 | 38.656 | 0.2561
2025-05-19 23:14 | 1552 | Remove | 2025-05-19 | 23:14 | ST | GS | - | 99.5 | g | 0 | 114.5 | 11.274 | 1110.4 | 65371 | 12:57 | 28.6 | 2.22 m/s | 25 | 29.8 | 3.96 m/s | 20.5 |  | 2.22 | m/s |  | 3.96 | m/s | 12.9528 | 0.0092533 | 14.9842 |  | 0.5 | 99.5 | 0.0995 | 150.5948 | 7.031 | 6.1554 | 0.02296 | 38.679 | 0.25725
2025-05-19 23:14 | 1553 | Remove | 2025-05-19 | 23:14 | ST | GS | - | 98 | g | 0 | 114.6 | 11.26 | 1108.6 | 65380 | 12:58 | 28.6 | 2.27 m/s | 26.3 | 29.8 | 4.2 m/s | 19.6 |  | 2.27 | m/s |  | 4.2 | m/s | 12.9611 | 0.0092383 | 14.9934 |  | -1.5 | 98 | 0.098 | 152.9941 | 7.3966 | 5.8852 | 0.024698 | 38.7037 | 0.25321
2025-05-19 23:15 | 1554 | Remove | 2025-05-19 | 23:15 | US | GS | - | 98.5 | g | 0 | 114.5 | 11.279 | 1110.6 | 65389 | 12:58 | 28.5 | 2.15 m/s | 25.9 | 29.8 | 4.04 m/s | 19 |  | 2.15 | m/s |  | 4.04 | m/s | 12.9694 | 0.009255 | 15.0027 |  | 0.5 | 98.5 | 0.0985 | 152.3115 | 7.2443 | 5.705 | 0.022911 | 38.7266 | 0.25435
2025-05-19 23:15 | 1555 | Remove | 2025-05-19 | 23:15 | US | GS | - | 97.5 | g | 0 | 114.5 | 11.277 | 1110.7 | 65398 | 12:59 | 28.5 | 2.19 m/s | 24.1 | 29.8 | 4.04 m/s | 19 |  | 2.19 | m/s |  | 4.04 | m/s | 12.9778 | 0.0092558 | 15.0119 |  | -1 | 97.5 | 0.0975 | 153.9686 | 6.7408 | 5.705 | 0.021715 | 38.7483 | 0.25162
2025-05-19 23:16 | 1556 | Remove | 2025-05-19 | 23:16 | ST | GS | - | 100.5 | g | 0 | 114.6 | 11.271 | 1110.6 | 65408 | 12:59 | 28.5 | 2.18 m/s | 25.1 | 29.8 | 4.26 m/s | 18.9 |  | 2.18 | m/s |  | 4.26 | m/s | 12.9861 | 0.009255 | 15.0212 |  | 3 | 100.5 | 0.1005 | 149.4646 | 7.0205 | 5.675 | 0.022513 | 38.7708 | 0.25922
2025-05-19 23:16 | 1557 | Remove | 2025-05-19 | 23:16 | US | GS | - | 99.5 | g | 0 | 114.5 | 11.279 | 1110.2 | 65417 | 13:00 | 28.5 | 2.16 m/s | 25.5 | 29.8 | 4.01 m/s | 19.5 |  | 2.16 | m/s |  | 4.01 | m/s | 12.9944 | 0.0092517 | 15.0304 |  | -1 | 99.5 | 0.0995 | 151.0597 | 7.1324 | 5.8552 | 0.022662 | 38.7935 | 0.25649
2025-05-19 23:17 | 1558 | Remove | 2025-05-19 | 23:17 | ST | GS | - | 98 | g | 0 | 114.5 | 11.278 | 1110.2 | 65426 | 13:00 | 28.5 | 2.35 m/s | 25.5 | 29.8 | 4.03 m/s | 20.4 |  | 2.35 | m/s |  | 4.03 | m/s | 13.0028 | 0.0092517 | 15.0397 |  | -1.5 | 98 | 0.098 | 153.4663 | 7.1324 | 6.1254 | 0.024655 | 38.8181 | 0.25246
2025-05-19 23:17 | 1559 | Remove | 2025-05-19 | 23:17 | US | GS | - | 100.5 | g | 0 | 114.6 | 11.282 | 1111.8 | 65435 | 13:01 | 28.5 | 2.38 m/s | 25.6 | 29.8 | 3.86 m/s | 19.8 |  | 2.38 | m/s |  | 3.86 | m/s | 13.0111 | 0.009265 | 15.049 |  | 2.5 | 100.5 | 0.1005 | 149.7409 | 7.1604 | 5.9452 | 0.025068 | 38.8432 | 0.25873
2025-05-19 23:18 | 1560 | Remove | 2025-05-19 | 23:18 | ST | GS | - | 101 | g | 0 | 114.5 | 11.312 | 1114.7 | 65445 | 13:01 | 28.6 | 2.47 m/s | 24.2 | 29.7 | 3.89 m/s | 18.7 |  | 2.47 | m/s |  | 3.89 | m/s | 13.0194 | 0.0092892 | 15.0582 |  | 0.5 | 101 | 0.101 | 149.0916 | 6.806 | 5.5845 | 0.024728 | 38.8679 | 0.25985
2025-05-19 23:18 | 1561 | Keep | 2025-05-19 | 23:18 | ST | GS | - | 99.5 | g | 0 | 114.5 | 11.278 | 1111.1 | 65454 | 13:02 | 28.6 | 2.09 m/s | 24.3 | 29.7 | 3.98 m/s | 18.4 |  | 2.09 | m/s |  | 3.98 | m/s | 13.0278 | 0.0092592 | 15.0675 |  | -1.5 | 99.5 | 0.0995 | 151.4322 | 6.8341 | 5.4949 | 0.02101 | 38.8889 | 0.25586
2025-05-19 23:19 | 1562 | Remove | 2025-05-19 | 23:19 | US | GS | - | 100.5 | g | 0 | 114.6 | 11.269 | 1109.8 | 65463 | 13:02 | 28.6 | 2.35 m/s | 27.6 | 29.8 | 4.18 m/s | 19.6 |  | 2.35 | m/s |  | 4.18 | m/s | 13.0361 | 0.0092483 | 15.0768 |  | 1 | 100.5 | 0.1005 | 150.0175 | 7.7622 | 5.8852 | 0.026832 | 38.9158 | 0.25825
2025-05-19 23:19 | 1563 | Remove | 2025-05-19 | 23:19 | ST | GS | - | 98.5 | g | 0 | 114.6 | 11.272 | 1109.4 | 65473 | 13:03 | 28.5 | 2.27 m/s | 26.4 | 29.7 | 4.15 m/s | 20.9 |  | 2.27 | m/s |  | 4.15 | m/s | 13.0444 | 0.009245 | 15.086 |  | -2 | 98.5 | 0.0985 | 153.1574 | 7.3841 | 6.2415 | 0.024656 | 38.9404 | 0.25295
2025-05-19 23:20 | 1564 | Remove | 2025-05-19 | 23:20 | ST | GS | - | 102 | g | 0 | 114.6 | 11.275 | 1110.5 | 65482 | 13:03 | 28.5 | 2.17 m/s | 26 | 29.7 | 4.26 m/s | 19.6 |  | 2.17 | m/s |  | 4.26 | m/s | 13.0528 | 0.0092542 | 15.0953 |  | 3.5 | 102 | 0.102 | 147.9927 | 7.2722 | 5.8533 | 0.023213 | 38.9636 | 0.26178
2025-05-19 23:20 | 1565 | Remove | 2025-05-19 | 23:20 | ST | GS | - | 102 | g | 0 | 114.6 | 11.295 | 1113.2 | 65491 | 13:04 | 28.5 | 2.45 m/s | 25.9 | 29.7 | 3.94 m/s | 20.7 |  | 2.45 | m/s |  | 3.94 | m/s | 13.0611 | 0.0092767 | 15.1045 |  | 0 | 102 | 0.102 | 148.0836 | 7.2443 | 6.1818 | 0.026107 | 38.9897 | 0.26161
2025-05-19 23:21 | 1566 | Remove | 2025-05-19 | 23:21 | US | GS | - | 102 | g | 0 | 114.6 | 11.286 | 1111.4 | 65501 | 13:04 | 28.5 | 2.19 m/s | 25.5 | 29.7 | 4.16 m/s | 19.6 |  | 2.19 | m/s |  | 4.16 | m/s | 13.0697 | 0.0092617 | 15.1138 |  | 0 | 102 | 0.102 | 148.1744 | 7.1324 | 5.8533 | 0.022976 | 39.0127 | 0.26145
2025-05-19 23:21 | 1567 | Remove | 2025-05-19 | 23:21 | US | GS | - | 99.5 | g | 0 | 114.6 | 11.275 | 1110.3 | 65510 | 13:05 | 28.5 | 2.19 m/s | 26.6 | 29.7 | 4.06 m/s | 20.9 |  | 2.19 | m/s |  | 4.06 | m/s | 13.0781 | 0.0092525 | 15.123 |  | -2.5 | 99.5 | 0.0995 | 151.9904 | 7.4401 | 6.2415 | 0.023967 | 39.0367 | 0.25489
2025-05-19 23:22 | 1568 | Remove | 2025-05-19 | 23:22 | ST | GS | - | 99 | g | 0 | 114.6 | 11.286 | 1111.3 | 65519 | 13:05 | 28.5 | 2.25 m/s | 26.5 | 29.7 | 4.06 m/s | 19.7 |  | 2.25 | m/s |  | 4.06 | m/s | 13.0864 | 0.0092608 | 15.1323 |  | -0.5 | 99 | 0.099 | 152.8516 | 7.4121 | 5.8832 | 0.024532 | 39.0612 | 0.25345
2025-05-19 23:22 | 1569 | Remove | 2025-05-19 | 23:22 | ST | GS | - | 101.5 | g | 0 | 114.6 | 11.288 | 1111.5 | 65528 | 13:06 | 28.5 | 2.12 m/s | 26.6 | 29.7 | 4.15 m/s | 19.8 |  | 2.12 | m/s |  | 4.15 | m/s | 13.0947 | 0.0092625 | 15.1416 |  | 2.5 | 101.5 | 0.1015 | 149.178 | 7.4401 | 5.913 | 0.023201 | 39.0844 | 0.25969
2025-05-19 23:23 | 1570 | Remove | 2025-05-19 | 23:23 | ST | GS | - | 98.5 | g | 0 | 114.6 | 11.248 | 1106.5 | 2 | 13:06 | 28.5 | 2.31 m/s | 26.1 | 29.7 | 3.98 m/s | 19.6 |  | 2.31 | m/s |  | 3.98 | m/s | 13.1031 | 0.0092208 | 15.1508 |  | -3 | 98.5 | 0.0985 | 153.8151 | 7.3002 | 5.8533 | 0.024806 | 39.1092 | 0.25186
2025-05-19 23:23 | 1571 | Remove | 2025-05-19 | 23:23 | ST | GS | - | 99 | g | 0 | 114.7 | 11.266 | 1108.8 | 11 | 13:07 | 28.5 | 2.3 m/s | 25.7 | 29.7 | 4.21 m/s | 20.2 |  | 2.3 | m/s |  | 4.21 | m/s | 13.1114 | 0.00924 | 15.16 |  | 0.5 | 99 | 0.099 | 153.1316 | 7.1883 | 6.0325 | 0.02432 | 39.1335 | 0.25298
2025-05-19 23:24 | 1572 | Remove | 2025-05-19 | 23:24 | ST | GS | - | 99 | g | 0 | 114.7 | 11.264 | 1108.4 | 20 | 13:07 | 28.5 | 2.25 m/s | 26.7 | 29.7 | 4.1 m/s | 20.6 |  | 2.25 | m/s |  | 4.1 | m/s | 13.1197 | 0.0092367 | 15.1693 |  | 0 | 99 | 0.099 | 153.2249 | 7.468 | 6.152 | 0.024717 | 39.1583 | 0.25282
2025-05-19 23:24 | 1573 | Remove | 2025-05-19 | 23:24 | US | GS | - | 102 | g | 0 | 114.6 | 11.279 | 1110.6 | 30 | 13:08 | 28.5 | 2.35 m/s | 26.4 | 29.7 | 3.97 m/s | 20.3 |  | 2.35 | m/s |  | 3.97 | m/s | 13.1281 | 0.009255 | 15.1785 |  | 3 | 102 | 0.102 | 148.809 | 7.3841 | 6.0624 | 0.025525 | 39.1838 | 0.26031
2025-05-19 23:25 | 1574 | Remove | 2025-05-19 | 23:25 | ST | GS | - | 99 | g | 0 | 114.7 | 11.278 | 1110.3 | 39 | 13:08 | 28.5 | 2.34 m/s | 28.1 | 29.7 | 4.12 m/s | 21.2 |  | 2.34 | m/s |  | 4.12 | m/s | 13.1364 | 0.0092525 | 15.1878 |  | -3 | 99 | 0.099 | 153.4118 | 7.8596 | 6.3311 | 0.027053 | 39.2108 | 0.25248
2025-05-19 23:25 | 1575 | Remove | 2025-05-19 | 23:25 | ST | GS | - | 99.5 | g | 0 | 114.7 | 11.281 | 1110.6 | 48 | 13:09 | 28.5 | 2.61 m/s | 28.4 | 29.7 | 3.92 m/s | 21.5 |  | 2.61 | m/s |  | 3.92 | m/s | 13.1447 | 0.009255 | 15.197 |  | 0.5 | 99.5 | 0.0995 | 152.7339 | 7.9435 | 6.4207 | 0.030497 | 39.2413 | 0.25356
2025-05-19 23:26 | 1576 | Remove | 2025-05-19 | 23:26 | ST | GS | - | 102.5 | g | 0 | 114.7 | 11.293 | 1112.7 | 57 | 13:09 | 28.5 | 2.51 m/s | 28.6 | 29.7 | 4.29 m/s | 22.3 |  | 2.51 | m/s |  | 4.29 | m/s | 13.1531 | 0.0092725 | 15.2063 |  | 3 | 102.5 | 0.1025 | 148.3541 | 7.9995 | 6.6596 | 0.029535 | 39.2709 | 0.26101
2025-05-19 23:26 | 1577 | Remove | 2025-05-19 | 23:26 | US | GS | - | 107 | g | 0 | 114.7 | 11.286 | 1111.5 | 67 | 13:10 | 28.5 | 2.22 m/s | 27.2 | 29.7 | 4.13 m/s | 21.4 |  | 2.22 | m/s |  | 4.13 | m/s | 13.1614 | 0.0092625 | 15.2156 |  | 4.5 | 107 | 0.107 | 142.2015 | 7.6079 | 6.3909 | 0.024844 | 39.2957 | 0.27229
2025-05-19 23:27 | 1578 | Remove | 2025-05-19 | 23:27 | US | GS | - | 99 | g | 0 | 114.7 | 11.285 | 1110.9 | 76 | 13:10 | 28.5 | 2.3 m/s | 27 | 29.7 | 3.93 m/s | 20.9 |  | 2.3 | m/s |  | 3.93 | m/s | 13.1697 | 0.0092575 | 15.2248 |  | -8 | 99 | 0.099 | 153.7861 | 7.5519 | 6.2415 | 0.02555 | 39.3213 | 0.25177
2025-05-19 23:27 | 1579 | Remove | 2025-05-19 | 23:27 | ST | GS | - | 99.5 | g | 0 | 114.7 | 11.291 | 1111.6 | 85 | 13:11 | 28.5 | 2.45 m/s | 27.1 | 29.7 | 4.38 m/s | 21.2 |  | 2.45 | m/s |  | 4.38 | m/s | 13.1781 | 0.0092633 | 15.2341 |  | 0.5 | 99.5 | 0.0995 | 153.1064 | 7.5799 | 6.3311 | 0.027317 | 39.3486 | 0.25287
2025-05-19 23:28 | 1580 | Remove | 2025-05-19 | 23:28 | ST | GS | - | 104 | g | 0 | 114.7 | 11.284 | 1111.5 | 95 | 13:11 | 28.5 | 2.18 m/s | 27.3 | 29.7 | 3.92 m/s | 20.9 |  | 2.18 | m/s |  | 3.92 | m/s | 13.1864 | 0.0092625 | 15.2433 |  | 4.5 | 104 | 0.104 | 146.5706 | 7.6358 | 6.2415 | 0.024486 | 39.3731 | 0.26414
2025-05-19 23:28 | 1581 | Remove | 2025-05-19 | 23:28 | ST | GS | - | 99 | g | 0 | 114.8 | 11.265 | 1108.6 | 104 | 13:12 | 28.5 | 2.5 m/s | 26.6 | 29.7 | 4.0 m/s | 20.4 |  | 2.5 | m/s |  | 4 | m/s | 13.1947 | 0.0092383 | 15.2526 |  | -5 | 99 | 0.099 | 154.0665 | 7.4401 | 6.0922 | 0.02736 | 39.4004 | 0.25127
2025-05-19 23:29 | 1582 | Remove | 2025-05-19 | 23:29 | ST | GS | - | 99 | g | 0 | 114.7 | 11.266 | 1108.6 | 113 | 13:12 | 28.5 | 2.04 m/s | 28.7 | 29.7 | 4.13 m/s | 22.1 |  | 2.04 | m/s |  | 4.13 | m/s | 13.2031 | 0.0092383 | 15.2618 |  | 0 | 99 | 0.099 | 154.1598 | 8.0274 | 6.5999 | 0.024088 | 39.4245 | 0.25111
2025-05-19 23:29 | 1583 | Remove | 2025-05-19 | 23:29 | ST | GS | - | 101.5 | g | 0 | 114.8 | 11.267 | 1109.3 | 122 | 13:13 | 28.5 | 2.23 m/s | 27.9 | 29.7 | 4.23 m/s | 21.7 |  | 2.23 | m/s |  | 4.23 | m/s | 13.2117 | 0.0092442 | 15.2711 |  | 2.5 | 101.5 | 0.1015 | 150.4539 | 7.8037 | 6.4805 | 0.025598 | 39.4501 | 0.25729
2025-05-19 23:30 | 1584 | Remove | 2025-05-19 | 23:30 | ST | GS | - | 99 | g | 0 | 114.8 | 11.265 | 1108.7 | 132 | 13:13 | 28.5 | 2.31 m/s | 27.5 | 29.7 | 4.29 m/s | 21.6 |  | 2.31 | m/s |  | 4.29 | m/s | 13.22 | 0.0092392 | 15.2803 |  | -2.5 | 99 | 0.099 | 154.3465 | 7.6918 | 6.4506 | 0.026136 | 39.4763 | 0.25078
2025-05-19 23:30 | 1585 | Remove | 2025-05-19 | 23:30 | ST | GS | - | 100 | g | 0 | 114.7 | 11.255 | 1107.5 | 141 | 13:14 | 28.5 | 2.08 m/s | 28.1 | 29.7 | 4.2 m/s | 20.9 |  | 2.08 | m/s |  | 4.2 | m/s | 13.2283 | 0.0092292 | 15.2895 |  | 1 | 100 | 0.1 | 152.8954 | 7.8596 | 6.2415 | 0.024047 | 39.5003 | 0.25316
2025-05-19 23:31 | 1586 | Remove | 2025-05-19 | 23:31 | ST | GS | - | 104.5 | g | 0 | 114.5 | 11.27 | 1109.2 | 150 | 13:14 | 28.5 | 2.22 m/s | 27.5 | 29.7 | 4.15 m/s | 20.6 |  | 2.22 | m/s |  | 4.15 | m/s | 13.2367 | 0.0092433 | 15.2988 |  | 4.5 | 104.5 | 0.1045 | 146.3998 | 7.6918 | 6.152 | 0.025118 | 39.5254 | 0.26439
2025-05-19 23:31 | 1587 | Remove | 2025-05-19 | 23:31 | US | GS | - | 98 | g | 0 | 114.7 | 11.291 | 1112.6 | 159 | 13:15 | 28.5 | 2.48 m/s | 28.3 | 29.7 | 4.07 m/s | 20.3 |  | 2.48 | m/s |  | 4.07 | m/s | 13.245 | 0.0092717 | 15.3081 |  | -6.5 | 98 | 0.098 | 156.2046 | 7.9155 | 6.0624 | 0.028876 | 39.5543 | 0.24776
2025-05-19 23:32 | 1588 | Remove | 2025-05-19 | 23:32 | US | GS | - | 101 | g | 0 | 114.6 | 11.272 | 1109.9 | 169 | 13:15 | 28.5 | 2.15 m/s | 27.5 | 29.7 | 4.0 m/s | 20.2 |  | 2.15 | m/s |  | 4 | m/s | 13.2533 | 0.0092492 | 15.3173 |  | 3 | 101 | 0.101 | 151.6564 | 7.6918 | 6.0325 | 0.024326 | 39.5786 | 0.25519
2025-05-19 23:32 | 1589 | Remove | 2025-05-19 | 23:32 | ST | GS | - | 102.5 | g | 0 | 114.8 | 11.264 | 1108.8 | 178 | 13:16 | 28.5 | 2.16 m/s | 27.5 | 29.7 | 4.13 m/s | 20.9 |  | 2.16 | m/s |  | 4.13 | m/s | 13.2617 | 0.00924 | 15.3265 |  | 1.5 | 102.5 | 0.1025 | 149.5272 | 7.6918 | 6.2415 | 0.024439 | 39.6031 | 0.25882
2025-05-19 23:33 | 1590 | Remove | 2025-05-19 | 23:33 | ST | GS | - | 101.5 | g | 0 | 114.7 | 11.277 | 1110.9 | 187 | 13:16 | 28.5 | 2.41 m/s | 26.7 | 29.7 | 4.06 m/s | 20.7 |  | 2.41 | m/s |  | 4.06 | m/s | 13.27 | 0.0092575 | 15.3358 |  | -1 | 102.5 | 0.1025 | 149.6175 | 7.468 | 6.1818 | 0.026474 | 39.6295 | 0.25865
2025-05-19 23:33 | 1591 | Keep | 2025-05-19 | 23:33 | US | GS | - | 107.5 | g | 0 | 114.8 | 11.272 | 1109.7 | 196 | 13:17 | 28.5 | 2.23 m/s | 27.9 | 29.7 | 3.97 m/s | 21.3 |  | 2.23 | m/s |  | 3.97 | m/s | 13.2783 | 0.0092475 | 15.345 |  | 6 | 108.5 | 0.1085 | 141.429 | 7.8037 | 6.361 | 0.025598 | 39.6551 | 0.27361
2025-05-19 23:34 | 1592 | Remove | 2025-05-19 | 23:34 | ST | GS | - | 100.5 | g | 0 | 114.7 | 11.273 | 1110 | 206 | 13:17 | 28.5 | 2.25 m/s | 26.3 | 29.7 | 4.01 m/s | 20 |  | 2.25 | m/s |  | 4.01 | m/s | 13.2867 | 0.00925 | 15.3543 |  | -7 | 108.5 | 0.1085 | 141.5142 | 7.3561 | 5.9728 | 0.024346 | 39.6795 | 0.27344
2025-05-19 23:34 | 1593 | Remove | 2025-05-19 | 23:34 | ST | GS | - | 102.5 | g | 0 | 114.8 | 11.274 | 1109.5 | 215 | 13:18 | 28.5 | 2.08 m/s | 26.3 | 29.7 | 4.23 m/s | 20.5 |  | 2.08 | m/s |  | 4.23 | m/s | 13.295 | 0.0092458 | 15.3635 |  | 2 | 110.5 | 0.1105 | 139.0366 | 7.3561 | 6.1221 | 0.022507 | 39.702 | 0.27832
2025-05-19 23:35 | 1594 | Remove | 2025-05-19 | 23:35 | ST | GS | - | 104 | g | 0 | 114.7 | 11.285 | 1111.3 | 224 | 13:18 | 28.5 | 2.12 m/s | 27.2 | 29.7 | 4.09 m/s | 20.9 |  | 2.12 | m/s |  | 4.09 | m/s | 13.3033 | 0.0092608 | 15.3728 |  | 1.5 | 112 | 0.112 | 137.2572 | 7.6079 | 6.2415 | 0.023725 | 39.7257 | 0.28193
2025-05-19 23:35 | 1595 | Remove | 2025-05-19 | 23:35 | ST | GS | - | 100.5 | g | 0 | 114.7 | 11.25 | 1107 | 234 | 13:19 | 28.5 | 2.11 m/s | 27.1 | 29.7 | 4.21 m/s | 20 |  | 2.11 | m/s |  | 4.21 | m/s | 13.3117 | 0.009225 | 15.382 |  | -3.5 | 112 | 0.112 | 137.3395 | 7.5799 | 5.9728 | 0.023526 | 39.7492 | 0.28177
2025-05-19 23:36 | 1596 | Remove | 2025-05-19 | 23:36 | US | GS | - | 103.5 | g | 0 | 114.5 | 11.262 | 1108.5 | 243 | 13:19 | 28.5 | 2.31 m/s | 27.8 | 29.7 | 4.1 m/s | 21 |  | 2.31 | m/s |  | 4.1 | m/s | 13.32 | 0.0092375 | 15.3913 |  | 3 | 115 | 0.115 | 133.8371 | 7.7757 | 6.2714 | 0.026421 | 39.7757 | 0.28912
2025-05-19 23:36 | 1597 | Remove | 2025-05-19 | 23:36 | ST | GS | - | 101 | g | 0 | 114.5 | 11.252 | 1106.7 | 252 | 13:20 | 28.5 | 2.25 m/s | 26.5 | 29.7 | 4.2 m/s | 19.6 |  | 2.25 | m/s |  | 4.2 | m/s | 13.3283 | 0.0092225 | 15.4005 |  | -2.5 | 115 | 0.115 | 133.9173 | 7.4121 | 5.8533 | 0.024532 | 39.8002 | 0.28894
2025-05-19 23:37 | 1598 | Remove | 2025-05-19 | 23:37 | ST | GS | - | 101.5 | g | 0 | 114.5 | 11.275 | 1109.8 | 261 | 13:20 | 28.5 | 2.42 m/s | 25.9 | 29.7 | 4.13 m/s | 20.1 |  | 2.42 | m/s |  | 4.13 | m/s | 13.3367 | 0.0092483 | 15.4097 |  | 0.5 | 115.5 | 0.1155 | 133.4176 | 7.2443 | 6.0026 | 0.025788 | 39.826 | 0.29001
2025-05-19 23:37 | 1599 | Remove | 2025-05-19 | 23:37 | ST | GS | - | 101 | g | 0 | 114.4 | 11.246 | 1106.7 | 271 | 13:21 | 28.5 | 2.37 m/s | 25.8 | 29.7 | 3.98 m/s | 19.6 |  | 2.37 | m/s |  | 3.98 | m/s | 13.345 | 0.0092225 | 15.419 |  | -0.5 | 115.5 | 0.1155 | 133.4975 | 7.2163 | 5.8533 | 0.025157 | 39.8511 | 0.28983
2025-05-19 23:38 | 1600 | Remove | 2025-05-19 | 23:38 | ST | GS | - | 100 | g | 0 | 114.4 | 11.233 | 1105.1 | 280 | 13:21 | 28.5 | 2.08 m/s | 26.3 | 29.7 | 4.01 m/s | 20.5 |  | 2.08 | m/s |  | 4.01 | m/s | 13.3536 | 0.0092092 | 15.4282 |  | -1 | 115.5 | 0.1155 | 133.5772 | 7.3561 | 6.1221 | 0.022507 | 39.8736 | 0.28967
2025-05-19 23:38 | 1601 | Remove | 2025-05-19 | 23:38 | ST | GS | - | 102.5 | g | 0 | 114.4 | 11.253 | 1107.3 | 289 | 13:22 | 28.5 | 2.16 m/s | 27.2 | 29.7 | 4.26 m/s | 20.7 |  | 2.16 | m/s |  | 4.26 | m/s | 13.3619 | 0.0092275 | 15.4374 |  | 2.5 | 118 | 0.118 | 130.8254 | 7.6079 | 6.1818 | 0.024172 | 39.8978 | 0.29576
2025-05-19 23:39 | 1602 | Remove | 2025-05-19 | 23:39 | ST | GS | - | 100 | g | 0 | 114.6 | 11.233 | 1104.9 | 298 | 13:22 | 28.5 | 2.34 m/s | 26.2 | 29.7 | 4.04 m/s | 19.7 |  | 2.34 | m/s |  | 4.04 | m/s | 13.3703 | 0.0092075 | 15.4466 |  | -2.5 | 118 | 0.118 | 130.9034 | 7.3282 | 5.8832 | 0.025224 | 39.923 | 0.29557
2025-05-19 23:39 | 1603 | Remove | 2025-05-19 | 23:39 | US | GS | - | 101 | g | 0 | 114.5 | 11.227 | 1104.3 | 308 | 13:23 | 28.5 | 2.37 m/s | 28.1 | 29.7 | 4.09 m/s | 21.1 |  | 2.37 | m/s |  | 4.09 | m/s | 13.3786 | 0.0092025 | 15.4558 |  | 1 | 119 | 0.119 | 129.8807 | 7.8596 | 6.3013 | 0.0274 | 39.9504 | 0.29787
2025-05-19 23:40 | 1604 | Remove | 2025-05-19 | 23:40 | ST | GS | - | 100.5 | g | 0 | 114.5 | 11.259 | 1107.5 | 317 | 13:23 | 28.5 | 2.16 m/s | 26.2 | 29.7 | 3.94 m/s | 20 |  | 2.16 | m/s |  | 3.94 | m/s | 13.3869 | 0.0092292 | 15.465 |  | -0.5 | 119 | 0.119 | 129.9583 | 7.3282 | 5.9728 | 0.023284 | 39.9737 | 0.2977
2025-05-19 23:40 | 1605 | Remove | 2025-05-19 | 23:40 | ST | GS | - | 105.5 | g | 0 | 114.5 | 11.231 | 1104.3 | 326 | 13:24 | 28.5 | 2.3 m/s | 27.5 | 29.7 | 4.1 m/s | 20.1 |  | 2.3 | m/s |  | 4.1 | m/s | 13.3953 | 0.0092025 | 15.4742 |  | 5 | 124 | 0.124 | 124.7922 | 7.6918 | 6.0026 | 0.026023 | 39.9997 | 0.31
2025-05-19 23:41 | 1606 | Remove | 2025-05-19 | 23:41 | US | GS | - | 108.5 | g | 0 | 114.5 | 11.276 | 1109.9 | 335 | 13:24 | 28.5 | 2.3 m/s | 25.4 | 29.7 | 3.84 m/s | 19.6 |  | 2.3 | m/s |  | 3.84 | m/s | 13.4036 | 0.0092492 | 15.4835 |  | 3 | 127 | 0.127 | 121.9172 | 7.1044 | 5.8533 | 0.024036 | 40.0238 | 0.31731
2025-05-19 23:41 | 1607 | Remove | 2025-05-19 | 23:41 | ST | GS | - | 101.5 | g | 0 | 114.5 | 11.242 | 1105.2 | 345 | 13:25 | 28.5 | 2.26 m/s | 26.5 | 29.7 | 4.06 m/s | 19.3 |  | 2.26 | m/s |  | 4.06 | m/s | 13.4119 | 0.00921 | 15.4927 |  | -7 | 127 | 0.127 | 121.9897 | 7.4121 | 5.7637 | 0.024641 | 40.0484 | 0.31712
2025-05-19 23:42 | 1608 | Remove | 2025-05-19 | 23:42 | US | GS | - | 103 | g | 0 | 114.5 | 11.232 | 1104.7 | 354 | 13:25 | 28.5 | 2.46 m/s | 27.6 | 29.7 | 3.97 m/s | 22.2 |  | 2.46 | m/s |  | 3.97 | m/s | 13.4203 | 0.0092058 | 15.5019 |  | 1.5 | 128.5 | 0.1285 | 120.6374 | 7.7198 | 6.6298 | 0.027935 | 40.0764 | 0.32064
2025-05-19 23:42 | 1609 | Remove | 2025-05-19 | 23:42 | ST | GS | - | 102.5 | g | 0 | 114.6 | 11.251 | 1106.8 | 363 | 13:26 | 28.5 | 2.52 m/s | 26.5 | 29.7 | 3.98 m/s | 20.2 |  | 2.52 | m/s |  | 3.98 | m/s | 13.4286 | 0.0092233 | 15.5111 |  | -0.5 | 128.5 | 0.1285 | 120.7091 | 7.4121 | 6.0325 | 0.027475 | 40.1038 | 0.32042
2025-05-19 23:43 | 1610 | Remove | 2025-05-19 | 23:43 | ST | GS | - | 101.5 | g | 0 | 114.6 | 11.224 | 1103 | 372 | 13:26 | 28.5 | 2.15 m/s | 26.2 | 29.7 | 4.16 m/s | 20.2 |  | 2.15 | m/s |  | 4.16 | m/s | 13.4369 | 0.0091917 | 15.5203 |  | -1 | 128.5 | 0.1285 | 120.7807 | 7.3282 | 6.0325 | 0.023176 | 40.127 | 0.32023
2025-05-19 23:43 | 1611 | Remove | 2025-05-19 | 23:43 | US | GS | - | 101 | g | 0 | 114.6 | 11.231 | 1103.9 | 381 | 13:27 | 28.5 | 2.18 m/s | 26.7 | 29.7 | 4.0 m/s | 21.1 |  | 2.18 | m/s |  | 4 | m/s | 13.4453 | 0.0091992 | 15.5295 |  | -0.5 | 128.5 | 0.1285 | 120.8523 | 7.468 | 6.3013 | 0.023948 | 40.151 | 0.32004
2025-05-19 23:44 | 1612 | Remove | 2025-05-19 | 23:44 | ST | GS | - | 101.5 | g | 0 | 114.5 | 11.227 | 1103.2 | 391 | 13:27 | 28.5 | 2.34 m/s | 28 | 29.7 | 4.1 m/s | 21.2 |  | 2.34 | m/s |  | 4.1 | m/s | 13.4536 | 0.0091933 | 15.5387 |  | 0.5 | 129 | 0.129 | 120.4551 | 7.8316 | 6.3311 | 0.026957 | 40.1779 | 0.32107
2025-05-19 23:44 | 1613 | Remove | 2025-05-19 | 23:44 | ST | GS | - | 103.5 | g | 0 | 114.4 | 11.207 | 1100.9 | 400 | 13:28 | 28.5 | 2.34 m/s | 25.5 | 29.7 | 4.01 m/s | 19.8 |  | 2.34 | m/s |  | 4.01 | m/s | 13.4619 | 0.0091742 | 15.5479 |  | 2 | 131 | 0.131 | 118.6861 | 7.1324 | 5.913 | 0.02455 | 40.2025 | 0.32585
2025-05-19 23:45 | 1614 | Remove | 2025-05-19 | 23:45 | ST | GS | - | 102.5 | g | 0 | 114.1 | 11.208 | 1101.3 | 409 | 13:28 | 28.4 | 2.3 m/s | 27 | 29.7 | 4.12 m/s | 20.7 |  | 2.3 | m/s |  | 4.12 | m/s | 13.4703 | 0.0091775 | 15.5571 |  | -1 | 131 | 0.131 | 118.7562 | 7.5106 | 6.1818 | 0.02541 | 40.2279 | 0.32564
2025-05-19 23:45 | 1615 | Remove | 2025-05-19 | 23:45 | US | GS | - | 105 | g | 0 | 114.1 | 11.215 | 1101.8 | 418 | 13:29 | 28.4 | 2.38 m/s | 26.9 | 29.7 | 3.97 m/s | 20.5 |  | 2.38 | m/s |  | 3.97 | m/s | 13.4786 | 0.0091817 | 15.5662 |  | 2.5 | 133.5 | 0.1335 | 116.6011 | 7.4828 | 6.1221 | 0.026197 | 40.2541 | 0.33164
2025-05-19 23:46 | 1616 | Remove | 2025-05-19 | 23:46 | ST | GS | - | 103 | g | 0 | 114.2 | 11.197 | 1099.6 | 428 | 13:29 | 28.4 | 2.3 m/s | 28.1 | 29.7 | 3.96 m/s | 21.7 |  | 2.3 | m/s |  | 3.96 | m/s | 13.4869 | 0.0091633 | 15.5754 |  | -2 | 133.5 | 0.1335 | 116.6697 | 7.8166 | 6.4805 | 0.026445 | 40.2805 | 0.33143
2025-05-19 23:46 | 1617 | Remove | 2025-05-19 | 23:46 | ST | GS | - | 104 | g | 0 | 114.2 | 11.221 | 1102.9 | 437 | 13:30 | 28.4 | 2.43 m/s | 27.9 | 29.7 | 3.96 m/s | 21.8 |  | 2.43 | m/s |  | 3.96 | m/s | 13.4956 | 0.0091908 | 15.5846 |  | 1 | 134.5 | 0.1345 | 115.8706 | 7.761 | 6.5103 | 0.027741 | 40.3083 | 0.33368
2025-05-19 23:47 | 1618 | Remove | 2025-05-19 | 23:47 | ST | GS | - | 104.5 | g | 0 | 114.2 | 11.202 | 1100.2 | 446 | 13:30 | 28.4 | 2.18 m/s | 27.5 | 29.7 | 3.96 m/s | 21.1 |  | 2.18 | m/s |  | 3.96 | m/s | 13.5039 | 0.0091683 | 15.5938 |  | 0.5 | 135 | 0.135 | 115.5094 | 7.6497 | 6.3013 | 0.02453 | 40.3328 | 0.33472
2025-05-19 23:47 | 1619 | Remove | 2025-05-19 | 23:47 | ST | GS | - | 101.5 | g | 0 | 114.3 | 11.201 | 1099.9 | 455 | 13:31 | 28.4 | 2.48 m/s | 27 | 29.6 | 3.97 m/s | 21.4 |  | 2.48 | m/s |  | 3.97 | m/s | 13.5122 | 0.0091658 | 15.6029 |  | -3 | 135 | 0.135 | 115.5773 | 7.5106 | 6.3562 | 0.027399 | 40.3602 | 0.33449
2025-05-19 23:48 | 1620 | Remove | 2025-05-19 | 23:48 | ST | GS | - | 101 | g | 0 | 114.1 | 11.197 | 1100 | 464 | 13:31 | 28.4 | 2.4 m/s | 27.4 | 29.6 | 3.96 m/s | 21.8 |  | 2.4 | m/s |  | 3.96 | m/s | 13.5206 | 0.0091667 | 15.6121 |  | -0.5 | 135 | 0.135 | 115.6452 | 7.6219 | 6.475 | 0.026908 | 40.3871 | 0.33427
2025-05-19 23:48 | 1621 | Keep | 2025-05-19 | 23:48 | ST | GS | - | 105 | g | 0 | 114.2 | 11.211 | 1101.3 | 474 | 13:32 | 28.4 | 2.35 m/s | 27.4 | 29.6 | 3.86 m/s | 21.3 |  | 2.35 | m/s |  | 3.86 | m/s | 13.5289 | 0.0091775 | 15.6213 |  | 4 | 139 | 0.139 | 112.3833 | 7.6219 | 6.3265 | 0.026347 | 40.4134 | 0.34394
2025-05-19 23:49 | 1622 | Remove | 2025-05-19 | 23:49 | ST | GS | - | 104.5 | g | 0 | 114.2 | 11.198 | 1100.1 | 483 | 13:32 | 28.4 | 2.05 m/s | 28.2 | 29.6 | 4.09 m/s | 21.5 |  | 2.05 | m/s |  | 4.09 | m/s | 13.5372 | 0.0091675 | 15.6304 |  | -0.5 | 139 | 0.139 | 112.4492 | 7.8444 | 6.3859 | 0.023655 | 40.4371 | 0.34374
2025-05-19 23:49 | 1623 | Remove | 2025-05-19 | 23:49 | ST | GS | - | 107.5 | g | 0 | 114.2 | 11.22 | 1102.4 | 492 | 13:33 | 28.4 | 2.33 m/s | 29.1 | 29.6 | 4.01 m/s | 22.2 |  | 2.33 | m/s |  | 4.01 | m/s | 13.5456 | 0.0091867 | 15.6396 |  | 3 | 142 | 0.142 | 110.1382 | 8.0948 | 6.5938 | 0.027744 | 40.4648 | 0.35092
2025-05-19 23:50 | 1624 | Remove | 2025-05-19 | 23:50 | ST | GS | - | 102.5 | g | 0 | 114.3 | 11.19 | 1098.8 | 501 | 13:33 | 28.4 | 2.16 m/s | 28.1 | 29.6 | 4.0 m/s | 21.1 |  | 2.16 | m/s |  | 4 | m/s | 13.5539 | 0.0091567 | 15.6488 |  | -5 | 142 | 0.142 | 110.2027 | 7.8166 | 6.2671 | 0.024836 | 40.4897 | 0.35071
2025-05-19 23:50 | 1625 | Remove | 2025-05-19 | 23:50 | ST | GS | - | 108 | g | 0 | 114.3 | 11.192 | 1099.1 | 510 | 13:34 | 28.4 | 2.09 m/s | 29.6 | 29.6 | 4.15 m/s | 22.5 |  | 2.09 | m/s |  | 4.15 | m/s | 13.5622 | 0.0091592 | 15.6579 |  | 5.5 | 147.5 | 0.1475 | 106.1555 | 8.2339 | 6.6829 | 0.025314 | 40.515 | 0.36406
2025-05-19 23:51 | 1626 | Remove | 2025-05-19 | 23:51 | ST | GS | - | 102.5 | g | 0 | 114.2 | 11.175 | 1096.4 | 520 | 13:34 | 28.4 | 2.37 m/s | 29.1 | 29.6 | 4.26 m/s | 20.7 |  | 2.37 | m/s |  | 4.26 | m/s | 13.5706 | 0.0091367 | 15.6671 |  | -5.5 | 147.5 | 0.1475 | 106.2175 | 8.0948 | 6.1483 | 0.02822 | 40.5432 | 0.36381
2025-05-19 23:51 | 1627 | Remove | 2025-05-19 | 23:51 | US | GS | - | 105 | g | 0 | 114.3 | 11.212 | 1101.7 | 529 | 13:35 | 28.4 | 2.13 m/s | 28.6 | 29.6 | 4.01 m/s | 22.5 |  | 2.13 | m/s |  | 4.01 | m/s | 13.5789 | 0.0091808 | 15.6763 |  | 2.5 | 150 | 0.15 | 104.5084 | 7.9557 | 6.6829 | 0.024926 | 40.5681 | 0.36975
2025-05-19 23:52 | 1628 | Remove | 2025-05-19 | 23:52 | ST | GS | - | 102.5 | g | 0 | 114.2 | 11.215 | 1102.5 | 538 | 13:35 | 28.4 | 2.3 m/s | 26.8 | 29.6 | 4.03 m/s | 20.2 |  | 2.3 | m/s |  | 4.03 | m/s | 13.5872 | 0.0091875 | 15.6854 |  | -2.5 | 150 | 0.15 | 104.5697 | 7.455 | 5.9998 | 0.025222 | 40.5934 | 0.36952
2025-05-19 23:52 | 1629 | Remove | 2025-05-19 | 23:52 | ST | GS | - | 101.5 | g | 0 | 114.2 | 11.209 | 1101.3 | 547 | 13:36 | 28.4 | 2.25 m/s | 27.8 | 29.6 | 3.97 m/s | 21.5 |  | 2.25 | m/s |  | 3.97 | m/s | 13.5956 | 0.0091775 | 15.6946 |  | -1 | 150 | 0.15 | 104.6308 | 7.7332 | 6.3859 | 0.025594 | 40.6189 | 0.36929
2025-05-19 23:53 | 1630 | Remove | 2025-05-19 | 23:53 | ST | GS | - | 106 | g | 0 | 114.2 | 11.204 | 1101.4 | 556 | 13:36 | 28.4 | 2.31 m/s | 26.3 | 29.6 | 4.01 m/s | 20.2 |  | 2.31 | m/s |  | 4.01 | m/s | 13.6039 | 0.0091783 | 15.7038 |  | 4.5 | 154.5 | 0.1545 | 101.6427 | 7.3159 | 5.9998 | 0.024859 | 40.6438 | 0.38013
2025-05-19 23:53 | 1631 | Remove | 2025-05-19 | 23:53 | ST | GS | - | 101.5 | g | 0 | 114.3 | 11.214 | 1101.7 | 566 | 13:37 | 28.4 | 2.09 m/s | 26.6 | 29.6 | 4.01 m/s | 21.5 |  | 2.09 | m/s |  | 4.01 | m/s | 13.6125 | 0.0091808 | 15.713 |  | -4.5 | 154.5 | 0.1545 | 101.7022 | 7.3993 | 6.3859 | 0.022748 | 40.6666 | 0.37992
2025-05-19 23:54 | 1632 | Remove | 2025-05-19 | 23:54 | ST | GS | - | 104 | g | 0 | 114.3 | 11.207 | 1101.9 | 575 | 13:37 | 28.4 | 2.23 m/s | 26.5 | 29.6 | 4.13 m/s | 20.3 |  | 2.23 | m/s |  | 4.13 | m/s | 13.6208 | 0.0091825 | 15.7222 |  | 2.5 | 157 | 0.157 | 100.1412 | 7.3715 | 6.0295 | 0.02418 | 40.6907 | 0.38584
2025-05-19 23:54 | 1633 | Remove | 2025-05-19 | 23:54 | ST | GS | - | 102.5 | g | 0 | 114.3 | 11.196 | 1100.2 | 584 | 13:38 | 28.4 | 2.22 m/s | 27 | 29.6 | 4.09 m/s | 20.3 |  | 2.22 | m/s |  | 4.09 | m/s | 13.6292 | 0.0091683 | 15.7313 |  | -1.5 | 157 | 0.157 | 100.1996 | 7.5106 | 6.0295 | 0.024526 | 40.7153 | 0.3856
2025-05-19 23:55 | 1634 | Remove | 2025-05-19 | 23:55 | ST | GS | - | 103 | g | 0 | 114.4 | 11.205 | 1100.6 | 593 | 13:38 | 28.4 | 2.16 m/s | 27.1 | 29.6 | 4.21 m/s | 21.4 |  | 2.16 | m/s |  | 4.21 | m/s | 13.6375 | 0.0091717 | 15.7405 |  | 0.5 | 157.5 | 0.1575 | 99.9397 | 7.5384 | 6.3562 | 0.023952 | 40.7392 | 0.38661
2025-05-19 23:55 | 1635 | Remove | 2025-05-19 | 23:55 | ST | GS | - | 106 | g | 0 | 114.4 | 11.211 | 1102.2 | 602 | 13:39 | 28.4 | 2.37 m/s | 26.7 | 29.6 | 4.09 m/s | 20.5 |  | 2.37 | m/s |  | 4.09 | m/s | 13.6461 | 0.009185 | 15.7497 |  | 3 | 160.5 | 0.1605 | 98.1289 | 7.4272 | 6.0889 | 0.025892 | 40.7651 | 0.39372
2025-05-19 23:56 | 1636 | Remove | 2025-05-19 | 23:56 | ST | GS | - | 104.5 | g | 0 | 114.4 | 11.219 | 1102.8 | 612 | 13:39 | 28.4 | 2.34 m/s | 26.6 | 29.6 | 4.15 m/s | 19.4 |  | 2.34 | m/s |  | 4.15 | m/s | 13.6544 | 0.00919 | 15.7589 |  | -1.5 | 160.5 | 0.1605 | 98.1862 | 7.3993 | 5.7622 | 0.025469 | 40.7906 | 0.39347
2025-05-19 23:56 | 1637 | Remove | 2025-05-19 | 23:56 | ST | GS | - | 107.5 | g | 0 | 114.3 | 11.214 | 1101.9 | 621 | 13:40 | 28.4 | 2.3 m/s | 25.3 | 29.6 | 4.16 m/s | 19.2 |  | 2.3 | m/s |  | 4.16 | m/s | 13.6628 | 0.0091825 | 15.7681 |  | 3 | 163.5 | 0.1635 | 96.4408 | 7.0377 | 5.7028 | 0.02381 | 40.8144 | 0.40059
2025-05-19 23:57 | 1638 | Remove | 2025-05-19 | 23:57 | US | GS | - | 101.5 | g | 0 | 114.4 | 11.209 | 1101.1 | 630 | 13:40 | 28.4 | 2.11 m/s | 26.8 | 29.6 | 4.1 m/s | 19.3 |  | 2.11 | m/s |  | 4.1 | m/s | 13.6711 | 0.0091758 | 15.7772 |  | -6 | 163.5 | 0.1635 | 96.4969 | 7.455 | 5.7325 | 0.023138 | 40.8375 | 0.40037
2025-05-19 23:57 | 1639 | Remove | 2025-05-19 | 23:57 | ST | GS | - | 104.5 | g | 0 | 114.4 | 11.205 | 1100.4 | 639 | 13:41 | 28.4 | 2.11 m/s | 26 | 29.6 | 4.03 m/s | 19.4 |  | 2.11 | m/s |  | 4.03 | m/s | 13.6794 | 0.00917 | 15.7864 |  | 3 | 166.5 | 0.1665 | 94.8133 | 7.2324 | 5.7622 | 0.022448 | 40.86 | 0.40749
2025-05-19 23:58 | 1640 | Remove | 2025-05-19 | 23:58 | ST | GS | - | 102.5 | g | 0 | 114.4 | 11.186 | 1097.7 | 648 | 13:41 | 28.4 | 2.27 m/s | 27.4 | 29.6 | 4.1 m/s | 20.1 |  | 2.27 | m/s |  | 4.1 | m/s | 13.6878 | 0.0091475 | 15.7956 |  | -2 | 166.5 | 0.1665 | 94.8682 | 7.6219 | 5.9701 | 0.02545 | 40.8854 | 0.40724
2025-05-19 23:58 | 1641 | Remove | 2025-05-19 | 23:58 | US | GS | - | 104 | g | 0 | 114.4 | 11.189 | 1097.3 | 658 | 13:42 | 28.4 | 2.12 m/s | 26.5 | 29.6 | 4.18 m/s | 19.8 |  | 2.12 | m/s |  | 4.18 | m/s | 13.6961 | 0.0091442 | 15.8047 |  | 1.5 | 168 | 0.168 | 94.0756 | 7.3715 | 5.881 | 0.022988 | 40.9084 | 0.41067
2025-05-19 23:59 | 1642 | Remove | 2025-05-19 | 23:59 | US | GS | - | 104 | g | 0 | 114.4 | 11.192 | 1098.1 | 667 | 13:42 | 28.4 | 2.25 m/s | 27.1 | 29.6 | 4.16 m/s | 20.5 |  | 2.25 | m/s |  | 4.16 | m/s | 13.7044 | 0.0091508 | 15.8139 |  | 0 | 168 | 0.168 | 94.1301 | 7.5384 | 6.0889 | 0.02495 | 40.9334 | 0.41042
2025-05-19 23:59 | 1643 | Remove | 2025-05-19 | 23:59 | US | GS | - | 107 | g | 0 | 114.4 | 11.194 | 1098.6 | 676 | 13:43 | 28.4 | 2.18 m/s | 26.6 | 29.6 | 4.09 m/s | 20.3 |  | 2.18 | m/s |  | 4.09 | m/s | 13.7128 | 0.009155 | 15.823 |  | 3 | 171 | 0.171 | 92.5322 | 7.3993 | 6.0295 | 0.023728 | 40.9571 | 0.41751
2025-05-20 | 1644 | Remove | 2025-05-19 | 24:00 | ST | GS | - | 103 | g | 0 | 114.4 | 11.206 | 1099.8 | 685 | 13:43 | 28.4 | 2.3 m/s | 26.4 | 29.6 | 4.07 m/s | 20 |  | 2.3 | m/s |  | 4.07 | m/s | 13.7211 | 0.009165 | 15.8322 |  | -4 | 171 | 0.171 | 92.5858 | 7.3437 | 5.9404 | 0.024845 | 40.9819 | 0.41726
2025-05-20 | 1645 | Remove | 2025-05-20 | 0:00 | US | GS | - | 103 | g | 0 | 114.3 | 11.175 | 1095.9 | 694 | 13:44 | 28.4 | 2.44 m/s | 26.5 | 29.6 | 4.0 m/s | 20 |  | 2.44 | m/s |  | 4 | m/s | 13.7294 | 0.0091325 | 15.8413 |  | 0 | 171 | 0.171 | 92.6392 | 7.3715 | 5.9404 | 0.026458 | 41.0084 | 0.41699
2025-05-20 00:01 | 1646 | Remove | 2025-05-20 | 0:01 | ST | GS | - | 106 | g | 0 | 114.3 | 11.193 | 1097.8 | 704 | 13:44 | 28.4 | 2.27 m/s | 26.2 | 29.6 | 4.03 m/s | 21 |  | 2.27 | m/s |  | 4.03 | m/s | 13.7378 | 0.0091483 | 15.8505 |  | 3 | 174 | 0.174 | 91.0946 | 7.2881 | 6.2374 | 0.024336 | 41.0327 | 0.42405
2025-05-20 00:01 | 1647 | Remove | 2025-05-20 | 0:01 | ST | GS | - | 102.5 | g | 0 | 114.4 | 11.191 | 1098.4 | 713 | 13:45 | 28.4 | 2.33 m/s | 25.9 | 29.6 | 4.15 m/s | 19.5 |  | 2.33 | m/s |  | 4.15 | m/s | 13.7461 | 0.0091533 | 15.8596 |  | -3.5 | 174 | 0.174 | 91.1472 | 7.2046 | 5.7919 | 0.024693 | 41.0574 | 0.4238
2025-05-20 00:02 | 1648 | Remove | 2025-05-20 | 0:02 | ST | GS | - | 107 | g | 0 | 114.3 | 11.206 | 1100.4 | 722 | 13:45 | 28.4 | 2.3 m/s | 25.3 | 29.6 | 4.0 m/s | 20 |  | 2.3 | m/s |  | 4 | m/s | 13.7544 | 0.00917 | 15.8688 |  | 4.5 | 178.5 | 0.1785 | 88.9007 | 7.0377 | 5.9404 | 0.02381 | 41.0812 | 0.43451
2025-05-20 00:02 | 1649 | Remove | 2025-05-20 | 0:02 | ST | GS | - | 104 | g | 0 | 114.3 | 11.2 | 1099.8 | 731 | 13:46 | 28.4 | 2.37 m/s | 25.7 | 29.6 | 4.16 m/s | 19.4 |  | 2.37 | m/s |  | 4.16 | m/s | 13.7628 | 0.009165 | 15.8779 |  | -3 | 178.5 | 0.1785 | 88.9521 | 7.149 | 5.7622 | 0.024923 | 41.1062 | 0.43424
2025-05-20 00:03 | 1650 | Remove | 2025-05-20 | 0:03 | US | GS | - | 105 | g | 0 | 114.3 | 11.193 | 1098.9 | 740 | 13:46 | 28.4 | 2.26 m/s | 25.8 | 29.6 | 3.97 m/s | 20 |  | 2.26 | m/s |  | 3.97 | m/s | 13.7711 | 0.0091575 | 15.8871 |  | 1 | 179.5 | 0.1795 | 88.5075 | 7.1768 | 5.9404 | 0.023858 | 41.13 | 0.43642
2025-05-20 00:03 | 1651 | Keep | 2025-05-20 | 0:03 | US | GS | - | 104.5 | g | 0 | 114.3 | 11.179 | 1096.4 | 750 | 13:47 | 28.4 | 2.2 m/s | 26.5 | 29.6 | 4.01 m/s | 19.8 |  | 2.2 | m/s |  | 4.01 | m/s | 13.7794 | 0.0091367 | 15.8962 |  | -0.5 | 179.5 | 0.1795 | 88.5584 | 7.3715 | 5.881 | 0.023855 | 41.1539 | 0.43617
2025-05-20 00:04 | 1652 | Remove | 2025-05-20 | 0:04 | ST | GS | - | 102.5 | g | 0 | 114.3 | 11.163 | 1094.6 | 759 | 13:47 | 28.4 | 2.15 m/s | 26.1 | 29.6 | 4.04 m/s | 20.1 |  | 2.15 | m/s |  | 4.04 | m/s | 13.7881 | 0.0091217 | 15.9054 |  | -2 | 179.5 | 0.1795 | 88.6092 | 7.2603 | 5.9701 | 0.022961 | 41.1768 | 0.43592
2025-05-20 00:04 | 1653 | Remove | 2025-05-20 | 0:04 | ST | GS | - | 105.5 | g | 0 | 114.3 | 11.184 | 1097.1 | 768 | 13:48 | 28.4 | 2.41 m/s | 28.1 | 29.6 | 3.89 m/s | 21.6 |  | 2.41 | m/s |  | 3.89 | m/s | 13.7964 | 0.0091425 | 15.9145 |  | 3 | 182.5 | 0.1825 | 87.2027 | 7.8166 | 6.4156 | 0.02771 | 41.2045 | 0.44291
2025-05-20 00:05 | 1654 | Remove | 2025-05-20 | 0:05 | US | GS | - | 107 | g | 0 | 114.3 | 11.179 | 1096.5 | 777 | 13:48 | 28.4 | 2.3 m/s | 28.9 | 29.6 | 3.98 m/s | 21.4 |  | 2.3 | m/s |  | 3.98 | m/s | 13.8047 | 0.0091375 | 15.9236 |  | 1.5 | 184 | 0.184 | 86.5415 | 8.0391 | 6.3562 | 0.027198 | 41.2317 | 0.44626
2025-05-20 00:05 | 1655 | Remove | 2025-05-20 | 0:05 | ST | GS | - | 106 | g | 0 | 114.3 | 11.166 | 1095.2 | 786 | 13:49 | 28.4 | 2.27 m/s | 30 | 29.6 | 4.18 m/s | 22 |  | 2.27 | m/s |  | 4.18 | m/s | 13.8131 | 0.0091267 | 15.9328 |  | -1 | 184 | 0.184 | 86.5911 | 8.3451 | 6.5344 | 0.027865 | 41.2596 | 0.44596
2025-05-20 00:06 | 1656 | Remove | 2025-05-20 | 0:06 | ST | GS | - | 105.5 | g | 0 | 114.2 | 11.163 | 1094.6 | 795 | 13:49 | 28.4 | 2.13 m/s | 29.6 | 29.6 | 4.11 m/s | 22.6 |  | 2.13 | m/s |  | 4.11 | m/s | 13.8214 | 0.0091217 | 15.9419 |  | -0.5 | 184 | 0.184 | 86.6407 | 8.2339 | 6.7126 | 0.025798 | 41.2854 | 0.44568
2025-05-20 00:06 | 1657 | Remove | 2025-05-20 | 0:06 | ST | GS | - | 103 | g | 0 | 114.2 | 11.151 | 1093.3 | 804 | 13:50 | 28.4 | 2.42 m/s | 28 | 29.6 | 3.9 m/s | 21.5 |  | 2.42 | m/s |  | 3.9 | m/s | 13.8297 | 0.0091108 | 15.951 |  | -2.5 | 184 | 0.184 | 86.6902 | 7.7888 | 6.3859 | 0.027726 | 41.3131 | 0.44538
2025-05-20 00:07 | 1658 | Remove | 2025-05-20 | 0:07 | ST | GS | - | 109 | g | 0 | 114.2 | 11.159 | 1094 | 813 | 13:50 | 28.4 | 2.23 m/s | 30.2 | 29.6 | 4.09 m/s | 22.2 |  | 2.23 | m/s |  | 4.09 | m/s | 13.8381 | 0.0091167 | 15.9601 |  | 6 | 190 | 0.19 | 84.0006 | 8.4008 | 6.5938 | 0.027557 | 41.3407 | 0.4596
2025-05-20 00:07 | 1659 | Remove | 2025-05-20 | 0:07 | ST | GS | - | 103.5 | g | 0 | 114.3 | 11.143 | 1092.5 | 823 | 13:51 | 28.4 | 2.06 m/s | 29.3 | 29.6 | 4.1 m/s | 22.2 |  | 2.06 | m/s |  | 4.1 | m/s | 13.8464 | 0.0091042 | 15.9692 |  | -5.5 | 190 | 0.19 | 84.0485 | 8.1504 | 6.5938 | 0.024697 | 41.3654 | 0.45932
2025-05-20 00:08 | 1660 | Remove | 2025-05-20 | 0:08 | ST | GS | - | 105 | g | 0 | 114.3 | 11.14 | 1092.4 | 832 | 13:51 | 28.3 | 2.05 m/s | 28.7 | 29.6 | 4.1 m/s | 22.1 |  | 2.05 | m/s |  | 4.1 | m/s | 13.8547 | 0.0091033 | 15.9783 |  | 1.5 | 191.5 | 0.1915 | 83.4377 | 7.9398 | 6.5641 | 0.023942 | 41.3893 | 0.46268
2025-05-20 00:08 | 1661 | Remove | 2025-05-20 | 0:08 | ST | GS | - | 104 | g | 0 | 114.3 | 11.135 | 1091.3 | 841 | 13:52 | 28.3 | 2.26 m/s | 30.7 | 29.6 | 4.04 m/s | 23.1 |  | 2.26 | m/s |  | 4.04 | m/s | 13.8631 | 0.0090942 | 15.9874 |  | -1 | 191.5 | 0.1915 | 83.4852 | 8.4931 | 6.8611 | 0.028234 | 41.4176 | 0.46236
2025-05-20 00:09 | 1662 | Remove | 2025-05-20 | 0:09 | US | GS | - | 108.5 | g | 0 | 114.4 | 11.152 | 1093.5 | 850 | 13:52 | 28.3 | 2.35 m/s | 30 | 29.6 | 3.97 m/s | 23 |  | 2.35 | m/s |  | 3.97 | m/s | 13.8714 | 0.0091125 | 15.9965 |  | 4.5 | 196 | 0.196 | 81.6149 | 8.2994 | 6.8314 | 0.028689 | 41.4462 | 0.4729
2025-05-20 00:09 | 1663 | Remove | 2025-05-20 | 0:09 | US | GS | - | 106 | g | 0 | 114.4 | 11.139 | 1091.9 | 859 | 13:53 | 28.3 | 2.16 m/s | 30.5 | 29.6 | 4.01 m/s | 23 |  | 2.16 | m/s |  | 4.01 | m/s | 13.8797 | 0.0090992 | 16.0056 |  | -2.5 | 196 | 0.196 | 81.6614 | 8.4378 | 6.8314 | 0.026809 | 41.4731 | 0.4726
2025-05-20 00:10 | 1664 | Remove | 2025-05-20 | 0:10 | ST | GS | - | 103.5 | g | 0 | 114.3 | 11.138 | 1092.3 | 868 | 13:53 | 28.3 | 2.37 m/s | 29.8 | 29.6 | 3.98 m/s | 23 |  | 2.37 | m/s |  | 3.98 | m/s | 13.8881 | 0.0091025 | 16.0147 |  | -2.5 | 196 | 0.196 | 81.7078 | 8.2441 | 6.8314 | 0.028741 | 41.5018 | 0.47227
2025-05-20 00:10 | 1665 | Remove | 2025-05-20 | 0:10 | ST | GS | - | 103.5 | g | 0 | 114.4 | 11.14 | 1091.8 | 877 | 13:54 | 28.3 | 2.16 m/s | 30.6 | 29.5 | 4.09 m/s | 22.7 |  | 2.16 | m/s |  | 4.09 | m/s | 13.8964 | 0.0090983 | 16.0238 |  | 0 | 196 | 0.196 | 81.7542 | 8.4654 | 6.7058 | 0.026897 | 41.5287 | 0.47196
2025-05-20 00:11 | 1666 | Remove | 2025-05-20 | 0:11 | US | GS | - | 105 | g | 0 | 114.4 | 11.147 | 1092.4 | 886 | 13:54 | 28.3 | 2.23 m/s | 31.1 | 29.5 | 4.0 m/s | 23.7 |  | 2.23 | m/s |  | 4 | m/s | 13.9047 | 0.0091033 | 16.0329 |  | 1.5 | 197.5 | 0.1975 | 81.1794 | 8.6038 | 7.0012 | 0.028222 | 41.5569 | 0.47525
2025-05-20 00:11 | 1667 | Remove | 2025-05-20 | 0:11 | US | GS | - | 106 | g | 0 | 114.4 | 11.137 | 1091.1 | 896 | 13:55 | 28.3 | 2.09 m/s | 29.5 | 29.5 | 4.06 m/s | 22.6 |  | 2.09 | m/s |  | 4.06 | m/s | 13.9131 | 0.0090925 | 16.042 |  | 1 | 198.5 | 0.1985 | 80.8162 | 8.1611 | 6.6762 | 0.02509 | 41.582 | 0.47737
2025-05-20 00:12 | 1668 | Remove | 2025-05-20 | 0:12 | ST | GS | - | 104 | g | 0 | 114.4 | 11.153 | 1093.8 | 905 | 13:55 | 28.3 | 2.16 m/s | 29.4 | 29.5 | 4.09 m/s | 21.7 |  | 2.16 | m/s |  | 4.09 | m/s | 13.9214 | 0.009115 | 16.0511 |  | -2 | 198.5 | 0.1985 | 80.8622 | 8.1335 | 6.4103 | 0.025842 | 41.6078 | 0.47707
2025-05-20 00:12 | 1669 | Remove | 2025-05-20 | 0:12 | ST | GS | - | 105 | g | 0 | 114.4 | 11.151 | 1093.1 | 914 | 13:56 | 28.3 | 2.38 m/s | 30.4 | 29.5 | 4.2 m/s | 23 |  | 2.38 | m/s |  | 4.2 | m/s | 13.93 | 0.0091092 | 16.0602 |  | 1 | 199.5 | 0.1995 | 80.5025 | 8.4101 | 6.7944 | 0.029443 | 41.6373 | 0.47914
2025-05-20 00:13 | 1670 | Remove | 2025-05-20 | 0:13 | ST | GS | - | 107 | g | 0 | 114.4 | 11.159 | 1094.3 | 923 | 13:56 | 28.3 | 2.27 m/s | 28.3 | 29.5 | 3.96 m/s | 21.7 |  | 2.27 | m/s |  | 3.96 | m/s | 13.9383 | 0.0091192 | 16.0694 |  | 2 | 201.5 | 0.2015 | 79.7487 | 7.8291 | 6.4103 | 0.026142 | 41.6634 | 0.48364
2025-05-20 00:14 | 1671 | Remove | 2025-05-20 | 0:14 | ST | GS | - | 105.5 | g | 0 | 114.4 | 11.136 | 1091.6 | 932 | 13:57 | 28.3 | 2.18 m/s | 29.5 | 29.5 | 4.0 m/s | 22.8 |  | 2.18 | m/s |  | 4 | m/s | 13.9467 | 0.0090967 | 16.0785 |  | -1.5 | 201.5 | 0.2015 | 79.7939 | 8.1611 | 6.7353 | 0.02617 | 41.6896 | 0.48333
2025-05-20 00:14 | 1672 | Remove | 2025-05-20 | 0:14 | ST | GS | - | 104 | g | 0 | 114.4 | 11.142 | 1092.2 | 941 | 13:57 | 28.3 | 2.35 m/s | 31.5 | 29.5 | 3.96 m/s | 24.5 |  | 2.35 | m/s |  | 3.96 | m/s | 13.955 | 0.0091017 | 16.0876 |  | -1.5 | 201.5 | 0.2015 | 79.839 | 8.7144 | 7.2375 | 0.030124 | 41.7197 | 0.48298
2025-05-20 00:14 | 1673 | Remove | 2025-05-20 | 0:15 | ST | GS | - | 104 | g | 0 | 114.4 | 11.142 | 1091.4 | 950 | 13:58 | 28.3 | 2.22 m/s | 30.6 | 29.5 | 4.0 m/s | 23.3 |  | 2.22 | m/s |  | 4 | m/s | 13.9633 | 0.009095 | 16.0967 |  | 0 | 201.5 | 0.2015 | 79.8842 | 8.4654 | 6.883 | 0.027644 | 41.7474 | 0.48267
2025-05-20 00:15 | 1674 | Remove | 2025-05-20 | 0:15 | ST | GS | - | 109 | g | 0 | 114.5 | 11.145 | 1092.4 | 960 | 13:58 | 28.3 | 2.11 m/s | 30.2 | 29.5 | 4.2 m/s | 22.9 |  | 2.11 | m/s |  | 4.2 | m/s | 13.9717 | 0.0091033 | 16.1058 |  | 5 | 206.5 | 0.2065 | 77.994 | 8.3548 | 6.7648 | 0.025931 | 41.7733 | 0.49433
2025-05-20 00:16 | 1675 | Remove | 2025-05-20 | 0:16 | ST | GS | - | 103.5 | g | 0 | 114.5 | 11.128 | 1089.9 | 969 | 13:59 | 28.3 | 2.09 m/s | 30.6 | 29.5 | 3.98 m/s | 23.7 |  | 2.09 | m/s |  | 3.98 | m/s | 13.98 | 0.0090825 | 16.1148 |  | -5.5 | 206.5 | 0.2065 | 78.038 | 8.4654 | 7.0012 | 0.026025 | 41.7993 | 0.49403
2025-05-20 00:16 | 1676 | Remove | 2025-05-20 | 0:16 | ST | GS | - | 104.5 | g | 0 | 114.5 | 11.14 | 1091.4 | 978 | 13:59 | 28.3 | 2.26 m/s | 30.1 | 29.5 | 4.3 m/s | 23 |  | 2.26 | m/s |  | 4.3 | m/s | 13.9883 | 0.009095 | 16.1239 |  | 1 | 207.5 | 0.2075 | 77.7057 | 8.3271 | 6.7944 | 0.027682 | 41.827 | 0.49609
2025-05-20 00:16 | 1677 | Remove | 2025-05-20 | 0:16 | ST | GS | - | 105 | g | 0 | 114.5 | 11.14 | 1091.8 | 987 | 14:00 | 28.3 | 2.34 m/s | 30.1 | 29.5 | 4.18 m/s | 22.5 |  | 2.34 | m/s |  | 4.18 | m/s | 13.9967 | 0.0090983 | 16.133 |  | 0.5 | 208 | 0.208 | 77.5627 | 8.3271 | 6.6467 | 0.028662 | 41.8557 | 0.49695
2025-05-20 00:17 | 1678 | Remove | 2025-05-20 | 0:17 | US | GS | - | 106.5 | g | 0 | 114.4 | 11.151 | 1093.1 | 996 | 14:00 | 28.3 | 2.31 m/s | 30 | 29.5 | 4.12 m/s | 23 |  | 2.31 | m/s |  | 4.12 | m/s | 14.005 | 0.0091092 | 16.1421 |  | 1.5 | 209.5 | 0.2095 | 77.0508 | 8.2994 | 6.7944 | 0.028201 | 41.8839 | 0.50019
2025-05-20 00:18 | 1679 | Remove | 2025-05-20 | 0:18 | ST | GS | - | 104.5 | g | 0 | 114.5 | 11.132 | 1090.6 | 1005 | 14:01 | 28.3 | 2.16 m/s | 29.1 | 29.5 | 4.04 m/s | 22.5 |  | 2.16 | m/s |  | 4.04 | m/s | 14.0133 | 0.0090883 | 16.1512 |  | -2 | 209.5 | 0.2095 | 77.0942 | 8.0505 | 6.6467 | 0.025579 | 41.9094 | 0.49989
2025-05-20 00:18 | 1680 | Remove | 2025-05-20 | 0:18 | ST | GS | - | 106 | g | 0 | 114.4 | 11.148 | 1093.2 | 1014 | 14:01 | 28.3 | 2.41 m/s | 30.1 | 29.5 | 4.2 m/s | 22.8 |  | 2.41 | m/s |  | 4.2 | m/s | 14.0217 | 0.00911 | 16.1603 |  | 1.5 | 211 | 0.211 | 76.5893 | 8.3271 | 6.7353 | 0.02952 | 41.939 | 0.50311
2025-05-20 00:18 | 1681 | Keep | 2025-05-20 | 0:18 | ST | GS | - | 106.5 | g | 0 | 114.5 | 11.163 | 1094.8 | 1023 | 14:02 | 28.3 | 2.16 m/s | 30.6 | 29.5 | 4.04 m/s | 23 |  | 2.16 | m/s |  | 4.04 | m/s | 14.03 | 0.0091233 | 16.1695 |  | 0.5 | 211.5 | 0.2115 | 76.4514 | 8.4654 | 6.7944 | 0.026897 | 41.9659 | 0.50398
2025-05-20 00:19 | 1682 | Remove | 2025-05-20 | 0:19 | ST | GS | - | 107 | g | 0 | 114.5 | 11.147 | 1092.8 | 1033 | 14:02 | 28.3 | 2.23 m/s | 30.6 | 29.5 | 4.24 m/s | 24 |  | 2.23 | m/s |  | 4.24 | m/s | 14.0383 | 0.0091067 | 16.1786 |  | 0.5 | 212 | 0.212 | 76.314 | 8.4654 | 7.0898 | 0.027769 | 41.9936 | 0.50484
2025-05-20 00:20 | 1683 | Remove | 2025-05-20 | 0:20 | ST | GS | - | 104 | g | 0 | 114.5 | 11.133 | 1090.5 | 1042 | 14:03 | 28.3 | 2.22 m/s | 30 | 29.5 | 4.24 m/s | 22.8 |  | 2.22 | m/s |  | 4.24 | m/s | 14.0467 | 0.0090875 | 16.1877 |  | -3 | 212 | 0.212 | 76.3569 | 8.2994 | 6.7353 | 0.027102 | 42.0207 | 0.50451
2025-05-20 00:20 | 1684 | Remove | 2025-05-20 | 0:20 | ST | GS | - | 104.5 | g | 0 | 114.5 | 11.153 | 1093.1 | 1051 | 14:03 | 28.3 | 2.38 m/s | 29.6 | 29.5 | 4.12 m/s | 22.8 |  | 2.38 | m/s |  | 4.12 | m/s | 14.055 | 0.0091092 | 16.1968 |  | 0.5 | 212.5 | 0.2125 | 76.2201 | 8.1888 | 6.7353 | 0.028668 | 42.0494 | 0.50536
2025-05-20 00:20 | 1685 | Remove | 2025-05-20 | 0:20 | ST | GS | - | 104 | g | 0 | 114.5 | 11.148 | 1093.1 | 1060 | 14:04 | 28.3 | 2.09 m/s | 28.8 | 29.5 | 4.2 m/s | 22.5 |  | 2.09 | m/s |  | 4.2 | m/s | 14.0633 | 0.0091092 | 16.2059 |  | -0.5 | 212.5 | 0.2125 | 76.263 | 7.9675 | 6.6467 | 0.024494 | 42.0739 | 0.50506
2025-05-20 00:21 | 1686 | Remove | 2025-05-20 | 0:21 | ST | GS | - | 104.5 | g | 0 | 114.5 | 11.161 | 1094.8 | 1069 | 14:04 | 28.3 | 2.35 m/s | 28 | 29.5 | 4.13 m/s | 21.6 |  | 2.35 | m/s |  | 4.13 | m/s | 14.0717 | 0.0091233 | 16.215 |  | 0.5 | 213 | 0.213 | 76.1268 | 7.7461 | 6.3808 | 0.026777 | 42.1007 | 0.50593
2025-05-20 00:22 | 1687 | Remove | 2025-05-20 | 0:22 | ST | GS | - | 104 | g | 0 | 114.5 | 11.162 | 1094.3 | 1078 | 14:05 | 28.3 | 2.33 m/s | 27.8 | 29.5 | 4.18 m/s | 21.6 |  | 2.33 | m/s |  | 4.18 | m/s | 14.08 | 0.0091192 | 16.2241 |  | -0.5 | 213 | 0.213 | 76.1696 | 7.6908 | 6.3808 | 0.026359 | 42.127 | 0.50561
2025-05-20 00:22 | 1688 | Remove | 2025-05-20 | 0:22 | ST | GS | - | 106 | g | 0 | 114.5 | 11.161 | 1094.1 | 1088 | 14:05 | 28.3 | 2.23 m/s | 28 | 29.5 | 4.1 m/s | 21.3 |  | 2.23 | m/s |  | 4.1 | m/s | 14.0886 | 0.0091175 | 16.2332 |  | 2 | 215 | 0.215 | 75.5035 | 7.7461 | 6.2922 | 0.025409 | 42.1524 | 0.51005
2025-05-20 00:23 | 1689 | Remove | 2025-05-20 | 0:23 | US | GS | - | 106 | g | 0 | 114.5 | 11.143 | 1091.9 | 1097 | 14:06 | 28.3 | 2.25 m/s | 28.7 | 29.5 | 4.18 m/s | 21.8 |  | 2.25 | m/s |  | 4.18 | m/s | 14.0969 | 0.0090992 | 16.2423 |  | 0 | 215 | 0.215 | 75.5458 | 7.9398 | 6.4399 | 0.026278 | 42.1787 | 0.50974
2025-05-20 00:23 | 1690 | Remove | 2025-05-20 | 0:23 | ST | GS | - | 108 | g | 0 | 114.5 | 11.153 | 1093.4 | 1106 | 14:06 | 28.3 | 2.33 m/s | 28.8 | 29.5 | 4.09 m/s | 22.3 |  | 2.33 | m/s |  | 4.09 | m/s | 14.1053 | 0.0091117 | 16.2515 |  | 2 | 217 | 0.217 | 74.8915 | 7.9675 | 6.5876 | 0.027307 | 42.206 | 0.51414
2025-05-20 00:24 | 1691 | Remove | 2025-05-20 | 0:24 | US | GS | - | 106 | g | 0 | 114.5 | 11.165 | 1094.5 | 1115 | 14:07 | 28.3 | 2.22 m/s | 28.4 | 29.5 | 3.99 m/s | 21.3 |  | 2.22 | m/s |  | 3.99 | m/s | 14.1136 | 0.0091208 | 16.2606 |  | -2 | 217 | 0.217 | 74.9335 | 7.8568 | 6.2922 | 0.025657 | 42.2317 | 0.51383
2025-05-20 00:24 | 1692 | Remove | 2025-05-20 | 0:24 | US | GS | - | 103 | g | 0 | 114.5 | 11.152 | 1093.2 | 1124 | 14:07 | 28.3 | 2.27 m/s | 28.5 | 29.5 | 4.16 m/s | 22 |  | 2.27 | m/s |  | 4.16 | m/s | 14.1219 | 0.00911 | 16.2697 |  | -3 | 217 | 0.217 | 74.9755 | 7.8845 | 6.499 | 0.026327 | 42.258 | 0.51351
2025-05-20 00:25 | 1693 | Remove | 2025-05-20 | 0:25 | US | GS | - | 108 | g | 0 | 114.5 | 11.166 | 1095.2 | 1133 | 14:08 | 28.3 | 2.22 m/s | 29.5 | 29.5 | 4.18 m/s | 22.9 |  | 2.22 | m/s |  | 4.18 | m/s | 14.1303 | 0.0091267 | 16.2788 |  | 5 | 222 | 0.222 | 73.328 | 8.1611 | 6.7648 | 0.02665 | 42.2847 | 0.52501
2025-05-20 00:25 | 1694 | Remove | 2025-05-20 | 0:25 | US | GS | - | 104.5 | g | 0 | 114.5 | 11.175 | 1095.9 | 1142 | 14:08 | 28.3 | 2.12 m/s | 30.1 | 29.5 | 4.09 m/s | 22.8 |  | 2.12 | m/s |  | 4.09 | m/s | 14.1386 | 0.0091325 | 16.2879 |  | -3.5 | 222 | 0.222 | 73.3691 | 8.3271 | 6.7353 | 0.025968 | 42.3106 | 0.52469
2025-05-20 00:26 | 1695 | Remove | 2025-05-20 | 0:26 | ST | GS | - | 105 | g | 0 | 114.5 | 11.178 | 1096.6 | 1151 | 14:09 | 28.3 | 2.54 m/s | 27.5 | 29.5 | 4.1 m/s | 21 |  | 2.54 | m/s |  | 4.1 | m/s | 14.1469 | 0.0091383 | 16.2971 |  | 0.5 | 222.5 | 0.2225 | 73.2453 | 7.6078 | 6.2036 | 0.028425 | 42.3391 | 0.52552
2025-05-20 00:26 | 1696 | Remove | 2025-05-20 | 0:26 | ST | GS | - | 103.5 | g | 0 | 114.6 | 11.163 | 1094 | 1161 | 14:09 | 28.3 | 2.26 m/s | 29.5 | 29.5 | 4.0 m/s | 22.1 |  | 2.26 | m/s |  | 4 | m/s | 14.1553 | 0.0091167 | 16.3062 |  | -1.5 | 222.5 | 0.2225 | 73.2863 | 8.1611 | 6.5285 | 0.027131 | 42.3662 | 0.52518
2025-05-20 00:27 | 1697 | Remove | 2025-05-20 | 0:27 | ST | GS | - | 104.5 | g | 0 | 114.5 | 11.152 | 1093.1 | 1170 | 14:10 | 28.3 | 2.11 m/s | 29.4 | 29.5 | 4.24 m/s | 22.3 |  | 2.11 | m/s |  | 4.24 | m/s | 14.1636 | 0.0091092 | 16.3153 |  | 1 | 223.5 | 0.2235 | 72.9991 | 8.1335 | 6.5876 | 0.025244 | 42.3914 | 0.52723
2025-05-20 00:27 | 1698 | Remove | 2025-05-20 | 0:27 | ST | GS | - | 104 | g | 0 | 114.5 | 11.148 | 1092.9 | 1179 | 14:10 | 28.3 | 2.19 m/s | 29 | 29.6 | 4.1 m/s | 22.5 |  | 2.19 | m/s |  | 4.1 | m/s | 14.1719 | 0.0091075 | 16.3244 |  | -0.5 | 223.5 | 0.2235 | 73.0399 | 8.0228 | 6.6829 | 0.025845 | 42.4173 | 0.52691
2025-05-20 00:28 | 1699 | Remove | 2025-05-20 | 0:28 | ST | GS | - | 105 | g | 0 | 114.5 | 11.141 | 1091.6 | 1188 | 14:11 | 28.3 | 2.16 m/s | 28.7 | 29.6 | 4.23 m/s | 21.9 |  | 2.16 | m/s |  | 4.23 | m/s | 14.1803 | 0.0090967 | 16.3335 |  | 1 | 224.5 | 0.2245 | 72.7551 | 7.9398 | 6.5047 | 0.025227 | 42.4425 | 0.52895
2025-05-20 00:28 | 1700 | Remove | 2025-05-20 | 0:28 | ST | GS | - | 105.5 | g | 0 | 114.5 | 11.137 | 1091.9 | 1197 | 14:11 | 28.3 | 2.2 m/s | 29.5 | 29.6 | 4.06 m/s | 22.5 |  | 2.2 | m/s |  | 4.06 | m/s | 14.1886 | 0.0090992 | 16.3426 |  | 0.5 | 225 | 0.225 | 72.6338 | 8.1611 | 6.6829 | 0.02641 | 42.4689 | 0.5298
2025-05-20 00:29 | 1701 | Remove | 2025-05-20 | 0:29 | ST | GS | - | 104.5 | g | 0 | 114.6 | 11.146 | 1092.3 | 1206 | 14:12 | 28.3 | 2.34 m/s | 30 | 29.6 | 4.26 m/s | 22.1 |  | 2.34 | m/s |  | 4.26 | m/s | 14.1969 | 0.0091025 | 16.3517 |  | -1 | 225 | 0.225 | 72.6743 | 8.2994 | 6.5641 | 0.028567 | 42.4975 | 0.52944
2025-05-20 00:29 | 1702 | Remove | 2025-05-20 | 0:29 | US | GS | - | 106 | g | 0 | 114.5 | 11.139 | 1091.8 | 1215 | 14:12 | 28.3 | 2.09 m/s | 28.9 | 29.6 | 4.18 m/s | 21.8 |  | 2.09 | m/s |  | 4.18 | m/s | 14.2053 | 0.0090983 | 16.3608 |  | 1.5 | 226.5 | 0.2265 | 72.2332 | 7.9951 | 6.475 | 0.02458 | 42.5221 | 0.53266
2025-05-20 00:30 | 1703 | Remove | 2025-05-20 | 0:30 | ST | GS | - | 105.5 | g | 0 | 114.7 | 11.147 | 1093.1 | 1225 | 14:13 | 28.3 | 2.18 m/s | 29.1 | 29.5 | 4.24 m/s | 22.2 |  | 2.18 | m/s |  | 4.24 | m/s | 14.2136 | 0.0091092 | 16.3699 |  | -0.5 | 226.5 | 0.2265 | 72.2734 | 8.0505 | 6.558 | 0.025815 | 42.5479 | 0.53234
2025-05-20 00:30 | 1704 | Remove | 2025-05-20 | 0:30 | ST | GS | - | 104.5 | g | 0 | 114.6 | 11.133 | 1091 | 1234 | 14:13 | 28.3 | 2.37 m/s | 30.1 | 29.5 | 4.01 m/s | 23.4 |  | 2.37 | m/s |  | 4.01 | m/s | 14.2219 | 0.0090917 | 16.379 |  | -1 | 226.5 | 0.2265 | 72.3135 | 8.3271 | 6.9125 | 0.02903 | 42.5769 | 0.53198
2025-05-20 00:31 | 1705 | Remove | 2025-05-20 | 0:31 | ST | GS | - | 106 | g | 0 | 114.6 | 11.149 | 1092.5 | 1243 | 14:14 | 28.3 | 2.18 m/s | 32 | 29.5 | 4.24 m/s | 24 |  | 2.18 | m/s |  | 4.24 | m/s | 14.2303 | 0.0091042 | 16.3881 |  | 1.5 | 228 | 0.228 | 71.8777 | 8.8527 | 7.0898 | 0.028388 | 42.6053 | 0.53514
2025-05-20 00:31 | 1706 | Remove | 2025-05-20 | 0:31 | ST | GS | - | 105 | g | 0 | 114.5 | 11.133 | 1091.5 | 1252 | 14:14 | 28.3 | 2.16 m/s | 31.4 | 29.5 | 4.12 m/s | 24.3 |  | 2.16 | m/s |  | 4.12 | m/s | 14.2389 | 0.0090958 | 16.3972 |  | -1 | 228 | 0.228 | 71.9176 | 8.6867 | 7.1784 | 0.0276 | 42.6329 | 0.5348
2025-05-20 00:32 | 1707 | Remove | 2025-05-20 | 0:32 | ST | GS | - | 105 | g | 0 | 114.6 | 11.142 | 1091.9 | 1261 | 14:15 | 28.3 | 2.23 m/s | 30.4 | 29.5 | 4.13 m/s | 22.8 |  | 2.23 | m/s |  | 4.13 | m/s | 14.2472 | 0.0090992 | 16.4063 |  | 0 | 228 | 0.228 | 71.9575 | 8.4101 | 6.7353 | 0.027587 | 42.6605 | 0.53445
2025-05-20 00:32 | 1708 | Remove | 2025-05-20 | 0:32 | ST | GS | - | 104 | g | 0 | 114.6 | 11.116 | 1089.1 | 1270 | 14:15 | 28.3 | 2.13 m/s | 32.5 | 29.5 | 4.0 m/s | 25.5 |  | 2.13 | m/s |  | 4 | m/s | 14.2556 | 0.0090758 | 16.4154 |  | -1 | 228 | 0.228 | 71.9973 | 8.9911 | 7.5329 | 0.02817 | 42.6887 | 0.5341
2025-05-20 00:33 | 1709 | Remove | 2025-05-20 | 0:33 | ST | GS | - | 105 | g | 0 | 114.6 | 11.14 | 1091.5 | 1279 | 14:16 | 28.3 | 2.3 m/s | 31.6 | 29.5 | 4.04 m/s | 24 |  | 2.3 | m/s |  | 4.04 | m/s | 14.2639 | 0.0090958 | 16.4245 |  | 1 | 229 | 0.229 | 71.7226 | 8.7421 | 7.0898 | 0.029576 | 42.7182 | 0.53607
2025-05-20 00:33 | 1710 | Remove | 2025-05-20 | 0:33 | US | GS | - | 106.5 | g | 0 | 114.7 | 11.15 | 1093.2 | 1288 | 14:16 | 28.3 | 2.16 m/s | 30 | 29.5 | 4.06 m/s | 23.2 |  | 2.16 | m/s |  | 4.06 | m/s | 14.2722 | 0.00911 | 16.4336 |  | 1.5 | 230.5 | 0.2305 | 71.2954 | 8.2994 | 6.8535 | 0.02637 | 42.7446 | 0.53925
2025-05-20 00:34 | 1711 | Keep | 2025-05-20 | 0:34 | US | GS | - | 107.5 | g | 0 | 114.7 | 11.13 | 1090.6 | 1297 | 14:17 | 28.3 | 2.12 m/s | 31 | 29.5 | 4.15 m/s | 23.8 |  | 2.12 | m/s |  | 4.15 | m/s | 14.2806 | 0.0090883 | 16.4427 |  | 1 | 231.5 | 0.2315 | 71.0267 | 8.5761 | 7.0307 | 0.026744 | 42.7713 | 0.54125
2025-05-20 00:34 | 1712 | Remove | 2025-05-20 | 0:34 | ST | GS | - | 105 | g | 0 | 114.7 | 11.111 | 1088 | 1307 | 14:17 | 28.3 | 2.08 m/s | 31 | 29.5 | 4.26 m/s | 23.8 |  | 2.08 | m/s |  | 4.26 | m/s | 14.2889 | 0.0090667 | 16.4517 |  | -2.5 | 231.5 | 0.2315 | 71.0659 | 8.5761 | 7.0307 | 0.026239 | 42.7976 | 0.54092
2025-05-20 00:35 | 1713 | Remove | 2025-05-20 | 0:35 | ST | GS | - | 105 | g | 0 | 114.7 | 11.116 | 1089 | 1316 | 14:18 | 28.3 | 2.11 m/s | 31.2 | 29.5 | 4.13 m/s | 23.5 |  | 2.11 | m/s |  | 4.13 | m/s | 14.2972 | 0.009075 | 16.4608 |  | 0 | 231.5 | 0.2315 | 71.1051 | 8.6314 | 6.9421 | 0.02679 | 42.8244 | 0.54058
2025-05-20 00:35 | 1714 | Remove | 2025-05-20 | 0:35 | ST | GS | - | 108 | g | 0 | 114.7 | 11.142 | 1091.9 | 1325 | 14:18 | 28.3 | 2.27 m/s | 31 | 29.5 | 4.2 m/s | 23.3 |  | 2.27 | m/s |  | 4.2 | m/s | 14.3056 | 0.0090992 | 16.4699 |  | 3 | 234.5 | 0.2345 | 70.2342 | 8.5761 | 6.883 | 0.028636 | 42.853 | 0.54722
2025-05-20 00:36 | 1715 | Remove | 2025-05-20 | 0:36 | US | GS | - | 105 | g | 0 | 114.7 | 11.129 | 1090.7 | 1334 | 14:19 | 28.3 | 2.09 m/s | 31.2 | 29.5 | 4.1 m/s | 23.5 |  | 2.09 | m/s |  | 4.1 | m/s | 14.3139 | 0.0090892 | 16.479 |  | -3 | 234.5 | 0.2345 | 70.273 | 8.6314 | 6.9421 | 0.026536 | 42.8795 | 0.54688
2025-05-20 00:36 | 1716 | Remove | 2025-05-20 | 0:36 | ST | GS | - | 107.5 | g | 0 | 114.7 | 11.13 | 1090.9 | 1343 | 14:19 | 28.3 | 2.2 m/s | 31.4 | 29.5 | 4.24 m/s | 24.2 |  | 2.2 | m/s |  | 4.24 | m/s | 14.3222 | 0.0090908 | 16.4881 |  | 2.5 | 237 | 0.237 | 69.5701 | 8.6867 | 7.1489 | 0.028111 | 42.9077 | 0.55235
2025-05-20 00:37 | 1717 | Remove | 2025-05-20 | 0:37 | ST | GS | - | 105 | g | 0 | 114.7 | 11.139 | 1091.3 | 1352 | 14:20 | 28.3 | 2.15 m/s | 31.2 | 29.5 | 4.1 m/s | 23.9 |  | 2.15 | m/s |  | 4.1 | m/s | 14.3306 | 0.0090942 | 16.4972 |  | -2.5 | 237 | 0.237 | 69.6084 | 8.6314 | 7.0602 | 0.027297 | 42.935 | 0.552
2025-05-20 00:37 | 1718 | Remove | 2025-05-20 | 0:37 | ST | GS | - | 106 | g | 0 | 114.7 | 11.118 | 1089.2 | 1361 | 14:20 | 28.3 | 2.11 m/s | 31.4 | 29.5 | 4.23 m/s | 23.8 |  | 2.11 | m/s |  | 4.23 | m/s | 14.3389 | 0.0090767 | 16.5063 |  | 1 | 238 | 0.238 | 69.3541 | 8.6867 | 7.0307 | 0.026961 | 42.9619 | 0.55398
2025-05-20 00:38 | 1719 | Remove | 2025-05-20 | 0:38 | ST | GS | - | 105.5 | g | 0 | 114.7 | 11.129 | 1090.8 | 1370 | 14:21 | 28.3 | 2.23 m/s | 31.8 | 29.5 | 4.04 m/s | 23.6 |  | 2.23 | m/s |  | 4.04 | m/s | 14.3472 | 0.00909 | 16.5154 |  | -0.5 | 238 | 0.238 | 69.3923 | 8.7974 | 6.9716 | 0.028858 | 42.9908 | 0.55361
2025-05-20 00:38 | 1720 | Remove | 2025-05-20 | 0:38 | ST | GS | - | 108 | g | 0 | 114.6 | 11.149 | 1093.1 | 1380 | 14:21 | 28.3 | 2.3 m/s | 31.7 | 29.5 | 4.04 m/s | 23.6 |  | 2.3 | m/s |  | 4.04 | m/s | 14.3556 | 0.0091092 | 16.5245 |  | 2.5 | 240.5 | 0.2405 | 68.7088 | 8.7697 | 6.9716 | 0.02967 | 43.0204 | 0.55904
2025-05-20 00:39 | 1721 | Remove | 2025-05-20 | 0:39 | ST | GS | - | 105.5 | g | 0 | 114.7 | 11.147 | 1092.3 | 1389 | 14:22 | 28.3 | 2.22 m/s | 29.6 | 29.5 | 4.0 m/s | 22.6 |  | 2.22 | m/s |  | 4 | m/s | 14.3639 | 0.0091025 | 16.5336 |  | -2.5 | 240.5 | 0.2405 | 68.7467 | 8.1888 | 6.6762 | 0.026741 | 43.0472 | 0.55869
2025-05-20 00:39 | 1722 | Remove | 2025-05-20 | 0:39 | ST | GS | - | 105.5 | g | 0 | 114.7 | 11.117 | 1088.4 | 1398 | 14:22 | 28.3 | 2.25 m/s | 31.3 | 29.5 | 4.33 m/s | 24 |  | 2.25 | m/s |  | 4.33 | m/s | 14.3722 | 0.00907 | 16.5426 |  | 0 | 240.5 | 0.2405 | 68.7844 | 8.6591 | 7.0898 | 0.028659 | 43.0758 | 0.55832
2025-05-20 00:40 | 1723 | Remove | 2025-05-20 | 0:40 | ST | GS | - | 108 | g | 0 | 114.6 | 11.137 | 1091.5 | 1407 | 14:23 | 28.3 | 2.18 m/s | 30.8 | 29.5 | 4.09 m/s | 23.5 |  | 2.18 | m/s |  | 4.09 | m/s | 14.3808 | 0.0090958 | 16.5517 |  | 2.5 | 243 | 0.243 | 68.1142 | 8.5208 | 6.9421 | 0.027324 | 43.1032 | 0.56376
2025-05-20 00:40 | 1724 | Remove | 2025-05-20 | 0:40 | ST | GS | - | 105.5 | g | 0 | 114.6 | 11.148 | 1092.7 | 1416 | 14:23 | 28.3 | 2.38 m/s | 30.8 | 29.5 | 3.97 m/s | 22.7 |  | 2.38 | m/s |  | 3.97 | m/s | 14.3892 | 0.0091058 | 16.5608 |  | -2.5 | 243 | 0.243 | 68.1516 | 8.5208 | 6.7058 | 0.02983 | 43.133 | 0.56337
2025-05-20 00:41 | 1725 | Remove | 2025-05-20 | 0:41 | ST | GS | - | 106 | g | 0 | 114.7 | 11.131 | 1090.7 | 1425 | 14:24 | 28.3 | 2.18 m/s | 32.1 | 29.5 | 4.24 m/s | 24.1 |  | 2.18 | m/s |  | 4.24 | m/s | 14.3975 | 0.0090892 | 16.5699 |  | 0.5 | 243.5 | 0.2435 | 68.049 | 8.8804 | 7.1193 | 0.028477 | 43.1615 | 0.56416
2025-05-20 00:41 | 1726 | Remove | 2025-05-20 | 0:41 | ST | GS | - | 106 | g | 0 | 114.6 | 11.142 | 1091.8 | 1434 | 14:24 | 28.3 | 2.19 m/s | 30.5 | 29.5 | 4.1 m/s | 22.9 |  | 2.19 | m/s |  | 4.1 | m/s | 14.4058 | 0.0090983 | 16.579 |  | 0 | 243.5 | 0.2435 | 68.0864 | 8.4378 | 6.7648 | 0.027182 | 43.1887 | 0.56381
2025-05-20 00:42 | 1727 | Remove | 2025-05-20 | 0:42 | ST | GS | - | 105.5 | g | 0 | 114.6 | 11.12 | 1089 | 1443 | 14:25 | 28.3 | 2.05 m/s | 30 | 29.5 | 4.23 m/s | 22.8 |  | 2.05 | m/s |  | 4.23 | m/s | 14.4142 | 0.009075 | 16.5881 |  | -0.5 | 243.5 | 0.2435 | 68.1237 | 8.2994 | 6.7353 | 0.025027 | 43.2137 | 0.56348
2025-05-20 00:42 | 1728 | Remove | 2025-05-20 | 0:42 | ST | GS | - | 105.5 | g | 0 | 114.8 | 11.133 | 1090.9 | 1453 | 14:25 | 28.3 | 2.2 m/s | 29.6 | 29.5 | 4.21 m/s | 22.3 |  | 2.2 | m/s |  | 4.21 | m/s | 14.4225 | 0.0090908 | 16.5972 |  | 0 | 243.5 | 0.2435 | 68.161 | 8.1888 | 6.5876 | 0.0265 | 43.2402 | 0.56313
2025-05-20 00:43 | 1729 | Remove | 2025-05-20 | 0:43 | ST | GS | - | 106.5 | g | 0 | 114.8 | 11.123 | 1090 | 1462 | 14:26 | 28.3 | 2.19 m/s | 29 | 29.5 | 4.1 m/s | 21.9 |  | 2.19 | m/s |  | 4.1 | m/s | 14.4308 | 0.0090833 | 16.6063 |  | 1 | 244.5 | 0.2445 | 67.9194 | 8.0228 | 6.4694 | 0.025845 | 43.266 | 0.56511
2025-05-20 00:43 | 1730 | Remove | 2025-05-20 | 0:43 | ST | GS | - | 106.5 | g | 0 | 114.7 | 11.125 | 1090.1 | 1471 | 14:26 | 28.3 | 2.12 m/s | 28.9 | 29.5 | 4.26 m/s | 21.3 |  | 2.12 | m/s |  | 4.26 | m/s | 14.4392 | 0.0090842 | 16.6154 |  | 0 | 244.5 | 0.2445 | 67.9565 | 7.9951 | 6.2922 | 0.024932 | 43.291 | 0.56478
2025-05-20 00:44 | 1731 | Remove | 2025-05-20 | 0:44 | ST | GS | - | 107 | g | 0 | 114.7 | 11.15 | 1093.4 | 1480 | 14:27 | 28.3 | 2.26 m/s | 27.3 | 29.5 | 4.1 m/s | 20.7 |  | 2.26 | m/s |  | 4.1 | m/s | 14.4475 | 0.0091117 | 16.6245 |  | 0.5 | 245 | 0.245 | 67.855 | 7.5525 | 6.1149 | 0.025107 | 43.3161 | 0.56561
2025-05-20 00:44 | 1732 | Remove | 2025-05-20 | 0:44 | ST | GS | - | 108.5 | g | 0 | 114.7 | 11.137 | 1091 | 1489 | 14:27 | 28.3 | 2.16 m/s | 28 | 29.5 | 4.09 m/s | 20.9 |  | 2.16 | m/s |  | 4.09 | m/s | 14.4558 | 0.0090917 | 16.6336 |  | 1.5 | 246.5 | 0.2465 | 67.479 | 7.7461 | 6.174 | 0.024612 | 43.3407 | 0.56875
2025-05-20 00:45 | 1733 | Remove | 2025-05-20 | 0:45 | US | GS | - | 106.5 | g | 0 | 114.7 | 11.137 | 1091.9 | 1498 | 14:28 | 28.3 | 2.27 m/s | 28.3 | 29.5 | 4.04 m/s | 22 |  | 2.27 | m/s |  | 4.04 | m/s | 14.4642 | 0.0090992 | 16.6427 |  | -2 | 246.5 | 0.2465 | 67.5159 | 7.8291 | 6.499 | 0.026142 | 43.3668 | 0.56841
2025-05-20 00:45 | 1734 | Remove | 2025-05-20 | 0:45 | ST | GS | - | 105.5 | g | 0 | 114.7 | 11.118 | 1088.9 | 1507 | 14:28 | 28.3 | 2.15 m/s | 27.2 | 29.5 | 4.07 m/s | 20.8 |  | 2.15 | m/s |  | 4.07 | m/s | 14.4725 | 0.0090742 | 16.6517 |  | -1 | 246.5 | 0.2465 | 67.5527 | 7.5248 | 6.1445 | 0.023798 | 43.3906 | 0.5681
2025-05-20 00:46 | 1735 | Remove | 2025-05-20 | 0:46 | ST | GS | - | 107 | g | 0 | 114.6 | 11.141 | 1091.6 | 1516 | 14:29 | 28.3 | 2.23 m/s | 27.2 | 29.5 | 4.03 m/s | 20.8 |  | 2.23 | m/s |  | 4.03 | m/s | 14.4808 | 0.0090967 | 16.6608 |  | 1.5 | 248 | 0.248 | 67.1808 | 7.5248 | 6.1445 | 0.024683 | 43.4153 | 0.57123
2025-05-20 00:46 | 1736 | Remove | 2025-05-20 | 0:46 | US | GS | - | 110 | g | 0 | 114.6 | 11.141 | 1092 | 1526 | 14:29 | 28.3 | 2.2 m/s | 26.4 | 29.5 | 4.04 m/s | 20.1 |  | 2.2 | m/s |  | 4.04 | m/s | 14.4892 | 0.0091 | 16.6699 |  | 3 | 251 | 0.251 | 66.4141 | 7.3035 | 5.9377 | 0.023635 | 43.4389 | 0.57782
2025-05-20 00:47 | 1737 | Remove | 2025-05-20 | 0:47 | ST | GS | - | 106.5 | g | 0 | 114.6 | 11.141 | 1091.9 | 1535 | 14:30 | 28.3 | 2.26 m/s | 26 | 29.5 | 4.03 m/s | 20 |  | 2.26 | m/s |  | 4.03 | m/s | 14.4975 | 0.0090992 | 16.679 |  | -3.5 | 251 | 0.251 | 66.4504 | 7.1928 | 5.9082 | 0.023912 | 43.4628 | 0.5775
2025-05-20 00:47 | 1738 | Remove | 2025-05-20 | 0:47 | ST | GS | - | 106 | g | 0 | 114.6 | 11.122 | 1089.6 | 1544 | 14:30 | 28.3 | 2.22 m/s | 26.4 | 29.5 | 4.07 m/s | 20.4 |  | 2.22 | m/s |  | 4.07 | m/s | 14.5058 | 0.00908 | 16.6881 |  | -0.5 | 251 | 0.251 | 66.4865 | 7.3035 | 6.0263 | 0.02385 | 43.4867 | 0.57719
2025-05-20 00:48 | 1739 | Remove | 2025-05-20 | 0:48 | ST | GS | - | 107.5 | g | 0 | 114.6 | 11.137 | 1091.1 | 1553 | 14:31 | 28.3 | 2.11 m/s | 26.1 | 29.5 | 4.06 m/s | 19.6 |  | 2.11 | m/s |  | 4.06 | m/s | 14.5142 | 0.0090925 | 16.6972 |  | 1.5 | 252.5 | 0.2525 | 66.1276 | 7.2205 | 5.79 | 0.022411 | 43.5091 | 0.58034
2025-05-20 00:48 | 1740 | Remove | 2025-05-20 | 0:48 | ST | GS | - | 107.5 | g | 0 | 114.5 | 11.144 | 1092.2 | 1562 | 14:31 | 28.3 | 2.34 m/s | 27 | 29.5 | 4.16 m/s | 20.9 |  | 2.34 | m/s |  | 4.16 | m/s | 14.5228 | 0.0091017 | 16.7063 |  | 0 | 252.5 | 0.2525 | 66.1636 | 7.4695 | 6.174 | 0.02571 | 43.5348 | 0.58
2025-05-20 00:49 | 1741 | Keep | 2025-05-20 | 0:49 | ST | GS | - | 106.5 | g | 0 | 114.7 | 11.148 | 1092.9 | 1571 | 14:32 | 28.3 | 2.27 m/s | 25.5 | 29.5 | 4.1 m/s | 19.3 |  | 2.27 | m/s |  | 4.1 | m/s | 14.5311 | 0.0091075 | 16.7154 |  | -1 | 252.5 | 0.2525 | 66.1997 | 7.0545 | 5.7014 | 0.023556 | 43.5584 | 0.57968
2025-05-20 00:49 | 1742 | Remove | 2025-05-20 | 0:49 | US | GS | - | 106.5 | g | 0 | 114.7 | 11.124 | 1090.1 | 1580 | 14:32 | 28.3 | 2.18 m/s | 26.3 | 29.5 | 3.94 m/s | 19.8 |  | 2.18 | m/s |  | 3.94 | m/s | 14.5394 | 0.0090842 | 16.7245 |  | 0 | 252.5 | 0.2525 | 66.2357 | 7.2758 | 5.8491 | 0.023331 | 43.5817 | 0.57937
2025-05-20 00:50 | 1743 | Remove | 2025-05-20 | 0:50 | ST | GS | - | 109 | g | 0 | 114.7 | 11.134 | 1090.6 | 1589 | 14:33 | 28.3 | 2.42 m/s | 26.4 | 29.5 | 3.93 m/s | 20.2 |  | 2.42 | m/s |  | 3.93 | m/s | 14.5478 | 0.0090883 | 16.7336 |  | 2.5 | 255 | 0.255 | 65.6219 | 7.3035 | 5.9672 | 0.025999 | 43.6077 | 0.58476
2025-05-20 00:50 | 1744 | Remove | 2025-05-20 | 0:50 | US | GS | - | 107.5 | g | 0 | 114.7 | 11.129 | 1090 | 1598 | 14:33 | 28.3 | 2.3 m/s | 27.2 | 29.5 | 4.16 m/s | 20.1 |  | 2.3 | m/s |  | 4.16 | m/s | 14.5561 | 0.0090833 | 16.7427 |  | -1.5 | 255 | 0.255 | 65.6576 | 7.5248 | 5.9377 | 0.025458 | 43.6332 | 0.58442
2025-05-20 00:51 | 1745 | Remove | 2025-05-20 | 0:51 | ST | GS | - | 107 | g | 0 | 114.6 | 11.133 | 1090.3 | 1607 | 14:34 | 28.3 | 2.35 m/s | 26.6 | 29.5 | 4.03 m/s | 20.3 |  | 2.35 | m/s |  | 4.03 | m/s | 14.5644 | 0.0090858 | 16.7518 |  | -0.5 | 255 | 0.255 | 65.6932 | 7.3588 | 5.9968 | 0.025438 | 43.6586 | 0.58408
2025-05-20 00:51 | 1746 | Remove | 2025-05-20 | 0:51 | ST | GS | - | 106 | g | 0 | 114.7 | 11.139 | 1091.3 | 1617 | 14:34 | 28.3 | 2.31 m/s | 25.6 | 29.5 | 4.04 m/s | 19.5 |  | 2.31 | m/s |  | 4.04 | m/s | 14.5728 | 0.0090942 | 16.7609 |  | -1 | 255 | 0.255 | 65.7289 | 7.0822 | 5.7604 | 0.024065 | 43.6827 | 0.58376
2025-05-20 00:52 | 1747 | Remove | 2025-05-20 | 0:52 | ST | GS | - | 109 | g | 0 | 114.6 | 11.131 | 1090 | 1626 | 14:35 | 28.3 | 2.22 m/s | 26.1 | 29.5 | 4.07 m/s | 20 |  | 2.22 | m/s |  | 4.07 | m/s | 14.5811 | 0.0090833 | 16.7699 |  | 3 | 258 | 0.258 | 64.9998 | 7.2205 | 5.9082 | 0.023579 | 43.7062 | 0.5903
2025-05-20 00:52 | 1748 | Remove | 2025-05-20 | 0:52 | ST | GS | - | 108.5 | g | 0 | 114.7 | 11.13 | 1089.5 | 1635 | 14:35 | 28.3 | 2.31 m/s | 25.7 | 29.5 | 4.1 m/s | 19.3 |  | 2.31 | m/s |  | 4.1 | m/s | 14.5894 | 0.0090792 | 16.779 |  | -0.5 | 258 | 0.258 | 65.035 | 7.1099 | 5.7014 | 0.024159 | 43.7304 | 0.58998
2025-05-20 00:53 | 1749 | Remove | 2025-05-20 | 0:53 | US | GS | - | 109.5 | g | 0 | 114.7 | 11.118 | 1088.2 | 1644 | 14:36 | 28.3 | 2.16 m/s | 26.5 | 29.4 | 4.16 m/s | 19.5 |  | 2.16 | m/s |  | 4.16 | m/s | 14.5978 | 0.0090683 | 16.7881 |  | 1 | 259 | 0.259 | 64.8189 | 7.3312 | 5.7292 | 0.023293 | 43.7537 | 0.59195
2025-05-20 00:53 | 1750 | Remove | 2025-05-20 | 0:53 | ST | GS | - | 109 | g | 0 | 114.7 | 11.119 | 1088.8 | 1653 | 14:36 | 28.3 | 2.33 m/s | 25.9 | 29.4 | 4.1 m/s | 20 |  | 2.33 | m/s |  | 4.1 | m/s | 14.6061 | 0.0090733 | 16.7972 |  | -0.5 | 259 | 0.259 | 64.8539 | 7.1652 | 5.8761 | 0.024558 | 43.7783 | 0.59162
2025-05-20 00:54 | 1751 | Remove | 2025-05-20 | 0:54 | ST | GS | - | 108 | g | 0 | 114.7 | 11.119 | 1088.6 | 1662 | 14:37 | 28.3 | 2.34 m/s | 27 | 29.4 | 3.98 m/s | 20.3 |  | 2.34 | m/s |  | 3.98 | m/s | 14.6144 | 0.0090717 | 16.8062 |  | -1 | 259 | 0.259 | 64.8889 | 7.4695 | 5.9642 | 0.02571 | 43.804 | 0.59127
2025-05-20 00:54 | 1752 | Remove | 2025-05-20 | 0:54 | ST | GS | - | 107 | g | 0 | 114.7 | 11.112 | 1087.8 | 1671 | 14:37 | 28.3 | 2.3 m/s | 26.1 | 29.4 | 4.06 m/s | 20.2 |  | 2.3 | m/s |  | 4.06 | m/s | 14.6228 | 0.009065 | 16.8153 |  | -1 | 259 | 0.259 | 64.9239 | 7.2205 | 5.9348 | 0.024429 | 43.8284 | 0.59094
2025-05-20 00:55 | 1753 | Remove | 2025-05-20 | 0:55 | ST | GS | - | 110 | g | 0 | 114.8 | 11.116 | 1088.9 | 1680 | 14:38 | 28.3 | 2.33 m/s | 25.6 | 29.4 | 3.94 m/s | 19.4 |  | 2.33 | m/s |  | 3.94 | m/s | 14.6311 | 0.0090742 | 16.8244 |  | 3 | 262 | 0.262 | 64.2152 | 7.0822 | 5.6998 | 0.024273 | 43.8527 | 0.59746
2025-05-20 00:55 | 1754 | Remove | 2025-05-20 | 0:55 | ST | GS | - | 108.5 | g | 0 | 114.7 | 11.116 | 1087.5 | 1689 | 14:38 | 28.3 | 2.31 m/s | 25.3 | 29.4 | 4.01 m/s | 19.3 |  | 2.31 | m/s |  | 4.01 | m/s | 14.6394 | 0.0090625 | 16.8334 |  | -1.5 | 262 | 0.262 | 64.2498 | 6.9992 | 5.6704 | 0.023783 | 43.8764 | 0.59713
2025-05-20 00:56 | 1755 | Remove | 2025-05-20 | 0:56 | ST | GS | - | 108 | g | 0 | 114.7 | 11.108 | 1087.4 | 1699 | 14:39 | 28.2 | 2.2 m/s | 26.7 | 29.4 | 4.15 m/s | 20.1 |  | 2.2 | m/s |  | 4.15 | m/s | 14.6478 | 0.0090617 | 16.8425 |  | -0.5 | 262 | 0.262 | 64.2843 | 7.346 | 5.9055 | 0.023773 | 43.9002 | 0.59681
2025-05-20 00:56 | 1756 | Remove | 2025-05-20 | 0:56 | ST | GS | - | 107.5 | g | 0 | 114.7 | 11.096 | 1086.1 | 1708 | 14:39 | 28.3 | 2.25 m/s | 25.9 | 29.4 | 3.98 m/s | 20 |  | 2.25 | m/s |  | 3.98 | m/s | 14.6561 | 0.0090508 | 16.8515 |  | -0.5 | 262 | 0.262 | 64.3189 | 7.1652 | 5.8761 | 0.023714 | 43.9239 | 0.59649
2025-05-20 00:57 | 1757 | Remove | 2025-05-20 | 0:57 | ST | GS | - | 108 | g | 0 | 114.8 | 11.1 | 1085.6 | 1717 | 14:40 | 28.2 | 2.18 m/s | 26.1 | 29.4 | 4.07 m/s | 20.2 |  | 2.18 | m/s |  | 4.07 | m/s | 14.6647 | 0.0090467 | 16.8606 |  | 0.5 | 262.5 | 0.2625 | 64.2308 | 7.1809 | 5.9348 | 0.023027 | 43.947 | 0.59731
2025-05-20 00:57 | 1758 | Remove | 2025-05-20 | 0:57 | ST | GS | - | 109 | g | 0 | 114.8 | 11.117 | 1087.8 | 1726 | 14:40 | 28.2 | 2.33 m/s | 25.6 | 29.4 | 3.97 m/s | 19.5 |  | 2.33 | m/s |  | 3.97 | m/s | 14.6731 | 0.009065 | 16.8697 |  | 1 | 263.5 | 0.2635 | 64.0215 | 7.0434 | 5.7292 | 0.02414 | 43.9711 | 0.59926
2025-05-20 00:58 | 1759 | Remove | 2025-05-20 | 0:58 | US | GS | - | 114 | g | 0 | 114.8 | 11.117 | 1088.1 | 1735 | 14:41 | 28.2 | 2.33 m/s | 26.9 | 29.4 | 4.04 m/s | 20.5 |  | 2.33 | m/s |  | 4.04 | m/s | 14.6814 | 0.0090675 | 16.8787 |  | 5 | 268.5 | 0.2685 | 62.863 | 7.4011 | 6.023 | 0.025366 | 43.9965 | 0.61028
2025-05-20 00:58 | 1760 | Remove | 2025-05-20 | 0:58 | US | GS | - | 108.5 | g | 0 | 114.8 | 11.096 | 1084.6 | 1744 | 14:41 | 28.2 | 2.19 m/s | 26.1 | 29.4 | 4.09 m/s | 20.1 |  | 2.19 | m/s |  | 4.09 | m/s | 14.6897 | 0.0090383 | 16.8878 |  | -5.5 | 268.5 | 0.2685 | 62.8967 | 7.1809 | 5.9055 | 0.023133 | 44.0196 | 0.60996
2025-05-20 00:59 | 1761 | Remove | 2025-05-20 | 0:59 | ST | GS | - | 110 | g | 0 | 114.8 | 11.102 | 1086 | 1753 | 14:42 | 28.2 | 2.34 m/s | 26.6 | 29.4 | 4.06 m/s | 20.4 |  | 2.34 | m/s |  | 4.06 | m/s | 14.6981 | 0.00905 | 16.8968 |  | 1.5 | 270 | 0.27 | 62.5808 | 7.3185 | 5.9936 | 0.025191 | 44.0448 | 0.61301
2025-05-20 00:59 | 1762 | Remove | 2025-05-20 | 0:59 | ST | GS | - | 108.5 | g | 0 | 114.8 | 11.088 | 1083.7 | 1762 | 14:42 | 28.2 | 2.25 m/s | 25.9 | 29.4 | 4.13 m/s | 19.7 |  | 2.25 | m/s |  | 4.13 | m/s | 14.7064 | 0.0090308 | 16.9058 |  | -1.5 | 270 | 0.27 | 62.6142 | 7.1259 | 5.7879 | 0.023584 | 44.0684 | 0.61268
2025-05-20 01:00 | 1763 | Remove | 2025-05-20 | 1:00 | ST | GS | - | 109 | g | 0 | 114.8 | 11.092 | 1085.1 | 1771 | 14:43 | 28.2 | 2.26 m/s | 25.8 | 29.4 | 4.09 m/s | 19.6 |  | 2.26 | m/s |  | 4.09 | m/s | 14.7147 | 0.0090425 | 16.9149 |  | 0.5 | 270.5 | 0.2705 | 62.5319 | 7.0984 | 5.7586 | 0.023598 | 44.092 | 0.61349
2025-05-20 01:00 | 1764 | Remove | 2025-05-20 | 1:00 | ST | GS | - | 108.5 | g | 0 | 114.7 | 11.091 | 1084.9 | 1780 | 14:43 | 28.2 | 2.25 m/s | 26.4 | 29.4 | 4.01 m/s | 20.2 |  | 2.25 | m/s |  | 4.01 | m/s | 14.7231 | 0.0090408 | 16.9239 |  | -0.5 | 270.5 | 0.2705 | 62.5654 | 7.2635 | 5.9348 | 0.02404 | 44.116 | 0.61316
2025-05-20 01:01 | 1765 | Remove | 2025-05-20 | 1:01 | ST | GS | - | 109.5 | g | 0 | 115.2 | 11.101 | 1084.8 | 1789 | 14:44 | 28.2 | 2.38 m/s | 26.3 | 29.4 | 4.1 m/s | 20.2 |  | 2.38 | m/s |  | 4.1 | m/s | 14.7314 | 0.00904 | 16.933 |  | 1 | 271.5 | 0.2715 | 62.3682 | 7.236 | 5.9348 | 0.025332 | 44.1413 | 0.61507
2025-05-20 01:01 | 1766 | Remove | 2025-05-20 | 1:01 | US | GS | - | 112.5 | g | 0 | 115.2 | 11.099 | 1085 | 1798 | 14:44 | 28.2 | 2.2 m/s | 26.8 | 29.4 | 4.13 m/s | 20.2 |  | 2.2 | m/s |  | 4.13 | m/s | 14.7397 | 0.0090417 | 16.942 |  | 3 | 274.5 | 0.2745 | 61.7195 | 7.3735 | 5.9348 | 0.023862 | 44.1652 | 0.62153
2025-05-20 01:02 | 1767 | Remove | 2025-05-20 | 1:02 | ST | GS | - | 108.5 | g | 0 | 115.1 | 11.083 | 1083.1 | 1808 | 14:45 | 28.2 | 2.27 m/s | 26.1 | 29.4 | 4.06 m/s | 20.2 |  | 2.27 | m/s |  | 4.06 | m/s | 14.7481 | 0.0090258 | 16.951 |  | -4 | 274.5 | 0.2745 | 61.7524 | 7.1809 | 5.9348 | 0.023978 | 44.1892 | 0.62119
2025-05-20 01:02 | 1768 | Remove | 2025-05-20 | 1:02 | ST | GS | - | 110.5 | g | 0 | 115.1 | 11.071 | 1081.5 | 1817 | 14:45 | 28.2 | 2.25 m/s | 27.9 | 29.4 | 4.09 m/s | 21.1 |  | 2.25 | m/s |  | 4.09 | m/s | 14.7564 | 0.0090125 | 16.9601 |  | 2 | 276.5 | 0.2765 | 61.3383 | 7.6762 | 6.1993 | 0.025406 | 44.2146 | 0.62536
2025-05-20 01:03 | 1769 | Remove | 2025-05-20 | 1:03 | ST | GS | - | 110 | g | 0 | 115.1 | 11.076 | 1082.6 | 1825 | 14:46 | 28.2 | 2.26 m/s | 26.5 | 29.3 | 4.09 m/s | 20.2 |  | 2.26 | m/s |  | 4.09 | m/s | 14.7647 | 0.0090217 | 16.9691 |  | -0.5 | 276.5 | 0.2765 | 61.371 | 7.291 | 5.9026 | 0.024238 | 44.2388 | 0.62502
2025-05-20 01:03 | 1770 | Remove | 2025-05-20 | 1:03 | ST | GS | - | 109.5 | g | 0 | 115.1 | 11.078 | 1082.6 | 1835 | 14:46 | 28.2 | 2.25 m/s | 25.9 | 29.3 | 4.07 m/s | 19.8 |  | 2.25 | m/s |  | 4.07 | m/s | 14.7731 | 0.0090217 | 16.9781 |  | -0.5 | 276.5 | 0.2765 | 61.4036 | 7.1259 | 5.7857 | 0.023584 | 44.2624 | 0.62468
2025-05-20 01:04 | 1771 | Keep | 2025-05-20 | 1:04 | ST | GS | - | 111 | g | 0 | 115.1 | 11.078 | 1082.6 | 1844 | 14:47 | 28.2 | 2.33 m/s | 26.7 | 29.3 | 4.0 m/s | 20.6 |  | 2.33 | m/s |  | 4 | m/s | 14.7814 | 0.0090217 | 16.9871 |  | 1.5 | 278 | 0.278 | 61.1047 | 7.346 | 6.0195 | 0.025177 | 44.2876 | 0.62772
2025-05-20 01:04 | 1772 | Remove | 2025-05-20 | 1:04 | ST | GS | - | 108.5 | g | 0 | 115.1 | 11.072 | 1081.9 | 1853 | 14:47 | 28.2 | 2.25 m/s | 26.1 | 29.3 | 4.06 m/s | 20.2 |  | 2.25 | m/s |  | 4.06 | m/s | 14.7897 | 0.0090158 | 16.9961 |  | -2.5 | 278 | 0.278 | 61.1372 | 7.1809 | 5.9026 | 0.023767 | 44.3114 | 0.62738
2025-05-20 01:05 | 1773 | Remove | 2025-05-20 | 1:05 | ST | GS | - | 109 | g | 0 | 115 | 11.065 | 1081.4 | 1862 | 14:48 | 28.2 | 2.19 m/s | 27.7 | 29.3 | 4.18 m/s | 21.7 |  | 2.19 | m/s |  | 4.18 | m/s | 14.7981 | 0.0090117 | 17.0051 |  | 0.5 | 278.5 | 0.2785 | 61.0598 | 7.6212 | 6.3409 | 0.024551 | 44.3359 | 0.62816
2025-05-20 01:05 | 1774 | Remove | 2025-05-20 | 1:05 | US | GS | - | 111 | g | 0 | 115 | 11.063 | 1080.9 | 1871 | 14:48 | 28.2 | 2.31 m/s | 28.3 | 29.3 | 4.04 m/s | 20.2 |  | 2.31 | m/s |  | 4.04 | m/s | 14.8067 | 0.0090075 | 17.0142 |  | 2 | 280.5 | 0.2805 | 60.6565 | 7.7862 | 5.9026 | 0.026457 | 44.3624 | 0.63229
2025-05-20 01:06 | 1775 | Remove | 2025-05-20 | 1:06 | ST | GS | - | 111.5 | g | 0 | 115 | 11.071 | 1081.9 | 1880 | 14:49 | 28.2 | 2.35 m/s | 26.4 | 29.3 | 4.0 m/s | 20.3 |  | 2.35 | m/s |  | 4 | m/s | 14.815 | 0.0090158 | 17.0232 |  | 0.5 | 281 | 0.281 | 60.5807 | 7.2635 | 5.9318 | 0.025108 | 44.3875 | 0.63306
2025-05-20 01:06 | 1776 | Remove | 2025-05-20 | 1:06 | ST | GS | - | 110 | g | 0 | 114.9 | 11.079 | 1082.9 | 1889 | 14:49 | 28.2 | 2.31 m/s | 26.1 | 29.3 | 4.04 m/s | 19.8 |  | 2.31 | m/s |  | 4.04 | m/s | 14.8233 | 0.0090242 | 17.0322 |  | -1.5 | 281 | 0.281 | 60.6128 | 7.1809 | 5.7857 | 0.0244 | 44.4119 | 0.63271
2025-05-20 01:07 | 1777 | Remove | 2025-05-20 | 1:07 | ST | GS | - | 112.5 | g | 0 | 115 | 11.065 | 1081.6 | 1898 | 14:50 | 28.2 | 2.23 m/s | 27.9 | 29.3 | 4.13 m/s | 20.6 |  | 2.23 | m/s |  | 4.13 | m/s | 14.8317 | 0.0090133 | 17.0412 |  | 2.5 | 283.5 | 0.2835 | 60.1101 | 7.6762 | 6.0195 | 0.02518 | 44.4371 | 0.63798
2025-05-20 01:07 | 1778 | Remove | 2025-05-20 | 1:07 | ST | GS | - | 110 | g | 0 | 114.9 | 11.054 | 1079.6 | 1907 | 14:50 | 28.1 | 2.26 m/s | 28.2 | 29.3 | 4.16 m/s | 21.3 |  | 2.26 | m/s |  | 4.16 | m/s | 14.84 | 0.0089967 | 17.0502 |  | -2.5 | 283.5 | 0.2835 | 60.1418 | 7.7162 | 6.224 | 0.025652 | 44.4627 | 0.63761
2025-05-20 01:08 | 1779 | Remove | 2025-05-20 | 1:08 | US | GS | - | 110.5 | g | 0 | 115 | 11.06 | 1080.3 | 1916 | 14:51 | 28.1 | 2.23 m/s | 27.6 | 29.3 | 4.06 m/s | 20.8 |  | 2.23 | m/s |  | 4.06 | m/s | 14.8483 | 0.0090025 | 17.0592 |  | 0.5 | 284 | 0.284 | 60.0676 | 7.552 | 6.0779 | 0.024772 | 44.4875 | 0.63838
2025-05-20 01:08 | 1780 | Remove | 2025-05-20 | 1:08 | ST | GS | - | 110 | g | 0 | 114.9 | 11.068 | 1081.6 | 1925 | 14:51 | 28.1 | 2.37 m/s | 27.5 | 29.3 | 4.03 m/s | 21 |  | 2.37 | m/s |  | 4.03 | m/s | 14.8567 | 0.0090133 | 17.0682 |  | -0.5 | 284 | 0.284 | 60.0994 | 7.5246 | 6.1363 | 0.026232 | 44.5137 | 0.63801
2025-05-20 01:09 | 1781 | Remove | 2025-05-20 | 1:09 | ST | GS | - | 112 | g | 0 | 115 | 11.065 | 1081.4 | 1934 | 14:52 | 28.1 | 2.44 m/s | 27.5 | 29.3 | 3.98 m/s | 21.2 |  | 2.44 | m/s |  | 3.98 | m/s | 14.865 | 0.0090117 | 17.0772 |  | 2 | 286 | 0.286 | 59.7106 | 7.5246 | 6.1948 | 0.027007 | 44.5407 | 0.64211
2025-05-20 01:09 | 1782 | Remove | 2025-05-20 | 1:09 | ST | GS | - | 109 | g | 0 | 114.9 | 11.051 | 1079.8 | 1943 | 14:52 | 28.1 | 2.3 m/s | 26.2 | 29.3 | 4.09 m/s | 20 |  | 2.3 | m/s |  | 4.09 | m/s | 14.8733 | 0.0089983 | 17.0862 |  | -3 | 286 | 0.286 | 59.742 | 7.1689 | 5.8441 | 0.024254 | 44.565 | 0.64176
2025-05-20 01:10 | 1783 | Remove | 2025-05-20 | 1:10 | ST | GS | - | 110 | g | 0 | 114.9 | 11.056 | 1079.9 | 1952 | 14:53 | 28.1 | 2.33 m/s | 26.4 | 29.3 | 3.98 m/s | 20.1 |  | 2.33 | m/s |  | 3.98 | m/s | 14.8817 | 0.0089992 | 17.0952 |  | 1 | 287 | 0.287 | 59.5652 | 7.2237 | 5.8734 | 0.024758 | 44.5897 | 0.64365
2025-05-20 01:10 | 1784 | Remove | 2025-05-20 | 1:10 | ST | GS | - | 110 | g | 0 | 115 | 11.038 | 1077.5 | 1961 | 14:53 | 28.1 | 2.19 m/s | 28.1 | 29.3 | 4.09 m/s | 21.4 |  | 2.19 | m/s |  | 4.09 | m/s | 14.89 | 0.0089792 | 17.1042 |  | 0 | 287 | 0.287 | 59.5965 | 7.6888 | 6.2532 | 0.024769 | 44.6145 | 0.64329
2025-05-20 01:11 | 1785 | Remove | 2025-05-20 | 1:11 | ST | GS | - | 109.5 | g | 0 | 115 | 11.048 | 1078.6 | 1970 | 14:54 | 28.1 | 2.3 m/s | 29.8 | 29.3 | 4.07 m/s | 23.1 |  | 2.3 | m/s |  | 4.07 | m/s | 14.8983 | 0.0089883 | 17.1132 |  | -0.5 | 287 | 0.287 | 59.6278 | 8.154 | 6.75 | 0.027587 | 44.6421 | 0.64289
2025-05-20 01:11 | 1786 | Remove | 2025-05-20 | 1:11 | US | GS | - | 110 | g | 0 | 115 | 11.033 | 1076.4 | 1979 | 14:54 | 28.1 | 2.19 m/s | 28.1 | 29.3 | 4.09 m/s | 21.1 |  | 2.19 | m/s |  | 4.09 | m/s | 14.9069 | 0.00897 | 17.1222 |  | 0.5 | 287.5 | 0.2875 | 59.5553 | 7.6888 | 6.1656 | 0.024769 | 44.6669 | 0.64365
2025-05-20 01:12 | 1787 | Remove | 2025-05-20 | 1:12 | US | GS | - | 111 | g | 0 | 115 | 11.044 | 1078.4 | 1988 | 14:55 | 28.1 | 2.19 m/s | 27.3 | 29.3 | 4.06 m/s | 20.8 |  | 2.19 | m/s |  | 4.06 | m/s | 14.9153 | 0.0089867 | 17.1311 |  | 1 | 288.5 | 0.2885 | 59.3801 | 7.4699 | 6.0779 | 0.024064 | 44.6909 | 0.64555
2025-05-20 01:12 | 1788 | Remove | 2025-05-20 | 1:12 | US | GS | - | 113 | g | 0 | 115 | 11.048 | 1078.7 | 1997 | 14:55 | 28.1 | 2.23 m/s | 26.5 | 29.3 | 4.09 m/s | 20.1 |  | 2.23 | m/s |  | 4.09 | m/s | 14.9236 | 0.0089892 | 17.1401 |  | 2 | 290.5 | 0.2905 | 59.0022 | 7.251 | 5.8734 | 0.023785 | 44.7147 | 0.64967
2025-05-20 01:13 | 1789 | Remove | 2025-05-20 | 1:13 | ST | GS | - | 109.5 | g | 0 | 115.2 | 11.041 | 1077.7 | 2006 | 14:56 | 28.1 | 2.22 m/s | 26.6 | 29.3 | 4.09 m/s | 20.1 |  | 2.22 | m/s |  | 4.09 | m/s | 14.9319 | 0.0089808 | 17.1491 |  | -3.5 | 290.5 | 0.2905 | 59.0331 | 7.2784 | 5.8734 | 0.023768 | 44.7385 | 0.64933
2025-05-20 01:13 | 1790 | Remove | 2025-05-20 | 1:13 | ST | GS | - | 112.5 | g | 0 | 115.1 | 11.047 | 1078.4 | 2015 | 14:56 | 28.1 | 2.4 m/s | 27.6 | 29.3 | 3.94 m/s | 21.1 |  | 2.4 | m/s |  | 3.94 | m/s | 14.9403 | 0.0089867 | 17.1581 |  | 3 | 293.5 | 0.2935 | 58.4603 | 7.552 | 6.1656 | 0.026661 | 44.7651 | 0.65564
2025-05-20 01:14 | 1791 | Remove | 2025-05-20 | 1:14 | ST | GS | - | 111.5 | g | 0 | 115.1 | 11.067 | 1081.2 | 2024 | 14:57 | 28.1 | 2.35 m/s | 26.2 | 29.3 | 3.97 m/s | 20 |  | 2.35 | m/s |  | 3.97 | m/s | 14.9489 | 0.00901 | 17.1671 |  | -1 | 293.5 | 0.2935 | 58.491 | 7.1689 | 5.8441 | 0.024781 | 44.7899 | 0.65528
2025-05-20 01:14 | 1792 | Remove | 2025-05-20 | 1:14 | ST | GS | - | 112 | g | 0 | 115.1 | 11.05 | 1079.1 | 2033 | 14:57 | 28.1 | 2.35 m/s | 27.8 | 29.3 | 4.06 m/s | 21.1 |  | 2.35 | m/s |  | 4.06 | m/s | 14.9572 | 0.0089925 | 17.1761 |  | 0.5 | 294 | 0.294 | 58.4221 | 7.6067 | 6.1656 | 0.026295 | 44.8162 | 0.65601
2025-05-20 01:15 | 1793 | Remove | 2025-05-20 | 1:15 | ST | GS | - | 112.5 | g | 0 | 115.1 | 11.052 | 1079.2 | 2042 | 14:58 | 28.1 | 2.2 m/s | 27.4 | 29.3 | 4.24 m/s | 21 |  | 2.2 | m/s |  | 4.24 | m/s | 14.9656 | 0.0089933 | 17.1851 |  | 0.5 | 294.5 | 0.2945 | 58.3535 | 7.4973 | 6.1363 | 0.024262 | 44.8405 | 0.65677
2025-05-20 01:15 | 1794 | Remove | 2025-05-20 | 1:15 | US | GS | - | 110.5 | g | 0 | 115.1 | 11.073 | 1081 | 2051 | 14:58 | 28.1 | 2.31 m/s | 26.3 | 29.3 | 3.98 m/s | 20 |  | 2.31 | m/s |  | 3.98 | m/s | 14.9739 | 0.0090083 | 17.1941 |  | -2 | 294.5 | 0.2945 | 58.3841 | 7.1963 | 5.8441 | 0.024452 | 44.8649 | 0.65641
2025-05-20 01:16 | 1795 | Remove | 2025-05-20 | 1:16 | ST | GS | - | 110.5 | g | 0 | 115.1 | 11.053 | 1079.5 | 2060 | 14:59 | 28.1 | 2.2 m/s | 26.6 | 29.3 | 4.09 m/s | 20.5 |  | 2.2 | m/s |  | 4.09 | m/s | 14.9822 | 0.0089958 | 17.2031 |  | 0 | 294.5 | 0.2945 | 58.4146 | 7.2784 | 5.9902 | 0.023554 | 44.8885 | 0.65607
2025-05-20 01:16 | 1796 | Remove | 2025-05-20 | 1:16 | ST | GS | - | 111.5 | g | 0 | 115.1 | 11.057 | 1079.8 | 2069 | 14:59 | 28.1 | 2.45 m/s | 26.2 | 29.3 | 3.97 m/s | 20.1 |  | 2.45 | m/s |  | 3.97 | m/s | 14.9906 | 0.0089983 | 17.2121 |  | 1 | 295.5 | 0.2955 | 58.2474 | 7.1689 | 5.8734 | 0.025836 | 44.9143 | 0.65792
2025-05-20 01:17 | 1797 | Remove | 2025-05-20 | 1:17 | ST | GS | - | 111 | g | 0 | 115.1 | 11.053 | 1078.7 | 2078 | 15:00 | 28.1 | 2.22 m/s | 27.2 | 29.3 | 4.12 m/s | 20.5 |  | 2.22 | m/s |  | 4.12 | m/s | 14.9989 | 0.0089892 | 17.2211 |  | -0.5 | 295.5 | 0.2955 | 58.2778 | 7.4426 | 5.9902 | 0.024304 | 44.9386 | 0.65756
2025-05-20 01:17 | 1798 | Remove | 2025-05-20 | 1:17 | ST | GS | - | 113 | g | 0 | 115.1 | 11.062 | 1079.9 | 2087 | 15:00 | 28.1 | 2.38 m/s | 27.2 | 29.3 | 4.03 m/s | 20.9 |  | 2.38 | m/s |  | 4.03 | m/s | 15.0072 | 0.0089992 | 17.2301 |  | 2 | 297.5 | 0.2975 | 57.9163 | 7.4426 | 6.1071 | 0.026056 | 44.9647 | 0.66163
2025-05-20 01:18 | 1799 | Remove | 2025-05-20 | 1:18 | ST | GS | - | 110 | g | 0 | 115.1 | 11.056 | 1080 | 2096 | 15:01 | 28.1 | 2.19 m/s | 26.7 | 29.3 | 4.12 m/s | 20.5 |  | 2.19 | m/s |  | 4.12 | m/s | 15.0156 | 0.009 | 17.2391 |  | -3 | 297.5 | 0.2975 | 57.9465 | 7.3057 | 5.9902 | 0.023535 | 44.9882 | 0.66128
2025-05-20 01:18 | 1800 | Remove | 2025-05-20 | 1:18 | ST | GS | - | 112 | g | 0 | 114.9 | 11.051 | 1079.4 | 2105 | 15:01 | 28.1 | 2.34 m/s | 26.7 | 29.3 | 4.07 m/s | 20.6 |  | 2.34 | m/s |  | 4.07 | m/s | 15.0239 | 0.008995 | 17.2481 |  | 2 | 299.5 | 0.2995 | 57.5896 | 7.3057 | 6.0195 | 0.025147 | 45.0134 | 0.66536
2025-05-20 01:19 | 1801 | Keep | 2025-05-20 | 1:19 | ST | GS | - | 111.5 | g | 0 | 115.1 | 11.048 | 1078.9 | 2115 | 15:02 | 28.1 | 2.26 m/s | 26.8 | 29.3 | 4.04 m/s | 20.7 |  | 2.26 | m/s |  | 4.04 | m/s | 15.0322 | 0.0089908 | 17.2571 |  | -0.5 | 299.5 | 0.2995 | 57.6196 | 7.3331 | 6.0487 | 0.024378 | 45.0377 | 0.665
2025-05-20 01:19 | 1802 | Remove | 2025-05-20 | 1:19 | ST | GS | - | 112 | g | 0 | 115.1 | 11.037 | 1076.7 | 2123 | 15:02 | 28.1 | 2.19 m/s | 28.4 | 29.3 | 4.1 m/s | 22 |  | 2.19 | m/s |  | 4.1 | m/s | 15.0406 | 0.0089725 | 17.2661 |  | 0.5 | 300 | 0.3 | 57.5535 | 7.7709 | 6.4286 | 0.025033 | 45.0628 | 0.66574
2025-05-20 01:20 | 1803 | Remove | 2025-05-20 | 1:20 | ST | GS | - | 110.5 | g | 0 | 115.2 | 11.028 | 1075.4 | 2132 | 15:03 | 28.1 | 2.18 m/s | 28 | 29.3 | 4.13 m/s | 21.6 |  | 2.18 | m/s |  | 4.13 | m/s | 15.0489 | 0.0089617 | 17.275 |  | -1.5 | 300 | 0.3 | 57.5834 | 7.6615 | 6.3117 | 0.024568 | 45.0873 | 0.66538
2025-05-20 01:20 | 1804 | Remove | 2025-05-20 | 1:20 | ST | GS | - | 110 | g | 0 | 115.2 | 11.009 | 1073.9 | 2141 | 15:03 | 28.1 | 2.15 m/s | 28.3 | 29.3 | 4.23 m/s | 22 |  | 2.15 | m/s |  | 4.23 | m/s | 15.0572 | 0.0089492 | 17.284 |  | -0.5 | 300 | 0.3 | 57.6132 | 7.7435 | 6.4286 | 0.02449 | 45.1118 | 0.66501
2025-05-20 01:21 | 1805 | Remove | 2025-05-20 | 1:21 | ST | GS | - | 110 | g | 0 | 115.1 | 11.022 | 1075.4 | 2150 | 15:04 | 28.1 | 2.19 m/s | 28.9 | 29.3 | 4.15 m/s | 22.1 |  | 2.19 | m/s |  | 4.15 | m/s | 15.0656 | 0.0089617 | 17.2929 |  | 0 | 300 | 0.3 | 57.6431 | 7.9077 | 6.4578 | 0.025474 | 45.1373 | 0.66464
2025-05-20 01:21 | 1806 | Remove | 2025-05-20 | 1:21 | ST | GS | - | 114.5 | g | 0 | 115.1 | 11.022 | 1075.7 | 2159 | 15:04 | 28.1 | 2.4 m/s | 30.4 | 29.3 | 3.96 m/s | 23.4 |  | 2.4 | m/s |  | 3.96 | m/s | 15.0739 | 0.0089642 | 17.3019 |  | 4.5 | 304.5 | 0.3045 | 56.8206 | 8.3181 | 6.8376 | 0.029366 | 45.1667 | 0.67417
2025-05-20 01:22 | 1807 | Remove | 2025-05-20 | 1:22 | US | GS | - | 112 | g | 0 | 115.1 | 11.019 | 1074.8 | 2168 | 15:05 | 28.1 | 2.19 m/s | 29.9 | 29.2 | 4.16 m/s | 22.8 |  | 2.19 | m/s |  | 4.16 | m/s | 15.0822 | 0.0089567 | 17.3108 |  | -2.5 | 304.5 | 0.3045 | 56.8501 | 8.1813 | 6.6261 | 0.026355 | 45.193 | 0.67378
2025-05-20 01:22 | 1808 | Remove | 2025-05-20 | 1:22 | ST | GS | - | 110.5 | g | 0 | 115.2 | 11.016 | 1074.6 | 2177 | 15:05 | 28.1 | 2.33 m/s | 31.3 | 29.3 | 4.01 m/s | 23.8 |  | 2.33 | m/s |  | 4.01 | m/s | 15.0908 | 0.008955 | 17.3198 |  | -1.5 | 304.5 | 0.3045 | 56.8795 | 8.5644 | 6.9545 | 0.029353 | 45.2224 | 0.67334
2025-05-20 01:23 | 1809 | Remove | 2025-05-20 | 1:23 | US | GS | - | 113 | g | 0 | 115 | 11 | 1072.9 | 2186 | 15:06 | 28.1 | 2.27 m/s | 31.7 | 29.2 | 4.0 m/s | 24.1 |  | 2.27 | m/s |  | 4 | m/s | 15.0992 | 0.0089408 | 17.3287 |  | 2.5 | 307 | 0.307 | 56.4454 | 8.6739 | 7.0039 | 0.028963 | 45.2513 | 0.67843
2025-05-20 01:23 | 1810 | Remove | 2025-05-20 | 1:23 | ST | GS | - | 110 | g | 0 | 115.2 | 11.022 | 1074.9 | 2195 | 15:06 | 28.1 | 2.33 m/s | 31.8 | 29.2 | 4.03 m/s | 24.5 |  | 2.33 | m/s |  | 4.03 | m/s | 15.1075 | 0.0089575 | 17.3377 |  | -3 | 307 | 0.307 | 56.4746 | 8.7012 | 7.1201 | 0.029822 | 45.2812 | 0.67799
2025-05-20 01:24 | 1811 | Remove | 2025-05-20 | 1:24 | ST | GS | - | 113 | g | 0 | 115.1 | 11.011 | 1074.1 | 2204 | 15:07 | 28.1 | 2.38 m/s | 32.1 | 29.2 | 3.98 m/s | 24.6 |  | 2.38 | m/s |  | 3.98 | m/s | 15.1158 | 0.0089508 | 17.3466 |  | 3 | 310 | 0.31 | 55.9569 | 8.7833 | 7.1492 | 0.030749 | 45.3119 | 0.68415
2025-05-20 01:24 | 1812 | Remove | 2025-05-20 | 1:24 | ST | GS | - | 116 | g | 0 | 115.2 | 11.03 | 1075.7 | 2213 | 15:07 | 28.1 | 2.41 m/s | 33.5 | 29.2 | 4.03 m/s | 25.7 |  | 2.41 | m/s |  | 4.03 | m/s | 15.1242 | 0.0089642 | 17.3556 |  | 3 | 313 | 0.313 | 55.4492 | 9.1664 | 7.4689 | 0.032495 | 45.3444 | 0.69027
2025-05-20 01:25 | 1813 | Remove | 2025-05-20 | 1:25 | ST | GS | - | 115 | g | 0 | 115.2 | 11.019 | 1074.5 | 2222 | 15:08 | 28.1 | 2.26 m/s | 32.1 | 29.2 | 4.03 m/s | 24.4 |  | 2.26 | m/s |  | 4.03 | m/s | 15.1325 | 0.0089542 | 17.3646 |  | -1 | 313 | 0.313 | 55.4778 | 8.7833 | 7.0911 | 0.029199 | 45.3736 | 0.68983
2025-05-20 01:25 | 1814 | Remove | 2025-05-20 | 1:25 | ST | GS | - | 111.5 | g | 0 | 115.1 | 11.019 | 1075 | 2231 | 15:08 | 28.1 | 2.25 m/s | 31.7 | 29.2 | 4.03 m/s | 24.5 |  | 2.25 | m/s |  | 4.03 | m/s | 15.1408 | 0.0089583 | 17.3735 |  | -3.5 | 313 | 0.313 | 55.5065 | 8.6739 | 7.1201 | 0.028708 | 45.4023 | 0.68939
2025-05-20 01:26 | 1815 | Remove | 2025-05-20 | 1:26 | ST | GS | - | 113.5 | g | 0 | 115.2 | 11.005 | 1072.7 | 2240 | 15:09 | 28.1 | 2.33 m/s | 33.9 | 29.2 | 4.0 m/s | 26.1 |  | 2.33 | m/s |  | 4 | m/s | 15.1492 | 0.0089392 | 17.3825 |  | 2 | 315 | 0.315 | 55.1824 | 9.2758 | 7.5851 | 0.031792 | 45.4341 | 0.69331
2025-05-20 01:26 | 1816 | Remove | 2025-05-20 | 1:26 | US | GS | - | 112 | g | 0 | 115.3 | 11.027 | 1075.6 | 2249 | 15:09 | 28.1 | 2.26 m/s | 31.7 | 29.2 | 4.09 m/s | 24.4 |  | 2.26 | m/s |  | 4.09 | m/s | 15.1575 | 0.0089633 | 17.3914 |  | -1.5 | 315 | 0.315 | 55.2109 | 8.6739 | 7.0911 | 0.028835 | 45.4629 | 0.69287
2025-05-20 01:27 | 1817 | Remove | 2025-05-20 | 1:27 | US | GS | - | 113.5 | g | 0 | 115.2 | 11.023 | 1075.2 | 2258 | 15:10 | 28.1 | 2.48 m/s | 32.6 | 29.2 | 4.0 m/s | 24.8 |  | 2.48 | m/s |  | 4 | m/s | 15.1658 | 0.00896 | 17.4004 |  | 1.5 | 316.5 | 0.3165 | 54.9775 | 8.9201 | 7.2073 | 0.032541 | 45.4955 | 0.69567
2025-05-20 01:27 | 1818 | Remove | 2025-05-20 | 1:27 | US | GS | - | 112 | g | 0 | 115.3 | 11.019 | 1074.5 | 2267 | 15:10 | 28 | 2.42 m/s | 32.6 | 29.2 | 3.96 m/s | 25.2 |  | 2.42 | m/s |  | 3.96 | m/s | 15.1742 | 0.0089542 | 17.4093 |  | -1.5 | 316.5 | 0.3165 | 55.0058 | 8.8712 | 7.3236 | 0.031579 | 45.527 | 0.69519
2025-05-20 01:28 | 1819 | Remove | 2025-05-20 | 1:28 | ST | GS | - | 113 | g | 0 | 115.2 | 11.025 | 1075 | 2276 | 15:11 | 28.1 | 2.35 m/s | 33 | 29.2 | 3.97 m/s | 25.6 |  | 2.35 | m/s |  | 3.97 | m/s | 15.1825 | 0.0089583 | 17.4183 |  | 1 | 317.5 | 0.3175 | 54.8608 | 9.0296 | 7.4398 | 0.031213 | 45.5583 | 0.69691
2025-05-20 01:28 | 1820 | Remove | 2025-05-20 | 1:28 | US | GS | - | 116.5 | g | 0 | 115.2 | 11.013 | 1073.8 | 2285 | 15:11 | 28 | 2.18 m/s | 33.3 | 29.2 | 4.0 m/s | 25.6 |  | 2.18 | m/s |  | 4 | m/s | 15.1908 | 0.0089483 | 17.4272 |  | 3.5 | 321 | 0.321 | 54.2905 | 9.0617 | 7.4398 | 0.029058 | 45.5873 | 0.70414
2025-05-20 01:29 | 1821 | Remove | 2025-05-20 | 1:29 | ST | GS | - | 112 | g | 0 | 115.3 | 11.018 | 1074.7 | 2294 | 15:12 | 28 | 2.26 m/s | 33.6 | 29.2 | 4.12 m/s | 25.8 |  | 2.26 | m/s |  | 4.12 | m/s | 15.1992 | 0.0089558 | 17.4362 |  | -4.5 | 321 | 0.321 | 54.3184 | 9.1433 | 7.4979 | 0.030396 | 45.6177 | 0.70367
2025-05-20 01:29 | 1822 | Remove | 2025-05-20 | 1:29 | US | GS | - | 112.5 | g | 0 | 115.2 | 11.018 | 1074.5 | 2303 | 15:12 | 28 | 2.38 m/s | 33 | 29.2 | 3.97 m/s | 25.5 |  | 2.38 | m/s |  | 3.97 | m/s | 15.2075 | 0.0089542 | 17.4452 |  | 0.5 | 321.5 | 0.3215 | 54.2618 | 8.98 | 7.4108 | 0.031438 | 45.6492 | 0.70428
2025-05-20 01:30 | 1823 | Remove | 2025-05-20 | 1:30 | ST | GS | - | 112.5 | g | 0 | 115.3 | 11.002 | 1072.6 | 2312 | 15:13 | 28 | 2.22 m/s | 33.8 | 29.2 | 4.13 m/s | 25.5 |  | 2.22 | m/s |  | 4.13 | m/s | 15.2158 | 0.0089383 | 17.4541 |  | 0 | 321.5 | 0.3215 | 54.2896 | 9.1977 | 7.4108 | 0.030036 | 45.6792 | 0.70382
2025-05-20 01:30 | 1824 | Remove | 2025-05-20 | 1:30 | US | GS | - | 114.5 | g | 0 | 115.3 | 11.015 | 1073.5 | 2321 | 15:13 | 28 | 2.33 m/s | 33.6 | 29.2 | 4.04 m/s | 25.8 |  | 2.33 | m/s |  | 4.04 | m/s | 15.2242 | 0.0089458 | 17.463 |  | 2 | 323.5 | 0.3235 | 53.9816 | 9.1433 | 7.4979 | 0.031337 | 45.7105 | 0.70771
2025-05-20 01:31 | 1825 | Remove | 2025-05-20 | 1:31 | ST | GS | - | 111.5 | g | 0 | 115.3 | 11.007 | 1073.3 | 2330 | 15:14 | 28 | 2.26 m/s | 33.9 | 29.2 | 4.1 m/s | 26 |  | 2.26 | m/s |  | 4.1 | m/s | 15.2328 | 0.0089442 | 17.472 |  | -3 | 323.5 | 0.3235 | 54.0092 | 9.2249 | 7.5561 | 0.030667 | 45.7412 | 0.70724
2025-05-20 01:31 | 1826 | Remove | 2025-05-20 | 1:31 | ST | GS | - | 112 | g | 0 | 115.2 | 11.005 | 1073.3 | 2339 | 15:14 | 28 | 2.35 m/s | 34 | 29.2 | 4.06 m/s | 26.4 |  | 2.35 | m/s |  | 4.06 | m/s | 15.2411 | 0.0089442 | 17.4809 |  | 0.5 | 324 | 0.324 | 53.9535 | 9.2521 | 7.6723 | 0.031982 | 45.7732 | 0.70784
2025-05-20 01:32 | 1827 | Remove | 2025-05-20 | 1:32 | ST | GS | - | 114 | g | 0 | 115.3 | 11.011 | 1073.1 | 2348 | 15:15 | 28 | 2.31 m/s | 31.8 | 29.2 | 4.03 m/s | 24.3 |  | 2.31 | m/s |  | 4.03 | m/s | 15.2494 | 0.0089425 | 17.4899 |  | 2 | 326 | 0.326 | 53.6499 | 8.6535 | 7.062 | 0.029404 | 45.8026 | 0.71175
2025-05-20 01:32 | 1828 | Remove | 2025-05-20 | 1:32 | ST | GS | - | 114.5 | g | 0 | 115.3 | 10.997 | 1071.9 | 2357 | 15:15 | 28 | 2.47 m/s | 32.2 | 29.2 | 3.97 m/s | 24.5 |  | 2.47 | m/s |  | 3.97 | m/s | 15.2578 | 0.0089325 | 17.4988 |  | 0.5 | 326.5 | 0.3265 | 53.5951 | 8.7623 | 7.1201 | 0.031836 | 45.8344 | 0.71235
2025-05-20 01:33 | 1829 | Remove | 2025-05-20 | 1:33 | ST | GS | - | 111 | g | 0 | 115.3 | 10.994 | 1071.1 | 2366 | 15:16 | 28 | 2.11 m/s | 32.7 | 29.2 | 4.2 m/s | 24.7 |  | 2.11 | m/s |  | 4.2 | m/s | 15.2661 | 0.0089258 | 17.5077 |  | -3.5 | 326.5 | 0.3265 | 53.6225 | 8.8984 | 7.1783 | 0.027618 | 45.862 | 0.71192
2025-05-20 01:33 | 1830 | Remove | 2025-05-20 | 1:33 | ST | GS | - | 112.5 | g | 0 | 115.3 | 11.005 | 1072.5 | 2375 | 15:16 | 28 | 2.23 m/s | 31 | 29.2 | 4.04 m/s | 23.6 |  | 2.23 | m/s |  | 4.04 | m/s | 15.2744 | 0.0089375 | 17.5167 |  | 1.5 | 328 | 0.328 | 53.4045 | 8.4358 | 6.8586 | 0.027671 | 45.8897 | 0.71476
2025-05-20 01:34 | 1831 | Keep | 2025-05-20 | 1:34 | ST | GS | - | 111 | g | 0 | 115.3 | 11.017 | 1074.4 | 2384 | 15:17 | 28 | 2.18 m/s | 32 | 29.2 | 4.1 m/s | 24.3 |  | 2.18 | m/s |  | 4.1 | m/s | 15.2828 | 0.0089533 | 17.5256 |  | -1.5 | 328 | 0.328 | 53.4318 | 8.7079 | 7.062 | 0.027924 | 45.9176 | 0.71432
2025-05-20 01:34 | 1832 | Remove | 2025-05-20 | 1:34 | ST | GS | - | 113.5 | g | 0 | 115.2 | 11.016 | 1074.4 | 2393 | 15:17 | 28 | 2.23 m/s | 29.9 | 29.2 | 4.13 m/s | 22.5 |  | 2.23 | m/s |  | 4.13 | m/s | 15.2911 | 0.0089533 | 17.5346 |  | 2.5 | 330.5 | 0.3305 | 53.0547 | 8.1364 | 6.5389 | 0.02669 | 45.9443 | 0.71935
2025-05-20 01:35 | 1833 | Remove | 2025-05-20 | 1:35 | ST | GS | - | 111 | g | 0 | 115.3 | 10.998 | 1072 | 2402 | 15:18 | 28 | 2.22 m/s | 30.7 | 29.2 | 4.15 m/s | 23.6 |  | 2.22 | m/s |  | 4.15 | m/s | 15.2994 | 0.0089333 | 17.5435 |  | -2.5 | 330.5 | 0.3305 | 53.0817 | 8.3541 | 6.8586 | 0.027281 | 45.9716 | 0.71892
2025-05-20 01:35 | 1834 | Remove | 2025-05-20 | 1:35 | ST | GS | - | 111 | g | 0 | 115.2 | 11.007 | 1073.5 | 2411 | 15:18 | 28 | 2.13 m/s | 28.7 | 29.2 | 4.16 m/s | 21.7 |  | 2.13 | m/s |  | 4.16 | m/s | 15.3078 | 0.0089458 | 17.5525 |  | 0 | 330.5 | 0.3305 | 53.1088 | 7.8099 | 6.3064 | 0.02447 | 45.9961 | 0.71854
2025-05-20 01:36 | 1835 | Remove | 2025-05-20 | 1:36 | US | GS | - | 114.5 | g | 0 | 115.3 | 11.019 | 1074.7 | 2420 | 15:19 | 28 | 2.34 m/s | 28.4 | 29.2 | 4.01 m/s | 21.6 |  | 2.34 | m/s |  | 4.01 | m/s | 15.3161 | 0.0089558 | 17.5614 |  | 3.5 | 334 | 0.334 | 52.5791 | 7.7283 | 6.2773 | 0.026601 | 46.0227 | 0.72573
2025-05-20 01:36 | 1836 | Remove | 2025-05-20 | 1:36 | ST | GS | - | 112 | g | 0 | 115.3 | 11.019 | 1074.6 | 2429 | 15:19 | 28 | 2.2 m/s | 28 | 29.2 | 4.1 m/s | 21.3 |  | 2.2 | m/s |  | 4.1 | m/s | 15.3244 | 0.008955 | 17.5704 |  | -2.5 | 334 | 0.334 | 52.6059 | 7.6194 | 6.1902 | 0.024657 | 46.0473 | 0.72534
2025-05-20 01:37 | 1837 | Remove | 2025-05-20 | 1:37 | ST | GS | - | 113.5 | g | 0 | 115.2 | 11.009 | 1073.2 | 2438 | 15:20 | 28 | 2.26 m/s | 28.4 | 29.2 | 4.07 m/s | 21.7 |  | 2.26 | m/s |  | 4.07 | m/s | 15.3328 | 0.0089433 | 17.5793 |  | 1.5 | 335.5 | 0.3355 | 52.3973 | 7.7283 | 6.3064 | 0.025692 | 46.073 | 0.72819
2025-05-20 01:37 | 1838 | Remove | 2025-05-20 | 1:37 | ST | GS | - | 113.5 | g | 0 | 115.2 | 11.014 | 1073.8 | 2447 | 15:20 | 28 | 2.33 m/s | 28.5 | 29.2 | 4.03 m/s | 21.5 |  | 2.33 | m/s |  | 4.03 | m/s | 15.3411 | 0.0089483 | 17.5883 |  | 0 | 335.5 | 0.3355 | 52.424 | 7.7555 | 6.2483 | 0.026581 | 46.0996 | 0.72777
2025-05-20 01:38 | 1839 | Remove | 2025-05-20 | 1:38 | ST | GS | - | 112 | g | 0 | 115.2 | 11.003 | 1073 | 2456 | 15:21 | 28 | 2.2 m/s | 27.5 | 29.2 | 4.18 m/s | 21 |  | 2.2 | m/s |  | 4.18 | m/s | 15.3494 | 0.0089417 | 17.5972 |  | -1.5 | 335.5 | 0.3355 | 52.4507 | 7.4833 | 6.103 | 0.024217 | 46.1238 | 0.72739
2025-05-20 01:38 | 1840 | Remove | 2025-05-20 | 1:38 | ST | GS | - | 115 | g | 0 | 115.3 | 11.008 | 1073.3 | 2465 | 15:21 | 28 | 2.35 m/s | 28 | 29.2 | 3.97 m/s | 21.5 |  | 2.35 | m/s |  | 3.97 | m/s | 15.3578 | 0.0089442 | 17.6061 |  | 3 | 338.5 | 0.3385 | 52.0122 | 7.6194 | 6.2483 | 0.026339 | 46.1502 | 0.73348
2025-05-20 01:39 | 1841 | Remove | 2025-05-20 | 1:39 | ST | GS | - | 112.5 | g | 0 | 115.3 | 11.016 | 1074.3 | 2473 | 15:22 | 28 | 2.25 m/s | 27.4 | 29.2 | 4.2 m/s | 20.9 |  | 2.25 | m/s |  | 4.2 | m/s | 15.3661 | 0.0089525 | 17.6151 |  | -2.5 | 338.5 | 0.3385 | 52.0387 | 7.4561 | 6.0739 | 0.024677 | 46.1748 | 0.73308
2025-05-20 01:39 | 1842 | Remove | 2025-05-20 | 1:39 | ST | GS | - | 113 | g | 0 | 114.8 | 10.997 | 1072.1 | 2483 | 15:22 | 28 | 2.34 m/s | 27.8 | 29.2 | 4.09 m/s | 21.2 |  | 2.34 | m/s |  | 4.09 | m/s | 15.3747 | 0.0089342 | 17.624 |  | 0.5 | 339 | 0.339 | 51.9883 | 7.565 | 6.1611 | 0.026039 | 46.2009 | 0.73375
2025-05-20 01:40 | 1843 | Remove | 2025-05-20 | 1:40 | ST | GS | - | 113.5 | g | 0 | 114.9 | 10.988 | 1070.7 | 2491 | 15:23 | 28 | 2.22 m/s | 28.5 | 29.2 | 4.07 m/s | 21.8 |  | 2.22 | m/s |  | 4.07 | m/s | 15.3831 | 0.0089225 | 17.633 |  | 0.5 | 339.5 | 0.3395 | 51.938 | 7.7555 | 6.3355 | 0.025326 | 46.2262 | 0.73443
2025-05-20 01:40 | 1844 | Remove | 2025-05-20 | 1:40 | US | GS | - | 114.5 | g | 0 | 114.8 | 10.996 | 1072.2 | 2500 | 15:23 | 28 | 2.35 m/s | 27.8 | 29.2 | 4.01 m/s | 21.1 |  | 2.35 | m/s |  | 4.01 | m/s | 15.3914 | 0.008935 | 17.6419 |  | 1 | 340.5 | 0.3405 | 51.8117 | 7.565 | 6.132 | 0.02615 | 46.2523 | 0.73618
2025-05-20 01:41 | 1845 | Remove | 2025-05-20 | 1:41 | ST | GS | - | 112 | g | 0 | 114.9 | 10.982 | 1070.1 | 2509 | 15:24 | 28 | 2.05 m/s | 28.8 | 29.2 | 4.18 m/s | 22.3 |  | 2.05 | m/s |  | 4.18 | m/s | 15.3997 | 0.0089175 | 17.6508 |  | -2.5 | 340.5 | 0.3405 | 51.8379 | 7.8371 | 6.4808 | 0.023633 | 46.276 | 0.7358
2025-05-20 01:41 | 1846 | Remove | 2025-05-20 | 1:41 | US | GS | - | 114.5 | g | 0 | 115 | 10.995 | 1072 | 2518 | 15:24 | 28 | 2.37 m/s | 27.6 | 29.2 | 3.98 m/s | 21.2 |  | 2.37 | m/s |  | 3.98 | m/s | 15.4081 | 0.0089333 | 17.6597 |  | 2.5 | 343 | 0.343 | 51.4861 | 7.5106 | 6.1611 | 0.026183 | 46.3022 | 0.74079
2025-05-20 01:42 | 1847 | Remove | 2025-05-20 | 1:42 | US | GS | - | 114 | g | 0 | 114.9 | 10.978 | 1069.8 | 2527 | 15:25 | 28 | 2.2 m/s | 28.4 | 29.2 | 4.12 m/s | 21.6 |  | 2.2 | m/s |  | 4.12 | m/s | 15.4164 | 0.008915 | 17.6687 |  | -0.5 | 343 | 0.343 | 51.5121 | 7.7283 | 6.2773 | 0.02501 | 46.3272 | 0.74039
2025-05-20 01:42 | 1848 | Remove | 2025-05-20 | 1:42 | ST | GS | - | 113 | g | 0 | 115 | 10.969 | 1068.8 | 2536 | 15:25 | 28 | 2.22 m/s | 29.6 | 29.2 | 4.1 m/s | 22.9 |  | 2.22 | m/s |  | 4.1 | m/s | 15.4247 | 0.0089067 | 17.6776 |  | -1 | 343 | 0.343 | 51.5381 | 8.0548 | 6.6552 | 0.026303 | 46.3535 | 0.73997
2025-05-20 01:43 | 1849 | Remove | 2025-05-20 | 1:43 | ST | GS | - | 113.5 | g | 0 | 114.9 | 10.989 | 1071.2 | 2545 | 15:26 | 28 | 2.2 m/s | 28.1 | 29.2 | 4.07 m/s | 21.5 |  | 2.2 | m/s |  | 4.07 | m/s | 15.4331 | 0.0089267 | 17.6865 |  | 0.5 | 343.5 | 0.3435 | 51.489 | 7.6466 | 6.2483 | 0.024745 | 46.3782 | 0.74065
2025-05-20 01:43 | 1850 | Remove | 2025-05-20 | 1:43 | ST | GS | - | 113 | g | 0 | 114.9 | 10.957 | 1067.3 | 2554 | 15:26 | 28 | 2.16 m/s | 29.3 | 29.2 | 4.1 m/s | 22.9 |  | 2.16 | m/s |  | 4.1 | m/s | 15.4414 | 0.0088942 | 17.6954 |  | -0.5 | 343.5 | 0.3435 | 51.5149 | 7.9732 | 6.6552 | 0.025333 | 46.4036 | 0.74024
2025-05-20 01:44 | 1851 | Remove | 2025-05-20 | 1:44 | US | GS | - | 114.5 | g | 0 | 114.9 | 10.973 | 1069.3 | 2563 | 15:27 | 28 | 2.2 m/s | 29.6 | 29.1 | 4.04 m/s | 22.9 |  | 2.2 | m/s |  | 4.04 | m/s | 15.4497 | 0.0089108 | 17.7043 |  | 1.5 | 345 | 0.345 | 51.3168 | 8.0548 | 6.6189 | 0.026066 | 46.4296 | 0.74306
2025-05-20 01:44 | 1852 | Remove | 2025-05-20 | 1:44 | ST | GS | - | 114 | g | 0 | 115 | 10.971 | 1068.4 | 2572 | 15:27 | 28 | 2.26 m/s | 30.2 | 29.2 | 4.1 m/s | 23.2 |  | 2.26 | m/s |  | 4.1 | m/s | 15.4581 | 0.0089033 | 17.7132 |  | -0.5 | 345 | 0.345 | 51.3426 | 8.2181 | 6.7423 | 0.02732 | 46.4569 | 0.74262
2025-05-20 01:45 | 1853 | Remove | 2025-05-20 | 1:45 | ST | GS | - | 115.5 | g | 0 | 115 | 10.96 | 1068.2 | 2581 | 15:28 | 28 | 2.26 m/s | 29.1 | 29.2 | 4.04 m/s | 22.6 |  | 2.26 | m/s |  | 4.04 | m/s | 15.4664 | 0.0089017 | 17.7221 |  | 1.5 | 346.5 | 0.3465 | 51.146 | 7.9187 | 6.568 | 0.026325 | 46.4833 | 0.74543
2025-05-20 01:45 | 1854 | Remove | 2025-05-20 | 1:45 | ST | GS | - | 117.5 | g | 0 | 115 | 10.974 | 1069.3 | 2590 | 15:28 | 28 | 2.3 m/s | 28.6 | 29.1 | 4.03 m/s | 22 |  | 2.3 | m/s |  | 4.03 | m/s | 15.4747 | 0.0089108 | 17.731 |  | 2 | 348.5 | 0.3485 | 50.8781 | 7.7827 | 6.3588 | 0.026331 | 46.5096 | 0.74931
2025-05-20 01:46 | 1855 | Remove | 2025-05-20 | 1:46 | ST | GS | - | 115 | g | 0 | 114.9 | 10.96 | 1067.5 | 2599 | 15:29 | 28 | 2.18 m/s | 29.5 | 29.1 | 4.09 m/s | 22.8 |  | 2.18 | m/s |  | 4.09 | m/s | 15.4831 | 0.0088958 | 17.7399 |  | -2.5 | 348.5 | 0.3485 | 50.9036 | 8.0276 | 6.59 | 0.025742 | 46.5353 | 0.74889
2025-05-20 01:46 | 1856 | Remove | 2025-05-20 | 1:46 | ST | GS | - | 116 | g | 0 | 115 | 10.971 | 1068.8 | 2608 | 15:29 | 28 | 2.3 m/s | 29.2 | 29.1 | 4.09 m/s | 22.2 |  | 2.3 | m/s |  | 4.09 | m/s | 15.4914 | 0.0089067 | 17.7488 |  | 1 | 349.5 | 0.3495 | 50.7834 | 7.946 | 6.4166 | 0.026883 | 46.5622 | 0.75061
2025-05-20 01:47 | 1857 | Remove | 2025-05-20 | 1:47 | ST | GS | - | 113 | g | 0 | 114.9 | 10.972 | 1069.2 | 2617 | 15:30 | 28 | 2.19 m/s | 28.3 | 29.1 | 4.04 m/s | 21.9 |  | 2.19 | m/s |  | 4.04 | m/s | 15.4997 | 0.00891 | 17.7577 |  | -3 | 349.5 | 0.3495 | 50.8089 | 7.701 | 6.3299 | 0.024808 | 46.587 | 0.75021
2025-05-20 01:47 | 1858 | Remove | 2025-05-20 | 1:47 | ST | GS | - | 117 | g | 0 | 115 | 10.972 | 1068.4 | 2625 | 15:30 | 28 | 2.22 m/s | 28.1 | 29.1 | 4.07 m/s | 21.5 |  | 2.22 | m/s |  | 4.07 | m/s | 15.5081 | 0.0089033 | 17.7666 |  | 4 | 353.5 | 0.3535 | 50.2592 | 7.6466 | 6.2143 | 0.02497 | 46.612 | 0.75839
2025-05-20 01:48 | 1859 | Remove | 2025-05-20 | 1:48 | ST | GS | - | 113 | g | 0 | 114.9 | 10.942 | 1064.2 | 2634 | 15:31 | 28 | 2.12 m/s | 29.9 | 29.1 | 4.23 m/s | 23.5 |  | 2.12 | m/s |  | 4.23 | m/s | 15.5167 | 0.0088683 | 17.7755 |  | -4 | 353.5 | 0.3535 | 50.2843 | 8.1364 | 6.7924 | 0.025373 | 46.6374 | 0.75798
2025-05-20 01:48 | 1860 | Remove | 2025-05-20 | 1:48 | ST | GS | - | 114 | g | 0 | 114.9 | 10.972 | 1068.7 | 2643 | 15:32 | 28 | 2.19 m/s | 29.1 | 29.1 | 4.07 m/s | 22.5 |  | 2.19 | m/s |  | 4.07 | m/s | 15.525 | 0.0089058 | 17.7844 |  | 1 | 354.5 | 0.3545 | 50.1676 | 7.9187 | 6.5033 | 0.02551 | 46.6629 | 0.7597
2025-05-20 01:49 | 1861 | Keep | 2025-05-20 | 1:49 | ST | GS | - | 114 | g | 0 | 115 | 10.98 | 1069.7 | 2652 | 15:32 | 28 | 2.25 m/s | 28.1 | 29.1 | 4.07 m/s | 21.4 |  | 2.25 | m/s |  | 4.07 | m/s | 15.5333 | 0.0089142 | 17.7933 |  | 0 | 354.5 | 0.3545 | 50.1927 | 7.6466 | 6.1854 | 0.025308 | 46.6882 | 0.75929
2025-05-20 01:49 | 1862 | Remove | 2025-05-20 | 1:49 | ST | GS | - | 113 | g | 0 | 114.9 | 10.96 | 1067.2 | 2661 | 15:32 | 28 | 2.18 m/s | 29.6 | 29.1 | 4.09 m/s | 22.6 |  | 2.18 | m/s |  | 4.09 | m/s | 15.5417 | 0.0088933 | 17.8022 |  | -1 | 354.5 | 0.3545 | 50.2178 | 8.0548 | 6.5322 | 0.025829 | 46.714 | 0.75887
2025-05-20 01:50 | 1863 | Remove | 2025-05-20 | 1:50 | ST | GS | - | 113.5 | g | 0 | 115 | 10.966 | 1068 | 2670 | 15:33 | 28 | 2.19 m/s | 29.8 | 29.1 | 4.1 m/s | 22.9 |  | 2.19 | m/s |  | 4.1 | m/s | 15.55 | 0.0089 | 17.8111 |  | 0.5 | 355 | 0.355 | 50.1721 | 8.1092 | 6.6189 | 0.026123 | 46.7401 | 0.75952
2025-05-20 01:50 | 1864 | Remove | 2025-05-20 | 1:50 | ST | GS | - | 113 | g | 0 | 115 | 10.933 | 1063.6 | 2679 | 15:34 | 28 | 2.11 m/s | 31.3 | 29.1 | 4.23 m/s | 24.3 |  | 2.11 | m/s |  | 4.23 | m/s | 15.5583 | 0.0088633 | 17.82 |  | -0.5 | 355 | 0.355 | 50.1971 | 8.5174 | 7.0236 | 0.026436 | 46.7666 | 0.75909
2025-05-20 01:51 | 1865 | Remove | 2025-05-20 | 1:51 | US | GS | - | 114 | g | 0 | 115 | 10.966 | 1067.4 | 2688 | 15:34 | 28 | 2.34 m/s | 28.9 | 29.1 | 4.16 m/s | 22.1 |  | 2.34 | m/s |  | 4.16 | m/s | 15.5667 | 0.008895 | 17.8289 |  | 1 | 356 | 0.356 | 50.0811 | 7.8643 | 6.3877 | 0.027069 | 46.7937 | 0.76079
2025-05-20 01:51 | 1866 | Remove | 2025-05-20 | 1:51 | US | GS | - | 113.5 | g | 0 | 115 | 10.97 | 1068.2 | 2697 | 15:34 | 28 | 2.22 m/s | 29.2 | 29.1 | 4.06 m/s | 22.5 |  | 2.22 | m/s |  | 4.06 | m/s | 15.575 | 0.0089017 | 17.8378 |  | -0.5 | 356 | 0.356 | 50.1061 | 7.946 | 6.5033 | 0.025948 | 46.8196 | 0.76037
2025-05-20 01:52 | 1867 | Remove | 2025-05-20 | 1:52 | ST | GS | - | 113.5 | g | 0 | 114.9 | 10.968 | 1068.6 | 2706 | 15:35 | 28 | 2.15 m/s | 28.2 | 29.1 | 4.2 m/s | 21.5 |  | 2.15 | m/s |  | 4.2 | m/s | 15.5833 | 0.008905 | 17.8467 |  | 0 | 356 | 0.356 | 50.1311 | 7.6738 | 6.2143 | 0.024269 | 46.8439 | 0.75997
2025-05-20 01:52 | 1868 | Remove | 2025-05-20 | 1:52 | US | GS | - | 116 | g | 0 | 115 | 10.965 | 1067 | 2715 | 15:36 | 28 | 2.23 m/s | 30.1 | 29.1 | 4.13 m/s | 23.3 |  | 2.23 | m/s |  | 4.13 | m/s | 15.5917 | 0.0088917 | 17.8556 |  | 2.5 | 358.5 | 0.3585 | 49.8063 | 8.1909 | 6.7345 | 0.026868 | 46.8707 | 0.76487
2025-05-20 01:53 | 1869 | Remove | 2025-05-20 | 1:53 | ST | GS | - | 113 | g | 0 | 114.9 | 10.967 | 1067.8 | 2724 | 15:36 | 28 | 2.23 m/s | 28.7 | 29.1 | 4.24 m/s | 22.3 |  | 2.23 | m/s |  | 4.24 | m/s | 15.6 | 0.0088983 | 17.8645 |  | -3 | 358.5 | 0.3585 | 49.8311 | 7.8099 | 6.4455 | 0.025618 | 46.8964 | 0.76445
2025-05-20 01:53 | 1870 | Remove | 2025-05-20 | 1:53 | ST | GS | - | 115 | g | 0 | 115 | 10.966 | 1067.9 | 2733 | 15:36 | 28 | 2.16 m/s | 29.2 | 29.1 | 4.09 m/s | 22.5 |  | 2.16 | m/s |  | 4.09 | m/s | 15.6083 | 0.0088992 | 17.8734 |  | 2 | 360.5 | 0.3605 | 49.5794 | 7.946 | 6.5033 | 0.025247 | 46.9216 | 0.7683
2025-05-20 01:54 | 1871 | Remove | 2025-05-20 | 1:54 | ST | GS | - | 113.5 | g | 0 | 114.9 | 10.97 | 1069 | 2742 | 15:37 | 28 | 2.16 m/s | 28 | 29.2 | 4.12 m/s | 21.8 |  | 2.16 | m/s |  | 4.12 | m/s | 15.6167 | 0.0089083 | 17.8823 |  | -1.5 | 360.5 | 0.3605 | 49.6041 | 7.6194 | 6.3355 | 0.024209 | 46.9458 | 0.76791
2025-05-20 01:54 | 1872 | Remove | 2025-05-20 | 1:54 | ST | GS | - | 115.5 | g | 0 | 115 | 10.976 | 1068.9 | 2750 | 15:38 | 28 | 2.19 m/s | 27.6 | 29.2 | 4.2 m/s | 21.2 |  | 2.19 | m/s |  | 4.2 | m/s | 15.625 | 0.0089075 | 17.8912 |  | 2 | 362.5 | 0.3625 | 49.355 | 7.5106 | 6.1611 | 0.024195 | 46.97 | 0.77177
2025-05-20 01:55 | 1873 | Remove | 2025-05-20 | 1:55 | US | GS | - | 113.5 | g | 0 | 115 | 10.959 | 1066.7 | 2759 | 15:38 | 28 | 2.13 m/s | 30 | 29.2 | 4.15 m/s | 23 |  | 2.13 | m/s |  | 4.15 | m/s | 15.6333 | 0.0088892 | 17.9001 |  | -2 | 362.5 | 0.3625 | 49.3795 | 8.1637 | 6.6842 | 0.025578 | 46.9956 | 0.77135
2025-05-20 01:55 | 1874 | Remove | 2025-05-20 | 1:55 | ST | GS | - | 114 | g | 0 | 114.9 | 10.979 | 1069.4 | 2768 | 15:38 | 28 | 2.31 m/s | 27.7 | 29.2 | 4.04 m/s | 21.1 |  | 2.31 | m/s |  | 4.04 | m/s | 15.6417 | 0.0089117 | 17.909 |  | 0.5 | 363 | 0.363 | 49.336 | 7.5378 | 6.132 | 0.025613 | 47.0212 | 0.77199
2025-05-20 01:56 | 1875 | Remove | 2025-05-20 | 1:56 | ST | GS | - | 114.5 | g | 0 | 115 | 10.969 | 1068.5 | 2777 | 15:39 | 28 | 2.2 m/s | 28.1 | 29.2 | 4.06 m/s | 21.5 |  | 2.2 | m/s |  | 4.06 | m/s | 15.65 | 0.0089042 | 17.9179 |  | 0.5 | 363.5 | 0.3635 | 49.2927 | 7.6466 | 6.2483 | 0.024745 | 47.0459 | 0.77265
2025-05-20 01:56 | 1876 | Remove | 2025-05-20 | 1:56 | US | GS | - | 116 | g | 0 | 115 | 10.978 | 1069.4 | 2786 | 15:39 | 28 | 2.33 m/s | 27.7 | 29.2 | 4.1 m/s | 21.3 |  | 2.33 | m/s |  | 4.1 | m/s | 15.6583 | 0.0089117 | 17.9268 |  | 1.5 | 365 | 0.365 | 49.1145 | 7.5378 | 6.1902 | 0.025835 | 47.0718 | 0.77541
2025-05-20 01:57 | 1877 | Remove | 2025-05-20 | 1:57 | ST | GS | - | 115 | g | 0 | 115 | 10.984 | 1069.5 | 2795 | 15:40 | 28 | 2.33 m/s | 27.3 | 29.1 | 4.03 m/s | 21 |  | 2.33 | m/s |  | 4.03 | m/s | 15.6669 | 0.0089125 | 17.9357 |  | -1 | 365 | 0.365 | 49.1389 | 7.4289 | 6.0698 | 0.025462 | 47.0972 | 0.77499
2025-05-20 01:57 | 1878 | Remove | 2025-05-20 | 1:57 | ST | GS | - | 114 | g | 0 | 115 | 10.968 | 1068.5 | 2804 | 15:41 | 28 | 2.12 m/s | 28.7 | 29.2 | 4.1 m/s | 21.6 |  | 2.12 | m/s |  | 4.1 | m/s | 15.6753 | 0.0089042 | 17.9446 |  | -1 | 365 | 0.365 | 49.1633 | 7.8099 | 6.2773 | 0.024355 | 47.1216 | 0.77459
2025-05-20 01:58 | 1879 | Remove | 2025-05-20 | 1:58 | ST | GS | - | 113.5 | g | 0 | 115 | 10.953 | 1065.9 | 2813 | 15:41 | 28 | 2.2 m/s | 29.5 | 29.2 | 4.06 m/s | 22.6 |  | 2.2 | m/s |  | 4.06 | m/s | 15.6836 | 0.0088825 | 17.9535 |  | -0.5 | 365 | 0.365 | 49.1876 | 8.0276 | 6.568 | 0.025978 | 47.1476 | 0.77417
2025-05-20 01:58 | 1880 | Remove | 2025-05-20 | 1:58 | ST | GS | - | 114.5 | g | 0 | 115 | 10.969 | 1068.3 | 2822 | 15:42 | 28 | 2.23 m/s | 28.4 | 29.2 | 4.07 m/s | 21.5 |  | 2.23 | m/s |  | 4.07 | m/s | 15.6919 | 0.0089025 | 17.9624 |  | 1 | 366 | 0.366 | 49.0776 | 7.7283 | 6.2483 | 0.025351 | 47.1729 | 0.77587
2025-05-20 01:59 | 1881 | Remove | 2025-05-20 | 1:59 | ST | GS | - | 114.5 | g | 0 | 115 | 10.983 | 1070 | 2831 | 15:42 | 28 | 2.31 m/s | 27 | 29.1 | 4.04 m/s | 20.6 |  | 2.31 | m/s |  | 4.04 | m/s | 15.7003 | 0.0089167 | 17.9713 |  | 0 | 366 | 0.366 | 49.1019 | 7.3473 | 5.9541 | 0.024966 | 47.1979 | 0.77546
2025-05-20 01:59 | 1882 | Remove | 2025-05-20 | 1:59 | ST | GS | - | 115.5 | g | 0 | 115 | 10.991 | 1070.2 | 2840 | 15:43 | 28 | 2.23 m/s | 27 | 29.1 | 4.04 m/s | 20.7 |  | 2.23 | m/s |  | 4.04 | m/s | 15.7086 | 0.0089183 | 17.9802 |  | 1 | 367 | 0.367 | 48.9924 | 7.3473 | 5.9831 | 0.024101 | 47.222 | 0.77718
2025-05-20 02:00 | 1883 | Remove | 2025-05-20 | 2:00 | US | GS | - | 115.5 | g | 0 | 115 | 10.986 | 1070 | 2849 | 15:43 | 28 | 2.26 m/s | 27.1 | 29.1 | 4.0 m/s | 20.7 |  | 2.26 | m/s |  | 4 | m/s | 15.7169 | 0.0089167 | 17.9891 |  | 0 | 367 | 0.367 | 49.0167 | 7.3745 | 5.9831 | 0.024516 | 47.2465 | 0.77678
2025-05-20 02:00 | 1884 | Remove | 2025-05-20 | 2:00 | ST | GS | - | 114 | g | 0 | 115.1 | 10.955 | 1066 | 2858 | 15:44 | 28 | 2.2 m/s | 30.2 | 29.2 | 4.09 m/s | 23.6 |  | 2.2 | m/s |  | 4.09 | m/s | 15.7253 | 0.0088833 | 17.998 |  | -1.5 | 367 | 0.367 | 49.0409 | 8.2181 | 6.8586 | 0.026595 | 47.2731 | 0.77634
2025-05-20 02:01 | 1885 | Remove | 2025-05-20 | 2:01 | ST | GS | - | 115.5 | g | 0 | 115 | 10.978 | 1069.4 | 2867 | 15:44 | 28 | 2.2 m/s | 27.9 | 29.1 | 4.06 m/s | 21.1 |  | 2.2 | m/s |  | 4.06 | m/s | 15.7336 | 0.0089117 | 18.0069 |  | 1.5 | 368.5 | 0.3685 | 48.8655 | 7.5922 | 6.0987 | 0.024569 | 47.2977 | 0.77911
2025-05-20 02:01 | 1886 | Remove | 2025-05-20 | 2:01 | ST | GS | - | 114.5 | g | 0 | 115 | 10.981 | 1070 | 2875 | 15:45 | 28 | 2.19 m/s | 27.1 | 29.1 | 4.09 m/s | 21 |  | 2.19 | m/s |  | 4.09 | m/s | 15.7419 | 0.0089167 | 18.0159 |  | -1 | 368.5 | 0.3685 | 48.8897 | 7.3745 | 6.0698 | 0.023756 | 47.3214 | 0.77872
2025-05-20 02:02 | 1887 | Remove | 2025-05-20 | 2:02 | ST | GS | - | 114 | g | 0 | 115.1 | 10.979 | 1069.2 | 2884 | 15:45 | 28 | 2.23 m/s | 27.6 | 29.1 | 4.03 m/s | 21.1 |  | 2.23 | m/s |  | 4.03 | m/s | 15.7503 | 0.00891 | 18.0248 |  | -0.5 | 368.5 | 0.3685 | 48.9139 | 7.5106 | 6.0987 | 0.024637 | 47.3461 | 0.77831
2025-05-20 02:02 | 1888 | Remove | 2025-05-20 | 2:02 | ST | GS | - | 114 | g | 0 | 115 | 10.959 | 1066.8 | 2893 | 15:46 | 28 | 2.2 m/s | 28.9 | 29.1 | 4.21 m/s | 22.3 |  | 2.2 | m/s |  | 4.21 | m/s | 15.7586 | 0.00889 | 18.0337 |  | 0 | 368.5 | 0.3685 | 48.938 | 7.8643 | 6.4455 | 0.02545 | 47.3715 | 0.77789
2025-05-20 02:03 | 1889 | Remove | 2025-05-20 | 2:03 | ST | GS | - | 114 | g | 0 | 115.1 | 10.965 | 1068 | 2902 | 15:46 | 28 | 2.25 m/s | 28.8 | 29.1 | 4.04 m/s | 22.2 |  | 2.25 | m/s |  | 4.04 | m/s | 15.7669 | 0.0089 | 18.0426 |  | 0 | 368.5 | 0.3685 | 48.9622 | 7.8371 | 6.4166 | 0.025938 | 47.3974 | 0.77747
2025-05-20 02:03 | 1890 | Remove | 2025-05-20 | 2:03 | ST | GS | - | 116.5 | g | 0 | 115.1 | 10.98 | 1069.4 | 2911 | 15:47 | 28 | 2.25 m/s | 28.3 | 29.1 | 4.2 m/s | 21.6 |  | 2.25 | m/s |  | 4.2 | m/s | 15.7753 | 0.0089117 | 18.0515 |  | 2.5 | 371 | 0.371 | 48.6562 | 7.701 | 6.2432 | 0.025488 | 47.4229 | 0.78232
2025-05-20 02:04 | 1891 | Keep | 2025-05-20 | 2:04 | ST | GS | - | 114 | g | 0 | 115.1 | 10.976 | 1068.6 | 2920 | 15:47 | 28 | 2.22 m/s | 28.4 | 29.2 | 4.07 m/s | 21.6 |  | 2.22 | m/s |  | 4.07 | m/s | 15.7836 | 0.008905 | 18.0604 |  | -2.5 | 371 | 0.371 | 48.6803 | 7.7283 | 6.2773 | 0.025237 | 47.4482 | 0.78191
2025-05-20 02:04 | 1892 | Remove | 2025-05-20 | 2:04 | US | GS | - | 114 | g | 0 | 115.1 | 10.978 | 1068 | 2929 | 15:48 | 28 | 2.27 m/s | 28.3 | 29.2 | 4.07 m/s | 21.6 |  | 2.27 | m/s |  | 4.07 | m/s | 15.7919 | 0.0089 | 18.0693 |  | 0 | 371 | 0.371 | 48.7042 | 7.701 | 6.2773 | 0.025714 | 47.4739 | 0.78148
2025-05-20 02:05 | 1893 | Remove | 2025-05-20 | 2:05 | ST | GS | - | 116.5 | g | 0 | 115.1 | 10.978 | 1068.8 | 2938 | 15:48 | 28 | 2.16 m/s | 28.3 | 29.2 | 4.09 m/s | 21.4 |  | 2.16 | m/s |  | 4.09 | m/s | 15.8003 | 0.0089067 | 18.0782 |  | 2.5 | 373.5 | 0.3735 | 48.4021 | 7.701 | 6.2192 | 0.024468 | 47.4984 | 0.78634
2025-05-20 02:05 | 1894 | Remove | 2025-05-20 | 2:05 | ST | GS | - | 114 | g | 0 | 115.1 | 10.961 | 1066.4 | 2947 | 15:49 | 28 | 2.19 m/s | 29.2 | 29.1 | 4.1 m/s | 22.5 |  | 2.19 | m/s |  | 4.1 | m/s | 15.8089 | 0.0088867 | 18.0871 |  | -2.5 | 373.5 | 0.3735 | 48.4259 | 7.946 | 6.5033 | 0.025597 | 47.524 | 0.78592
2025-05-20 02:06 | 1895 | Remove | 2025-05-20 | 2:06 | ST | GS | - | 115 | g | 0 | 115.1 | 10.974 | 1068.3 | 2956 | 15:49 | 28 | 2.19 m/s | 28.4 | 29.1 | 4.09 m/s | 21.5 |  | 2.19 | m/s |  | 4.09 | m/s | 15.8172 | 0.0089025 | 18.096 |  | 1 | 374.5 | 0.3745 | 48.3203 | 7.7283 | 6.2143 | 0.024896 | 47.5488 | 0.78761
2025-05-20 02:06 | 1896 | Remove | 2025-05-20 | 2:06 | ST | GS | - | 114 | g | 0 | 115.1 | 10.97 | 1068.2 | 2965 | 15:50 | 28 | 2.25 m/s | 28.7 | 29.1 | 4.03 m/s | 22.2 |  | 2.25 | m/s |  | 4.03 | m/s | 15.8256 | 0.0089017 | 18.1049 |  | -1 | 374.5 | 0.3745 | 48.3441 | 7.8099 | 6.4166 | 0.025848 | 47.5747 | 0.78718
2025-05-20 02:07 | 1897 | Remove | 2025-05-20 | 2:07 | ST | GS | - | 116 | g | 0 | 115 | 10.961 | 1067.4 | 2974 | 15:50 | 28 | 2.33 m/s | 29.1 | 29.1 | 4.1 m/s | 22.5 |  | 2.33 | m/s |  | 4.1 | m/s | 15.8339 | 0.008895 | 18.1138 |  | 2 | 376.5 | 0.3765 | 48.1109 | 7.9187 | 6.5033 | 0.02714 | 47.6018 | 0.79094
2025-05-20 02:07 | 1898 | Remove | 2025-05-20 | 2:07 | ST | GS | - | 116 | g | 0 | 115 | 10.971 | 1067.5 | 2983 | 15:51 | 28 | 2.27 m/s | 28.6 | 29.1 | 4.1 m/s | 22.5 |  | 2.27 | m/s |  | 4.1 | m/s | 15.8422 | 0.0088958 | 18.1227 |  | 0 | 376.5 | 0.3765 | 48.1346 | 7.7827 | 6.5033 | 0.025987 | 47.6278 | 0.7905
2025-05-20 02:08 | 1899 | Remove | 2025-05-20 | 2:08 | ST | GS | - | 117 | g | 0 | 115 | 10.971 | 1067.8 | 2992 | 15:51 | 28 | 2.22 m/s | 28.5 | 29.1 | 4.06 m/s | 21.7 |  | 2.22 | m/s |  | 4.06 | m/s | 15.8506 | 0.0088983 | 18.1316 |  | 1 | 377.5 | 0.3775 | 48.0306 | 7.7555 | 6.2721 | 0.025326 | 47.6531 | 0.79218
2025-05-20 02:08 | 1900 | Remove | 2025-05-20 | 2:08 | ST | GS | - | 116 | g | 0 | 115 | 10.971 | 1067.9 | 3001 | 15:52 | 28 | 2.31 m/s | 28.6 | 29.1 | 4.1 m/s | 22.6 |  | 2.31 | m/s |  | 4.1 | m/s | 15.8589 | 0.0088992 | 18.1405 |  | -1 | 377.5 | 0.3775 | 48.0542 | 7.7827 | 6.5322 | 0.026445 | 47.6796 | 0.79174
2025-05-20 02:09 | 1901 | Remove | 2025-05-20 | 2:09 | US | GS | - | 114.5 | g | 0 | 115 | 10.968 | 1068.3 | 3009 | 15:52 | 28 | 2.18 m/s | 28.1 | 29.1 | 4.12 m/s | 21.3 |  | 2.18 | m/s |  | 4.12 | m/s | 15.8672 | 0.0089025 | 18.1494 |  | -1.5 | 377.5 | 0.3775 | 48.0778 | 7.6466 | 6.1565 | 0.02452 | 47.7041 | 0.79134
2025-05-20 02:09 | 1902 | Remove | 2025-05-20 | 2:09 | ST | GS | - | 114 | g | 0 | 115.1 | 10.964 | 1066.3 | 3018 | 15:53 | 28 | 2.26 m/s | 30.2 | 29.1 | 4.07 m/s | 21.6 |  | 2.26 | m/s |  | 4.07 | m/s | 15.8756 | 0.0088858 | 18.1582 |  | -0.5 | 377.5 | 0.3775 | 48.1013 | 8.2181 | 6.2432 | 0.02732 | 47.7314 | 0.79088
2025-05-20 02:10 | 1903 | Remove | 2025-05-20 | 2:10 | ST | GS | - | 115.5 | g | 0 | 115.1 | 10.974 | 1068.3 | 3027 | 15:53 | 28 | 2.23 m/s | 28.6 | 29.1 | 4.06 m/s | 23.1 |  | 2.23 | m/s |  | 4.06 | m/s | 15.8839 | 0.0089025 | 18.1672 |  | 1.5 | 379 | 0.379 | 47.9344 | 7.7827 | 6.6767 | 0.025529 | 47.757 | 0.7936
2025-05-20 02:10 | 1904 | Remove | 2025-05-20 | 2:10 | ST | GS | - | 116 | g | 0 | 115 | 10.984 | 1069.4 | 3036 | 15:54 | 28 | 2.31 m/s | 30.1 | 29.1 | 4.0 m/s | 21.7 |  | 2.31 | m/s |  | 4 | m/s | 15.8922 | 0.0089117 | 18.1761 |  | 0.5 | 379.5 | 0.3795 | 47.8948 | 8.1909 | 6.2721 | 0.027832 | 47.7848 | 0.79419
2025-05-20 02:11 | 1905 | Remove | 2025-05-20 | 2:11 | ST | GS | - | 116 | g | 0 | 115.1 | 10.956 | 1066.3 | 3045 | 15:54 | 28 | 2.16 m/s | 32.4 | 29.1 | 4.13 m/s | 23.3 |  | 2.16 | m/s |  | 4.13 | m/s | 15.9006 | 0.0088858 | 18.1849 |  | 0 | 379.5 | 0.3795 | 47.9182 | 8.8167 | 6.7345 | 0.028013 | 47.8128 | 0.79372
2025-05-20 02:11 | 1906 | Remove | 2025-05-20 | 2:11 | ST | GS | - | 116 | g | 0 | 115.2 | 10.951 | 1066.2 | 3054 | 15:55 | 28 | 2.23 m/s | 31.2 | 29.1 | 4.13 m/s | 25.6 |  | 2.23 | m/s |  | 4.13 | m/s | 15.9089 | 0.008885 | 18.1938 |  | 0 | 379.5 | 0.3795 | 47.9416 | 8.4902 | 7.3993 | 0.02785 | 47.8407 | 0.79326
2025-05-20 02:12 | 1907 | Remove | 2025-05-20 | 2:12 | ST | GS | - | 116.5 | g | 0 | 115.1 | 10.971 | 1068.9 | 3063 | 15:55 | 28 | 2.23 m/s | 29.9 | 29.1 | 4.09 m/s | 23.7 |  | 2.23 | m/s |  | 4.09 | m/s | 15.9172 | 0.0089075 | 18.2027 |  | 0.5 | 380 | 0.38 | 47.9019 | 8.1364 | 6.8502 | 0.02669 | 47.8673 | 0.79386
2025-05-20 02:12 | 1908 | Remove | 2025-05-20 | 2:12 | ST | GS | - | 114.5 | g | 0 | 115.1 | 10.966 | 1067.3 | 3072 | 15:56 | 28 | 2.18 m/s | 31.1 | 29.1 | 4.04 m/s | 23.2 |  | 2.18 | m/s |  | 4.04 | m/s | 15.9256 | 0.0088942 | 18.2116 |  | -2 | 380 | 0.38 | 47.9254 | 8.463 | 6.7056 | 0.027138 | 47.8945 | 0.79341
2025-05-20 02:13 | 1909 | Remove | 2025-05-20 | 2:13 | ST | GS | - | 115.5 | g | 0 | 115.1 | 10.967 | 1067.9 | 3081 | 15:56 | 28 | 2.15 m/s | 31.5 | 29.1 | 4.13 m/s | 24.5 |  | 2.15 | m/s |  | 4.13 | m/s | 15.9339 | 0.0088992 | 18.2205 |  | 1 | 381 | 0.381 | 47.8229 | 8.5718 | 7.0814 | 0.027109 | 47.9216 | 0.79505
2025-05-20 02:13 | 1910 | Remove | 2025-05-20 | 2:13 | ST | GS | - | 115 | g | 0 | 115.2 | 10.974 | 1068.7 | 3090 | 15:57 | 28 | 2.27 m/s | 31 | 29.1 | 4.06 m/s | 24.3 |  | 2.27 | m/s |  | 4.06 | m/s | 15.9422 | 0.0089058 | 18.2294 |  | -0.5 | 381 | 0.381 | 47.8463 | 8.4358 | 7.0236 | 0.028168 | 47.9498 | 0.79458
2025-05-20 02:14 | 1911 | Remove | 2025-05-20 | 2:14 | US | GS | - | 115.5 | g | 0 | 115.1 | 10.961 | 1066.8 | 3099 | 15:57 | 28 | 2.18 m/s | 33.7 | 29.1 | 4.07 m/s | 24 |  | 2.18 | m/s |  | 4.07 | m/s | 15.9508 | 0.00889 | 18.2383 |  | 0.5 | 381.5 | 0.3815 | 47.8069 | 9.1705 | 6.9369 | 0.029407 | 47.9792 | 0.79514
2025-05-20 02:14 | 1912 | Remove | 2025-05-20 | 2:14 | ST | GS | - | 114.5 | g | 0 | 115.2 | 10.945 | 1065.2 | 3108 | 15:58 | 28 | 2.22 m/s | 33.2 | 29.1 | 4.0 m/s | 26.3 |  | 2.22 | m/s |  | 4 | m/s | 15.9592 | 0.0088767 | 18.2472 |  | -1 | 381.5 | 0.3815 | 47.8302 | 9.0344 | 7.6017 | 0.029502 | 48.0087 | 0.79465
2025-05-20 02:15 | 1913 | Remove | 2025-05-20 | 2:15 | US | GS | - | 119 | g | 0 | 115.2 | 10.964 | 1067.4 | 3117 | 15:58 | 28 | 2.25 m/s | 31.7 | 29.1 | 4.1 m/s | 25.9 |  | 2.25 | m/s |  | 4.1 | m/s | 15.9675 | 0.008895 | 18.2561 |  | 4.5 | 386 | 0.386 | 47.2956 | 8.6263 | 7.486 | 0.02855 | 48.0372 | 0.80354
2025-05-20 02:15 | 1914 | Remove | 2025-05-20 | 2:15 | ST | GS | - | 115 | g | 0 | 115.2 | 10.954 | 1065.8 | 3126 | 15:59 | 28 | 2.19 m/s | 33.6 | 29.1 | 4.12 m/s | 24.4 |  | 2.19 | m/s |  | 4.12 | m/s | 15.9758 | 0.0088817 | 18.265 |  | -4 | 386 | 0.386 | 47.3186 | 9.1433 | 7.0525 | 0.029454 | 48.0667 | 0.80305
2025-05-20 02:16 | 1915 | Remove | 2025-05-20 | 2:16 | ST | GS | - | 115.5 | g | 0 | 115.2 | 10.942 | 1064.4 | 3134 | 15:59 | 28 | 2.2 m/s | 33.9 | 29.1 | 4.09 m/s | 26.3 |  | 2.2 | m/s |  | 4.09 | m/s | 15.9842 | 0.00887 | 18.2739 |  | 0.5 | 386.5 | 0.3865 | 47.2803 | 9.2249 | 7.6017 | 0.029853 | 48.0965 | 0.80359
2025-05-20 02:16 | 1916 | Remove | 2025-05-20 | 2:16 | ST | GS | - | 115 | g | 0 | 115.2 | 10.948 | 1065.5 | 3143 | 16:00 | 28 | 2.22 m/s | 33 | 29.1 | 4.07 m/s | 26 |  | 2.22 | m/s |  | 4.07 | m/s | 15.9925 | 0.0088792 | 18.2827 |  | -0.5 | 386.5 | 0.3865 | 47.3033 | 8.98 | 7.5149 | 0.029325 | 48.1259 | 0.8031
2025-05-20 02:17 | 1917 | Remove | 2025-05-20 | 2:17 | ST | GS | - | 116 | g | 0 | 115.1 | 10.955 | 1066.4 | 3152 | 16:00 | 28 | 2.19 m/s | 32.7 | 29.1 | 4.07 m/s | 25.3 |  | 2.19 | m/s |  | 4.07 | m/s | 16.0008 | 0.0088867 | 18.2916 |  | 1 | 387.5 | 0.3875 | 47.2042 | 8.8984 | 7.3126 | 0.028665 | 48.1545 | 0.8047
2025-05-20 02:17 | 1918 | Remove | 2025-05-20 | 2:17 | ST | GS | - | 115.5 | g | 0 | 115.2 | 10.959 | 1066.5 | 3161 | 16:01 | 28 | 2.23 m/s | 33.7 | 29.1 | 4.1 m/s | 25.2 |  | 2.23 | m/s |  | 4.1 | m/s | 16.0092 | 0.0088875 | 18.3005 |  | -0.5 | 387.5 | 0.3875 | 47.2271 | 9.1705 | 7.2837 | 0.030082 | 48.1846 | 0.8042
2025-05-20 02:18 | 1919 | Remove | 2025-05-20 | 2:18 | ST | GS | - | 117.5 | g | 0 | 115.2 | 10.948 | 1065.5 | 3170 | 16:01 | 28 | 2.3 m/s | 34.1 | 29.1 | 4.18 m/s | 25.9 |  | 2.3 | m/s |  | 4.18 | m/s | 16.0175 | 0.0088792 | 18.3094 |  | 2 | 389.5 | 0.3895 | 47.0074 | 9.2794 | 7.486 | 0.031394 | 48.216 | 0.80782
2025-05-20 02:18 | 1920 | Remove | 2025-05-20 | 2:18 | ST | GS | - | 115.5 | g | 0 | 115.1 | 10.963 | 1067.6 | 3179 | 16:02 | 28 | 2.2 m/s | 33 | 29.1 | 4.06 m/s | 26.3 |  | 2.2 | m/s |  | 4.06 | m/s | 16.0258 | 0.0088967 | 18.3183 |  | -2 | 389.5 | 0.3895 | 47.0302 | 8.98 | 7.6017 | 0.02906 | 48.2451 | 0.80734
2025-05-20 02:19 | 1921 | Keep | 2025-05-20 | 2:19 | ST | GS | - | 115 | g | 0 | 115.2 | 10.952 | 1066.4 | 3188 | 16:02 | 28 | 2.31 m/s | 33.8 | 29.1 | 4.15 m/s | 25.6 |  | 2.31 | m/s |  | 4.15 | m/s | 16.0342 | 0.0088867 | 18.3272 |  | -0.5 | 389.5 | 0.3895 | 47.0531 | 9.1977 | 7.3993 | 0.031253 | 48.2763 | 0.80681
2025-05-20 02:19 | 1922 | Remove | 2025-05-20 | 2:19 | ST | GS | - | 114.5 | g | 0 | 115.1 | 10.947 | 1065.5 | 3197 | 16:03 | 27.9 | 2.27 m/s | 32.7 | 29.1 | 4.04 m/s | 25.9 |  | 2.27 | m/s |  | 4.04 | m/s | 16.0425 | 0.0088792 | 18.336 |  | -0.5 | 389.5 | 0.3895 | 47.0759 | 8.8495 | 7.486 | 0.029549 | 48.3059 | 0.80632
2025-05-20 02:20 | 1923 | Remove | 2025-05-20 | 2:20 | ST | GS | - | 116.5 | g | 0 | 115.1 | 10.956 | 1066.6 | 3206 | 16:03 | 28 | 2.44 m/s | 33.5 | 29.1 | 4.03 m/s | 25 |  | 2.44 | m/s |  | 4.03 | m/s | 16.0508 | 0.0088883 | 18.3449 |  | 2 | 391.5 | 0.3915 | 46.8581 | 9.1161 | 7.2259 | 0.032719 | 48.3386 | 0.80991
2025-05-20 02:20 | 1924 | Remove | 2025-05-20 | 2:20 | ST | GS | - | 116 | g | 0 | 115.2 | 10.966 | 1067.5 | 3215 | 16:04 | 28 | 2.34 m/s | 34.5 | 29.1 | 4.01 m/s | 25.7 |  | 2.34 | m/s |  | 4.01 | m/s | 16.0592 | 0.0088958 | 18.3538 |  | -0.5 | 391.5 | 0.3915 | 46.8808 | 9.3882 | 7.4282 | 0.032315 | 48.3709 | 0.80937
2025-05-20 02:21 | 1925 | Remove | 2025-05-20 | 2:21 | ST | GS | - | 116.5 | g | 0 | 115.2 | 10.967 | 1068.4 | 3223 | 16:04 | 28 | 2.31 m/s | 34.2 | 29.1 | 4.12 m/s | 26.4 |  | 2.31 | m/s |  | 4.12 | m/s | 16.0675 | 0.0089033 | 18.3627 |  | 0.5 | 392 | 0.392 | 46.8437 | 9.3066 | 7.6306 | 0.031623 | 48.4025 | 0.80988
2025-05-20 02:21 | 1926 | Remove | 2025-05-20 | 2:21 | ST | GS | - | 116 | g | 0 | 115.1 | 10.963 | 1067.2 | 3232 | 16:05 | 28 | 2.22 m/s | 34.4 | 29.1 | 4.18 m/s | 26.5 |  | 2.22 | m/s |  | 4.18 | m/s | 16.0758 | 0.0088933 | 18.3716 |  | -0.5 | 392 | 0.392 | 46.8664 | 9.361 | 7.6595 | 0.030569 | 48.4331 | 0.80936
2025-05-20 02:22 | 1927 | Remove | 2025-05-20 | 2:22 | US | GS | - | 118 | g | 0 | 115.1 | 10.951 | 1065.6 | 3241 | 16:05 | 28 | 2.31 m/s | 35.8 | 29.1 | 4.09 m/s | 26.6 |  | 2.31 | m/s |  | 4.09 | m/s | 16.0842 | 0.00888 | 18.3805 |  | 2 | 394 | 0.394 | 46.651 | 9.742 | 7.6884 | 0.033102 | 48.4662 | 0.81294
2025-05-20 02:22 | 1928 | Remove | 2025-05-20 | 2:22 | ST | GS | - | 116.5 | g | 0 | 115.2 | 10.971 | 1068.1 | 3250 | 16:06 | 28 | 2.26 m/s | 35.5 | 29.1 | 4.07 m/s | 27.6 |  | 2.26 | m/s |  | 4.07 | m/s | 16.0928 | 0.0089008 | 18.3894 |  | -1.5 | 394 | 0.394 | 46.6736 | 9.6603 | 7.9774 | 0.032115 | 48.4983 | 0.8124
2025-05-20 02:23 | 1929 | Remove | 2025-05-20 | 2:23 | ST | GS | - | 115.5 | g | 0 | 115.1 | 10.96 | 1065.8 | 3259 | 16:06 | 28 | 2.2 m/s | 37.6 | 29.1 | 4.0 m/s | 27.5 |  | 2.2 | m/s |  | 4 | m/s | 16.1011 | 0.0088817 | 18.3983 |  | -1 | 394 | 0.394 | 46.6962 | 10.2318 | 7.9485 | 0.033111 | 48.5314 | 0.81185
2025-05-20 02:23 | 1930 | Remove | 2025-05-20 | 2:23 | ST | GS | - | 115 | g | 0 | 115.1 | 10.97 | 1067.5 | 3268 | 16:07 | 28 | 2.26 m/s | 35 | 29.1 | 4.03 m/s | 28.8 |  | 2.26 | m/s |  | 4.03 | m/s | 16.1094 | 0.0088958 | 18.4072 |  | -0.5 | 394 | 0.394 | 46.7187 | 9.5243 | 8.3242 | 0.031662 | 48.5631 | 0.81132
2025-05-20 02:24 | 1931 | Remove | 2025-05-20 | 2:24 | ST | GS | - | 116 | g | 0 | 115.2 | 10.964 | 1066.9 | 3277 | 16:07 | 28 | 2.22 m/s | 34.3 | 29.1 | 4.13 m/s | 26.8 |  | 2.22 | m/s |  | 4.13 | m/s | 16.1178 | 0.0088908 | 18.4161 |  | 1 | 395 | 0.395 | 46.623 | 9.3338 | 7.7462 | 0.03048 | 48.5936 | 0.81286
2025-05-20 02:24 | 1932 | Remove | 2025-05-20 | 2:24 | ST | GS | - | 116 | g | 0 | 115.1 | 10.96 | 1066.9 | 3286 | 16:08 | 28 | 2.2 m/s | 34.3 | 29.1 | 4.13 m/s | 26.3 |  | 2.2 | m/s |  | 4.13 | m/s | 16.1261 | 0.0088908 | 18.425 |  | 0 | 395 | 0.395 | 46.6455 | 9.3338 | 7.6017 | 0.030205 | 48.6238 | 0.81236
2025-05-20 02:25 | 1933 | Remove | 2025-05-20 | 2:25 | ST | GS | - | 116.5 | g | 0 | 115.2 | 10.976 | 1068.5 | 3295 | 16:08 | 28 | 2.16 m/s | 34.5 | 29.1 | 4.13 m/s | 26.4 |  | 2.16 | m/s |  | 4.13 | m/s | 16.1344 | 0.0089042 | 18.4339 |  | 0.5 | 395.5 | 0.3955 | 46.609 | 9.3882 | 7.6306 | 0.029829 | 48.6536 | 0.81289
2025-05-20 02:25 | 1934 | Remove | 2025-05-20 | 2:25 | ST | GS | - | 117.5 | g | 0 | 115.2 | 10.953 | 1065.4 | 3304 | 16:09 | 28 | 2.26 m/s | 35.4 | 29.1 | 4.2 m/s | 26.5 |  | 2.26 | m/s |  | 4.2 | m/s | 16.1428 | 0.0088783 | 18.4428 |  | 1 | 396.5 | 0.3965 | 46.5139 | 9.6331 | 7.6595 | 0.032024 | 48.6856 | 0.81441
2025-05-20 02:26 | 1935 | Remove | 2025-05-20 | 2:26 | ST | GS | - | 117 | g | 0 | 115.2 | 10.962 | 1067.5 | 3313 | 16:09 | 28 | 2.2 m/s | 34.8 | 29.1 | 4.27 m/s | 27.4 |  | 2.2 | m/s |  | 4.27 | m/s | 16.1511 | 0.0088958 | 18.4516 |  | -0.5 | 396.5 | 0.3965 | 46.5363 | 9.4698 | 7.9196 | 0.030646 | 48.7163 | 0.8139
2025-05-20 02:26 | 1936 | Remove | 2025-05-20 | 2:26 | US | GS | - | 117.5 | g | 0 | 115.2 | 10.971 | 1067.4 | 3322 | 16:10 | 28 | 2.25 m/s | 34.8 | 29.1 | 4.2 m/s | 26.7 |  | 2.25 | m/s |  | 4.2 | m/s | 16.1594 | 0.008895 | 18.4605 |  | 0.5 | 397 | 0.397 | 46.5001 | 9.4698 | 7.7173 | 0.031342 | 48.7476 | 0.8144
2025-05-20 02:27 | 1937 | Remove | 2025-05-20 | 2:27 | ST | GS | - | 115 | g | 0 | 115.3 | 10.961 | 1066.6 | 3330 | 16:10 | 28 | 2.19 m/s | 36.7 | 29.1 | 4.07 m/s | 26.7 |  | 2.19 | m/s |  | 4.07 | m/s | 16.1678 | 0.0088883 | 18.4694 |  | -2.5 | 397 | 0.397 | 46.5225 | 9.9869 | 7.7173 | 0.032172 | 48.7798 | 0.81386
2025-05-20 02:27 | 1938 | Remove | 2025-05-20 | 2:27 | ST | GS | - | 115.5 | g | 0 | 115.3 | 10.942 | 1064.1 | 3339 | 16:11 | 28 | 2.19 m/s | 35.1 | 29.1 | 4.18 m/s | 28.2 |  | 2.19 | m/s |  | 4.18 | m/s | 16.1761 | 0.0088675 | 18.4783 |  | 0.5 | 397.5 | 0.3975 | 46.4863 | 9.5515 | 8.1508 | 0.030769 | 48.8105 | 0.81437
2025-05-20 02:28 | 1939 | Remove | 2025-05-20 | 2:28 | ST | GS | - | 115.5 | g | 0 | 115.3 | 10.945 | 1063.8 | 3348 | 16:11 | 28 | 2.25 m/s | 34.2 | 29.1 | 4.17 m/s | 26.9 |  | 2.25 | m/s |  | 4.17 | m/s | 16.1844 | 0.008865 | 18.4872 |  | 0 | 397.5 | 0.3975 | 46.5086 | 9.3066 | 7.7751 | 0.030802 | 48.8413 | 0.81386
2025-05-20 02:28 | 1940 | Remove | 2025-05-20 | 2:28 | ST | GS | - | 115.5 | g | 0 | 115.3 | 10.967 | 1066.7 | 3357 | 16:12 | 28 | 2.25 m/s | 34.2 | 29.1 | 4.26 m/s | 26.4 |  | 2.25 | m/s |  | 4.26 | m/s | 16.1928 | 0.0088892 | 18.4961 |  | 0 | 397.5 | 0.3975 | 46.5309 | 9.3066 | 7.6306 | 0.030802 | 48.8721 | 0.81335
2025-05-20 02:29 | 1941 | Remove | 2025-05-20 | 2:29 | ST | GS | - | 115.5 | g | 0 | 115.3 | 10.926 | 1062.1 | 3366 | 16:12 | 27.9 | 2.11 m/s | 35.2 | 29.1 | 4.29 m/s | 27.3 |  | 2.11 | m/s |  | 4.29 | m/s | 16.2011 | 0.0088508 | 18.5049 |  | 0 | 397.5 | 0.3975 | 46.5532 | 9.5261 | 7.8907 | 0.029566 | 48.9017 | 0.81285
2025-05-20 02:29 | 1942 | Remove | 2025-05-20 | 2:29 | ST | GS | - | 115.5 | g | 0 | 115.3 | 10.948 | 1064.3 | 3375 | 16:13 | 27.9 | 2.13 m/s | 35.7 | 29.1 | 4.2 m/s | 27.3 |  | 2.13 | m/s |  | 4.2 | m/s | 16.2094 | 0.0088692 | 18.5138 |  | 0 | 397.5 | 0.3975 | 46.5755 | 9.6614 | 7.8907 | 0.030271 | 48.932 | 0.81235
2025-05-20 02:30 | 1943 | Remove | 2025-05-20 | 2:30 | ST | GS | - | 117 | g | 0 | 115.3 | 10.971 | 1067 | 3384 | 16:13 | 27.9 | 2.1 m/s | 34.2 | 29.1 | 4.27 m/s | 26.4 |  | 2.1 | m/s |  | 4.27 | m/s | 16.2178 | 0.0088917 | 18.5227 |  | 1.5 | 399 | 0.399 | 46.4227 | 9.2555 | 7.6306 | 0.02859 | 48.9606 | 0.81494
2025-05-20 02:30 | 1944 | Remove | 2025-05-20 | 2:30 | ST | GS | - | 117 | g | 0 | 115.2 | 10.995 | 1070.9 | 3393 | 16:14 | 27.9 | 2.09 m/s | 34.3 | 29.1 | 4.27 m/s | 26.2 |  | 2.09 | m/s |  | 4.27 | m/s | 16.2261 | 0.0089242 | 18.5316 |  | 0 | 399 | 0.399 | 46.4451 | 9.2825 | 7.5728 | 0.028537 | 48.9891 | 0.81447
2025-05-20 02:31 | 1945 | Remove | 2025-05-20 | 2:31 | ST | GS | - | 124.5 | g | 0 | 115.2 | 11.007 | 1073.2 | 3402 | 16:14 | 28 | 2.09 m/s | 32.7 | 29.2 | 4.32 m/s | 24.6 |  | 2.09 | m/s |  | 4.32 | m/s | 16.2344 | 0.0089433 | 18.5405 |  | 7.5 | 406.5 | 0.4065 | 45.6102 | 8.8984 | 7.1492 | 0.027356 | 49.0165 | 0.82931
2025-05-20 02:31 | 1946 | Remove | 2025-05-20 | 2:31 | ST | GS | - | 119 | g | 0 | 115.2 | 11.012 | 1072.6 | 3411 | 16:15 | 28 | 2.15 m/s | 33.1 | 29.2 | 4.29 m/s | 23.5 |  | 2.15 | m/s |  | 4.29 | m/s | 16.2431 | 0.0089383 | 18.5495 |  | -5.5 | 406.5 | 0.4065 | 45.6322 | 9.0072 | 6.8295 | 0.028486 | 49.045 | 0.82883
2025-05-20 02:32 | 1947 | Remove | 2025-05-20 | 2:32 | US | GS | - | 115.5 | g | 0 | 115.1 | 11.029 | 1075.6 | 3420 | 16:15 | 28 | 2.05 m/s | 33.4 | 29.2 | 4.3 m/s | 23.9 |  | 2.05 | m/s |  | 4.3 | m/s | 16.2514 | 0.0089633 | 18.5584 |  | -3.5 | 406.5 | 0.4065 | 45.6542 | 9.0889 | 6.9458 | 0.027407 | 49.0724 | 0.82837
2025-05-20 02:32 | 1948 | Remove | 2025-05-20 | 2:32 | US | GS | - | 118.5 | g | 0 | 115.2 | 11.026 | 1074.5 | 3429 | 16:16 | 28 | 2.11 m/s | 31.5 | 29.2 | 4.24 m/s | 23.6 |  | 2.11 | m/s |  | 4.24 | m/s | 16.2597 | 0.0089542 | 18.5674 |  | 3 | 409.5 | 0.4095 | 45.3416 | 8.5718 | 6.8586 | 0.026605 | 49.099 | 0.83403
2025-05-20 02:33 | 1949 | Remove | 2025-05-20 | 2:33 | ST | GS | - | 121 | g | 0 | 115.2 | 11.04 | 1077.6 | 3438 | 16:16 | 28 | 2.06 m/s | 31.8 | 29.2 | 4.26 m/s | 22.9 |  | 2.06 | m/s |  | 4.26 | m/s | 16.2681 | 0.00898 | 18.5764 |  | 2.5 | 412 | 0.412 | 45.0883 | 8.6535 | 6.6552 | 0.026222 | 49.1252 | 0.83867
2025-05-20 02:33 | 1950 | Remove | 2025-05-20 | 2:33 | US | GS | - | 123 | g | 0 | 115.2 | 11.028 | 1075.7 | 3447 | 16:17 | 28 | 2.06 m/s | 31.8 | 29.2 | 4.29 m/s | 23 |  | 2.06 | m/s |  | 4.29 | m/s | 16.2764 | 0.0089642 | 18.5853 |  | 2 | 414 | 0.414 | 44.8921 | 8.6535 | 6.6842 | 0.026222 | 49.1514 | 0.8423
2025-05-20 02:34 | 1951 | Keep | 2025-05-20 | 2:34 | US | GS | - | 119 | g | 0 | 115.2 | 11.028 | 1075.7 | 3456 | 16:17 | 28 | 1.98 m/s | 32.7 | 29.3 | 4.24 m/s | 23.3 |  | 1.98 | m/s |  | 4.24 | m/s | 16.2847 | 0.0089642 | 18.5943 |  | -4 | 414 | 0.414 | 44.9138 | 8.8984 | 6.8084 | 0.025917 | 49.1773 | 0.84185
2025-05-20 02:34 | 1952 | Remove | 2025-05-20 | 2:34 | ST | GS | - | 122.5 | g | 0 | 115.2 | 11.042 | 1077 | 3465 | 16:18 | 28 | 2.03 m/s | 31.2 | 29.3 | 4.3 m/s | 22.5 |  | 2.03 | m/s |  | 4.3 | m/s | 16.2931 | 0.008975 | 18.6033 |  | 3.5 | 417.5 | 0.4175 | 44.5587 | 8.4902 | 6.5747 | 0.025352 | 49.2027 | 0.84853
2025-05-20 02:35 | 1953 | Remove | 2025-05-20 | 2:35 | ST | GS | - | 119.5 | g | 0 | 115.2 | 11.024 | 1075.7 | 3474 | 16:18 | 28.1 | 2.02 m/s | 30.2 | 29.3 | 4.3 m/s | 22.1 |  | 2.02 | m/s |  | 4.3 | m/s | 16.3014 | 0.0089642 | 18.6122 |  | -3 | 417.5 | 0.4175 | 44.5802 | 8.2634 | 6.4578 | 0.024554 | 49.2272 | 0.84811
2025-05-20 02:35 | 1954 | Remove | 2025-05-20 | 2:35 | ST | GS | - | 118.5 | g | 0 | 115.2 | 11.036 | 1076.9 | 3483 | 16:19 | 28.1 | 2.05 m/s | 31.7 | 29.3 | 4.29 m/s | 22.8 |  | 2.05 | m/s |  | 4.29 | m/s | 16.3097 | 0.0089742 | 18.6212 |  | -1 | 417.5 | 0.4175 | 44.6017 | 8.6739 | 6.6623 | 0.026156 | 49.2534 | 0.84766
2025-05-20 02:36 | 1955 | Remove | 2025-05-20 | 2:36 | US | GS | - | 121 | g | 0 | 115.2 | 11.025 | 1075.7 | 3492 | 16:19 | 28.1 | 1.91 m/s | 30.1 | 29.3 | 4.3 m/s | 22.3 |  | 1.91 | m/s |  | 4.3 | m/s | 16.3181 | 0.0089642 | 18.6302 |  | 2.5 | 420 | 0.42 | 44.3576 | 8.2361 | 6.5162 | 0.02314 | 49.2765 | 0.85233
2025-05-20 02:36 | 1956 | Remove | 2025-05-20 | 2:36 | US | GS | - | 125.5 | g | 0 | 115.2 | 11.027 | 1075.2 | 3501 | 16:20 | 28.1 | 1.94 m/s | 30.6 | 29.3 | 4.23 m/s | 23.3 |  | 1.94 | m/s |  | 4.23 | m/s | 16.3264 | 0.00896 | 18.6391 |  | 4.5 | 424.5 | 0.4245 | 43.9084 | 8.3729 | 6.8084 | 0.023893 | 49.3004 | 0.86105
2025-05-20 02:37 | 1957 | Remove | 2025-05-20 | 2:37 | US | GS | - | 124.5 | g | 0 | 115.2 | 11.024 | 1075.2 | 3510 | 16:20 | 28.1 | 1.98 m/s | 30.8 | 29.3 | 4.26 m/s | 23.5 |  | 1.98 | m/s |  | 4.26 | m/s | 16.335 | 0.00896 | 18.6481 |  | -1 | 424.5 | 0.4245 | 43.9295 | 8.4276 | 6.8669 | 0.024545 | 49.325 | 0.86062
2025-05-20 02:37 | 1958 | Remove | 2025-05-20 | 2:37 | US | GS | - | 121.5 | g | 0 | 115.2 | 11.027 | 1075.9 | 3519 | 16:21 | 28.1 | 2.0 m/s | 29.5 | 29.3 | 4.26 m/s | 21.6 |  | 2 | m/s |  | 4.26 | m/s | 16.3433 | 0.0089658 | 18.6571 |  | -3 | 424.5 | 0.4245 | 43.9507 | 8.0719 | 6.3117 | 0.023747 | 49.3487 | 0.8602
2025-05-20 02:38 | 1959 | Remove | 2025-05-20 | 2:38 | ST | GS | - | 125 | g | 0 | 115.3 | 10.988 | 1070.4 | 3527 | 16:21 | 28.1 | 1.98 m/s | 30.7 | 29.3 | 4.29 m/s | 22.5 |  | 1.98 | m/s |  | 4.29 | m/s | 16.3517 | 0.00892 | 18.666 |  | 3.5 | 428 | 0.428 | 43.6121 | 8.4002 | 6.5747 | 0.024466 | 49.3732 | 0.86687
2025-05-20 02:38 | 1960 | Remove | 2025-05-20 | 2:38 | ST | GS | - | 124 | g | 0 | 115.2 | 11.012 | 1073.1 | 3537 | 16:22 | 28.1 | 1.81 m/s | 32.8 | 29.3 | 4.33 m/s | 23.7 |  | 1.81 | m/s |  | 4.33 | m/s | 16.36 | 0.0089425 | 18.6749 |  | -1 | 428 | 0.428 | 43.633 | 8.9748 | 6.9253 | 0.023895 | 49.3971 | 0.86645
2025-05-20 02:39 | 1961 | Remove | 2025-05-20 | 2:39 | ST | GS | - | 125 | g | 0 | 115.2 | 11.005 | 1072.4 | 3546 | 16:22 | 28.1 | 1.95 m/s | 29.5 | 29.3 | 4.32 m/s | 21.9 |  | 1.95 | m/s |  | 4.32 | m/s | 16.3683 | 0.0089367 | 18.6839 |  | 1 | 429 | 0.429 | 43.5521 | 8.0719 | 6.3993 | 0.023153 | 49.4202 | 0.86807
2025-05-20 02:39 | 1962 | Remove | 2025-05-20 | 2:39 | ST | GS | - | 126 | g | 0 | 115.2 | 11.009 | 1073.4 | 3554 | 16:23 | 28.1 | 1.86 m/s | 29.9 | 29.3 | 4.29 m/s | 22.5 |  | 1.86 | m/s |  | 4.29 | m/s | 16.3767 | 0.008945 | 18.6928 |  | 1 | 430 | 0.43 | 43.4716 | 8.1813 | 6.5747 | 0.022384 | 49.4426 | 0.8697
2025-05-20 02:40 | 1963 | Remove | 2025-05-20 | 2:40 | US | GS | - | 126.5 | g | 0 | 115.2 | 11.026 | 1075.1 | 3563 | 16:23 | 28.1 | 1.9 m/s | 29.8 | 29.3 | 4.33 m/s | 21.8 |  | 1.9 | m/s |  | 4.33 | m/s | 16.3853 | 0.0089592 | 18.7018 |  | 0.5 | 430.5 | 0.4305 | 43.442 | 8.154 | 6.3701 | 0.022789 | 49.4654 | 0.87031
2025-05-20 02:40 | 1964 | Remove | 2025-05-20 | 2:40 | ST | GS | - | 114.5 | g | 0 | 115.3 | 11.016 | 1074.5 | 3573 | 16:24 | 28.1 | 1.95 m/s | 29.1 | 29.3 | 4.29 m/s | 22.3 |  | 1.95 | m/s |  | 4.29 | m/s | 16.3936 | 0.0089542 | 18.7107 |  | -12 | 430.5 | 0.4305 | 43.4628 | 7.9624 | 6.5162 | 0.022839 | 49.4882 | 0.8699
2025-05-20 02:41 | 1965 | Remove | 2025-05-20 | 2:41 | ST | GS | - | 116.5 | g | 0 | 115.2 | 11.027 | 1075.3 | 3581 | 16:24 | 28.1 | 2.05 m/s | 31 | 29.3 | 4.3 m/s | 22.8 |  | 2.05 | m/s |  | 4.3 | m/s | 16.4019 | 0.0089608 | 18.7197 |  | 2 | 432.5 | 0.4325 | 43.2825 | 8.4823 | 6.6623 | 0.025578 | 49.5138 | 0.87349
2025-05-20 02:41 | 1966 | Remove | 2025-05-20 | 2:41 | ST | GS | - | 122 | g | 0 | 115.2 | 11.018 | 1074.9 | 3590 | 16:25 | 28.1 | 2.05 m/s | 30.2 | 29.3 | 4.26 m/s | 21.3 |  | 2.05 | m/s |  | 4.26 | m/s | 16.4103 | 0.0089575 | 18.7286 |  | 5.5 | 438 | 0.438 | 42.7594 | 8.2634 | 6.224 | 0.024918 | 49.5387 | 0.88416
2025-05-20 02:42 | 1967 | Remove | 2025-05-20 | 2:42 | US | GS | - | 116.5 | g | 0 | 115.2 | 11.056 | 1079.9 | 3600 | 16:25 | 28.1 | 2.09 m/s | 28.2 | 29.3 | 4.32 m/s | 21.1 |  | 2.09 | m/s |  | 4.32 | m/s | 16.4186 | 0.0089992 | 18.7376 |  | -5.5 | 438 | 0.438 | 42.78 | 7.7162 | 6.1656 | 0.023722 | 49.5625 | 0.88373
2025-05-20 02:42 | 1968 | Remove | 2025-05-20 | 2:42 | US | GS | - | 121.5 | g | 0 | 115.1 | 11.075 | 1082.1 | 3608 | 16:26 | 28.1 | 2.01 m/s | 28.6 | 29.3 | 4.27 m/s | 21.7 |  | 2.01 | m/s |  | 4.27 | m/s | 16.4269 | 0.0090175 | 18.7467 |  | 5 | 443 | 0.443 | 42.3175 | 7.8256 | 6.3409 | 0.023138 | 49.5856 | 0.8934
2025-05-20 02:43 | 1969 | Remove | 2025-05-20 | 2:43 | US | GS | - | 117 | g | 0 | 115.2 | 11.052 | 1079.8 | 3617 | 16:26 | 28.1 | 2.02 m/s | 28.8 | 29.3 | 4.32 m/s | 21.4 |  | 2.02 | m/s |  | 4.32 | m/s | 16.4353 | 0.0089983 | 18.7556 |  | -4.5 | 443 | 0.443 | 42.3378 | 7.8804 | 6.2532 | 0.023415 | 49.609 | 0.89298
2025-05-20 02:43 | 1970 | Remove | 2025-05-20 | 2:43 | ST | GS | - | 115 | g | 0 | 115.1 | 11.067 | 1081.7 | 3627 | 16:27 | 28.1 | 1.94 m/s | 31.2 | 29.3 | 4.32 m/s | 22.5 |  | 1.94 | m/s |  | 4.32 | m/s | 16.4436 | 0.0090142 | 18.7647 |  | -2 | 443 | 0.443 | 42.3582 | 8.537 | 6.5747 | 0.024362 | 49.6334 | 0.89254
2025-05-20 02:44 | 1971 | Remove | 2025-05-20 | 2:44 | ST | GS | - | 121.5 | g | 0 | 115.1 | 11.042 | 1077.8 | 3636 | 16:27 | 28.1 | 2.15 m/s | 30.6 | 29.4 | 4.27 m/s | 24.3 |  | 2.15 | m/s |  | 4.27 | m/s | 16.4519 | 0.0089817 | 18.7736 |  | 6.5 | 449.5 | 0.4495 | 41.7656 | 8.3729 | 7.1394 | 0.02648 | 49.6599 | 0.90516
2025-05-20 02:44 | 1972 | Remove | 2025-05-20 | 2:44 | ST | GS | - | 115 | g | 0 | 115.2 | 11.004 | 1073 | 3645 | 16:28 | 28.1 | 2.0 m/s | 30.6 | 29.4 | 4.23 m/s | 22.3 |  | 2 | m/s |  | 4.23 | m/s | 16.4603 | 0.0089417 | 18.7826 |  | -6.5 | 449.5 | 0.4495 | 41.7855 | 8.3729 | 6.5518 | 0.024632 | 49.6845 | 0.90471
2025-05-20 02:45 | 1973 | Remove | 2025-05-20 | 2:45 | ST | GS | - | 118.5 | g | 0 | 115.2 | 11.049 | 1078.9 | 3654 | 16:28 | 28.1 | 2.04 m/s | 29.5 | 29.4 | 4.26 m/s | 22.1 |  | 2.04 | m/s |  | 4.26 | m/s | 16.4686 | 0.0089908 | 18.7916 |  | 3.5 | 453 | 0.453 | 41.4825 | 8.0719 | 6.4931 | 0.024222 | 49.7087 | 0.91131
2025-05-20 02:45 | 1974 | Remove | 2025-05-20 | 2:45 | ST | GS | - | 115.5 | g | 0 | 115.1 | 11.011 | 1074 | 3663 | 16:29 | 28.1 | 2.09 m/s | 30.2 | 29.4 | 4.3 m/s | 22 |  | 2.09 | m/s |  | 4.3 | m/s | 16.4769 | 0.00895 | 18.8005 |  | -3 | 453 | 0.453 | 41.5023 | 8.2634 | 6.4637 | 0.025404 | 49.7341 | 0.91084
2025-05-20 02:46 | 1975 | Remove | 2025-05-20 | 2:46 | ST | GS | - | 117 | g | 0 | 115.1 | 11.072 | 1082 | 3672 | 16:29 | 28.1 | 2.06 m/s | 29.5 | 29.3 | 4.26 m/s | 22.3 |  | 2.06 | m/s |  | 4.26 | m/s | 16.4853 | 0.0090167 | 18.8095 |  | 1.5 | 454.5 | 0.4545 | 41.3851 | 8.0719 | 6.5162 | 0.024459 | 49.7586 | 0.91341
2025-05-20 02:46 | 1976 | Remove | 2025-05-20 | 2:46 | ST | GS | - | 116 | g | 0 | 115.2 | 11.036 | 1076.9 | 3681 | 16:30 | 28.1 | 2.08 m/s | 28.7 | 29.3 | 4.2 m/s | 21.4 |  | 2.08 | m/s |  | 4.2 | m/s | 16.4936 | 0.0089742 | 18.8185 |  | -1 | 454.5 | 0.4545 | 41.4049 | 7.853 | 6.2532 | 0.024027 | 49.7826 | 0.91297
2025-05-20 02:47 | 1977 | Remove | 2025-05-20 | 2:47 | US | GS | - | 117.5 | g | 0 | 115.1 | 11.036 | 1077.3 | 3690 | 16:30 | 28.1 | 2.08 m/s | 29.3 | 29.4 | 4.35 m/s | 21.6 |  | 2.08 | m/s |  | 4.35 | m/s | 16.5019 | 0.0089775 | 18.8275 |  | 1.5 | 456 | 0.456 | 41.2884 | 8.0172 | 6.3462 | 0.024529 | 49.8071 | 0.91553
2025-05-20 02:47 | 1978 | Remove | 2025-05-20 | 2:47 | US | GS | - | 120.5 | g | 0 | 115.2 | 11.052 | 1079.5 | 3699 | 16:31 | 28.1 | 1.94 m/s | 30.3 | 29.4 | 4.26 m/s | 21.5 |  | 1.94 | m/s |  | 4.26 | m/s | 16.5103 | 0.0089958 | 18.8365 |  | 3 | 459 | 0.459 | 41.0381 | 8.2908 | 6.3168 | 0.023659 | 49.8308 | 0.92112
2025-05-20 02:48 | 1979 | Remove | 2025-05-20 | 2:48 | ST | GS | - | 116 | g | 0 | 115.2 | 11.042 | 1078.4 | 3708 | 16:31 | 28.1 | 2.01 m/s | 29.1 | 29.4 | 4.23 m/s | 21.6 |  | 2.01 | m/s |  | 4.23 | m/s | 16.5186 | 0.0089867 | 18.8455 |  | -4.5 | 459 | 0.459 | 41.0577 | 7.9624 | 6.3462 | 0.023542 | 49.8543 | 0.92068
2025-05-20 02:48 | 1980 | Remove | 2025-05-20 | 2:48 | US | GS | - | 118 | g | 0 | 115.1 | 11.043 | 1078.5 | 3717 | 16:32 | 28.1 | 2.11 m/s | 28.5 | 29.4 | 4.29 m/s | 20.7 |  | 2.11 | m/s |  | 4.29 | m/s | 16.5272 | 0.0089875 | 18.8545 |  | 2 | 461 | 0.461 | 40.8991 | 7.7983 | 6.0817 | 0.024204 | 49.8785 | 0.92425
2025-05-20 02:49 | 1981 | Keep | 2025-05-20 | 2:49 | US | GS | - | 116.5 | g | 0 | 115.2 | 11.026 | 1075.8 | 3726 | 16:32 | 28.1 | 2.01 m/s | 31.9 | 29.4 | 4.2 m/s | 22.2 |  | 2.01 | m/s |  | 4.2 | m/s | 16.5356 | 0.008965 | 18.8634 |  | -1.5 | 461 | 0.461 | 40.9185 | 8.7286 | 6.5224 | 0.025807 | 49.9043 | 0.92377
2025-05-20 02:49 | 1982 | Remove | 2025-05-20 | 2:49 | ST | GS | - | 115.5 | g | 0 | 115.2 | 11.055 | 1079.4 | 3735 | 16:33 | 28.1 | 2.02 m/s | 30.7 | 29.4 | 4.23 m/s | 21.8 |  | 2.02 | m/s |  | 4.23 | m/s | 16.5439 | 0.008995 | 18.8724 |  | -1 | 461 | 0.461 | 40.938 | 8.4002 | 6.4049 | 0.02496 | 49.9293 | 0.92331
2025-05-20 02:50 | 1983 | Remove | 2025-05-20 | 2:50 | ST | GS | - | 117.5 | g | 0 | 115.1 | 11.067 | 1081.9 | 3744 | 16:33 | 28.1 | 2.02 m/s | 30.9 | 29.4 | 4.24 m/s | 21.2 |  | 2.02 | m/s |  | 4.24 | m/s | 16.5522 | 0.0090158 | 18.8814 |  | 2 | 463 | 0.463 | 40.7807 | 8.455 | 6.2286 | 0.025123 | 49.9544 | 0.92684
2025-05-20 02:50 | 1984 | Remove | 2025-05-20 | 2:50 | ST | GS | - | 120 | g | 0 | 115.1 | 11.056 | 1080.1 | 3753 | 16:34 | 28.1 | 2.05 m/s | 29.6 | 29.3 | 4.24 m/s | 21.2 |  | 2.05 | m/s |  | 4.24 | m/s | 16.5606 | 0.0090008 | 18.8904 |  | 2.5 | 465.5 | 0.4655 | 40.581 | 8.0993 | 6.1948 | 0.024423 | 49.9788 | 0.93139
2025-05-20 02:51 | 1985 | Remove | 2025-05-20 | 2:51 | ST | GS | - | 114.5 | g | 0 | 115.1 | 11.075 | 1082.8 | 3762 | 16:34 | 28.1 | 1.94 m/s | 30.1 | 29.3 | 4.26 m/s | 20.4 |  | 1.94 | m/s |  | 4.26 | m/s | 16.5689 | 0.0090233 | 18.8995 |  | -5.5 | 465.5 | 0.4655 | 40.6004 | 8.2361 | 5.961 | 0.023503 | 50.0023 | 0.93096
2025-05-20 02:51 | 1986 | Remove | 2025-05-20 | 2:51 | ST | GS | - | 115.5 | g | 0 | 115.2 | 11.059 | 1080.8 | 3771 | 16:35 | 28.1 | 2.02 m/s | 28.8 | 29.4 | 4.27 m/s | 21.3 |  | 2.02 | m/s |  | 4.27 | m/s | 16.5772 | 0.0090067 | 18.9085 |  | 1 | 466.5 | 0.4665 | 40.5326 | 7.8804 | 6.258 | 0.023415 | 50.0258 | 0.93252
2025-05-20 02:52 | 1987 | Remove | 2025-05-20 | 2:52 | ST | GS | - | 115.5 | g | 0 | 115.2 | 11.029 | 1076.5 | 3780 | 16:35 | 28.1 | 2.16 m/s | 29.5 | 29.4 | 4.29 m/s | 22.1 |  | 2.16 | m/s |  | 4.29 | m/s | 16.5856 | 0.0089708 | 18.9174 |  | 0 | 466.5 | 0.4665 | 40.5519 | 8.0719 | 6.4931 | 0.025647 | 50.0514 | 0.93204
2025-05-20 02:52 | 1988 | Remove | 2025-05-20 | 2:52 | US | GS | - | 117.5 | g | 0 | 115.1 | 11.105 | 1086.7 | 3789 | 16:36 | 28.1 | 2.06 m/s | 29.6 | 29.4 | 4.21 m/s | 21.3 |  | 2.06 | m/s |  | 4.21 | m/s | 16.5939 | 0.0090558 | 18.9265 |  | 2 | 468.5 | 0.4685 | 40.3981 | 8.0993 | 6.258 | 0.024542 | 50.076 | 0.93558
2025-05-20 02:53 | 1989 | Remove | 2025-05-20 | 2:53 | ST | GS | - | 115 | g | 0 | 115.1 | 11.042 | 1078.5 | 3798 | 16:36 | 28.1 | 2.04 m/s | 29.6 | 29.4 | 4.27 m/s | 21.5 |  | 2.04 | m/s |  | 4.27 | m/s | 16.6022 | 0.0089875 | 18.9355 |  | -2.5 | 468.5 | 0.4685 | 40.4173 | 8.0993 | 6.3168 | 0.024304 | 50.1003 | 0.93512
2025-05-20 02:53 | 1990 | Remove | 2025-05-20 | 2:53 | ST | GS | - | 117.5 | g | 0 | 115.1 | 11.059 | 1080.3 | 3807 | 16:37 | 28.1 | 2.09 m/s | 28 | 29.4 | 4.3 m/s | 21.4 |  | 2.09 | m/s |  | 4.3 | m/s | 16.6106 | 0.0090025 | 18.9445 |  | 2.5 | 471 | 0.471 | 40.2218 | 7.6615 | 6.2874 | 0.023554 | 50.1238 | 0.93967
2025-05-20 02:54 | 1991 | Remove | 2025-05-20 | 2:54 | ST | GS | - | 115 | g | 0 | 115.1 | 11.068 | 1082.4 | 3816 | 16:37 | 28.1 | 2.15 m/s | 27 | 29.4 | 4.24 m/s | 20 |  | 2.15 | m/s |  | 4.24 | m/s | 16.6189 | 0.00902 | 18.9535 |  | -2.5 | 471 | 0.471 | 40.241 | 7.3878 | 5.8761 | 0.023365 | 50.1472 | 0.93924
2025-05-20 02:54 | 1992 | Remove | 2025-05-20 | 2:54 | ST | GS | - | 115.5 | g | 0 | 115.1 | 11.042 | 1078.5 | 3825 | 16:38 | 28.1 | 2.12 m/s | 27.4 | 29.4 | 4.29 m/s | 21.3 |  | 2.12 | m/s |  | 4.29 | m/s | 16.6272 | 0.0089875 | 18.9625 |  | 0.5 | 471.5 | 0.4715 | 40.2174 | 7.4973 | 6.258 | 0.02338 | 50.1706 | 0.93979
2025-05-20 02:55 | 1993 | Remove | 2025-05-20 | 2:55 | ST | GS | - | 115.5 | g | 0 | 115.1 | 11.008 | 1074.1 | 3834 | 16:38 | 28.1 | 2.08 m/s | 27.2 | 29.4 | 4.23 m/s | 21.8 |  | 2.08 | m/s |  | 4.23 | m/s | 16.6356 | 0.0089508 | 18.9714 |  | 0 | 471.5 | 0.4715 | 40.2364 | 7.4426 | 6.4049 | 0.022771 | 50.1933 | 0.93937
2025-05-20 02:55 | 1994 | Remove | 2025-05-20 | 2:55 | ST | GS | - | 115.5 | g | 0 | 115.2 | 11.001 | 1072.4 | 3843 | 16:39 | 28.1 | 2.09 m/s | 28.2 | 29.4 | 4.23 m/s | 20.6 |  | 2.09 | m/s |  | 4.23 | m/s | 16.6439 | 0.0089367 | 18.9804 |  | 0 | 471.5 | 0.4715 | 40.2553 | 7.7162 | 6.0524 | 0.023722 | 50.217 | 0.93892
2025-05-20 02:56 | 1995 | Remove | 2025-05-20 | 2:56 | ST | GS | - | 116 | g | 0 | 115.2 | 10.993 | 1071.3 | 3852 | 16:39 | 28.1 | 2.12 m/s | 28.8 | 29.4 | 4.27 m/s | 22 |  | 2.12 | m/s |  | 4.27 | m/s | 16.6522 | 0.0089275 | 18.9893 |  | 0.5 | 472 | 0.472 | 40.2316 | 7.8804 | 6.4637 | 0.024574 | 50.2416 | 0.93946
2025-05-20 02:56 | 1996 | Remove | 2025-05-20 | 2:56 | ST | GS | - | 117.5 | g | 0 | 115.1 | 11.015 | 1074.7 | 3861 | 16:40 | 28 | 2.06 m/s | 28.4 | 29.4 | 4.23 m/s | 22 |  | 2.06 | m/s |  | 4.23 | m/s | 16.6606 | 0.0089558 | 18.9983 |  | 1.5 | 473.5 | 0.4735 | 40.1231 | 7.7283 | 6.4637 | 0.023418 | 50.265 | 0.94201
2025-05-20 02:57 | 1997 | Remove | 2025-05-20 | 2:57 | US | GS | - | 117.5 | g | 0 | 115.2 | 11.019 | 1075 | 3870 | 16:40 | 28 | 2.12 m/s | 29.5 | 29.3 | 4.36 m/s | 21.8 |  | 2.12 | m/s |  | 4.36 | m/s | 16.6692 | 0.0089583 | 19.0072 |  | 0 | 473.5 | 0.4735 | 40.142 | 8.0276 | 6.3701 | 0.025034 | 50.2901 | 0.94154
2025-05-20 02:57 | 1998 | Remove | 2025-05-20 | 2:57 | ST | GS | - | 118 | g | 0 | 115.1 | 11.098 | 1085.6 | 3879 | 16:41 | 28 | 2.01 m/s | 29.1 | 29.3 | 4.3 m/s | 21.4 |  | 2.01 | m/s |  | 4.3 | m/s | 16.6775 | 0.0090467 | 19.0163 |  | 0.5 | 474 | 0.474 | 40.1187 | 7.9187 | 6.2532 | 0.023413 | 50.3135 | 0.94209
2025-05-20 02:58 | 1999 | Remove | 2025-05-20 | 2:58 | ST | GS | - | 115.5 | g | 0 | 115.3 | 11.03 | 1076.5 | 3888 | 16:41 | 28.1 | 2.11 m/s | 29 | 29.3 | 4.26 m/s | 22.1 |  | 2.11 | m/s |  | 4.26 | m/s | 16.6858 | 0.0089708 | 19.0252 |  | -2.5 | 474 | 0.474 | 40.1376 | 7.9351 | 6.4578 | 0.024628 | 50.3381 | 0.94163
2025-05-20 02:58 | 2000 | Remove | 2025-05-20 | 2:58 | ST | GS | - | 116 | g | 0 | 115.2 | 11.001 | 1073.1 | 3897 | 16:42 | 28.1 | 2.12 m/s | 28.3 | 29.4 | 4.26 m/s | 22.7 |  | 2.12 | m/s |  | 4.26 | m/s | 16.6942 | 0.0089425 | 19.0342 |  | 0.5 | 474.5 | 0.4745 | 40.1142 | 7.7435 | 6.6693 | 0.024148 | 50.3623 | 0.94217
2025-05-20 02:59 | 2001 | Remove | 2025-05-20 | 2:59 | ST | GS | - | 116 | g | 0 | 115.2 | 11.016 | 1074.7 | 3906 | 16:42 | 28.1 | 2.11 m/s | 28.5 | 29.3 | 4.24 m/s | 21.8 |  | 2.11 | m/s |  | 4.24 | m/s | 16.7025 | 0.0089558 | 19.0431 |  | 0 | 474.5 | 0.4745 | 40.1331 | 7.7983 | 6.3701 | 0.024204 | 50.3865 | 0.94172
2025-05-20 02:59 | 2002 | Remove | 2025-05-20 | 2:59 | ST | GS | - | 116 | g | 0 | 115.2 | 11.04 | 1078.1 | 3915 | 16:43 | 28 | 2.15 m/s | 28.7 | 29.3 | 4.21 m/s | 21.1 |  | 2.15 | m/s |  | 4.21 | m/s | 16.7108 | 0.0089842 | 19.0521 |  | 0 | 474.5 | 0.4745 | 40.152 | 7.8099 | 6.1656 | 0.024699 | 50.4112 | 0.94126
2025-05-20 03:00 | 2003 | Remove | 2025-05-20 | 3:00 | ST | GS | - | 116 | g | 0 | 115.2 | 11.005 | 1073.2 | 3924 | 16:43 | 28.1 | 2.06 m/s | 27.6 | 29.3 | 4.24 m/s | 20.7 |  | 2.06 | m/s |  | 4.24 | m/s | 16.7192 | 0.0089433 | 19.0611 |  | 0 | 474.5 | 0.4745 | 40.1709 | 7.552 | 6.0487 | 0.022884 | 50.434 | 0.94083
2025-05-20 03:00 | 2004 | Remove | 2025-05-20 | 3:00 | ST | GS | - | 116.5 | g | 0 | 115.3 | 11.004 | 1072.7 | 3933 | 16:44 | 28 | 2.16 m/s | 28 | 29.3 | 4.29 m/s | 21.1 |  | 2.16 | m/s |  | 4.29 | m/s | 16.7275 | 0.0089392 | 19.07 |  | 0.5 | 475 | 0.475 | 40.1474 | 7.6194 | 6.1656 | 0.024209 | 50.4583 | 0.94137
2025-05-20 03:01 | 2005 | Remove | 2025-05-20 | 3:01 | ST | GS | - | 116.5 | g | 0 | 115.2 | 11.006 | 1073.2 | 3942 | 16:44 | 28 | 2.08 m/s | 28.1 | 29.3 | 4.29 m/s | 22 |  | 2.08 | m/s |  | 4.29 | m/s | 16.7358 | 0.0089433 | 19.079 |  | 0 | 475 | 0.475 | 40.1662 | 7.6466 | 6.4286 | 0.023396 | 50.4817 | 0.94094
2025-05-20 03:01 | 2006 | Remove | 2025-05-20 | 3:01 | ST | GS | - | 116 | g | 0 | 115.2 | 11.028 | 1075.7 | 3951 | 16:45 | 28 | 2.08 m/s | 28.3 | 29.3 | 4.21 m/s | 20.8 |  | 2.08 | m/s |  | 4.21 | m/s | 16.7442 | 0.0089642 | 19.0879 |  | -0.5 | 475 | 0.475 | 40.1851 | 7.701 | 6.0779 | 0.023562 | 50.5052 | 0.9405
2025-05-20 03:02 | 2007 | Remove | 2025-05-20 | 3:02 | US | GS | - | 119 | g | 0 | 115.2 | 11.025 | 1075.9 | 3960 | 16:45 | 28 | 2.12 m/s | 28.8 | 29.3 | 4.29 m/s | 21.4 |  | 2.12 | m/s |  | 4.29 | m/s | 16.7525 | 0.0089658 | 19.0969 |  | 3 | 478 | 0.478 | 39.9516 | 7.8371 | 6.2532 | 0.02444 | 50.5297 | 0.94598
2025-05-20 03:02 | 2008 | Remove | 2025-05-20 | 3:02 | ST | GS | - | 116 | g | 0 | 115.2 | 11.044 | 1077.6 | 3969 | 16:46 | 28 | 2.12 m/s | 30.2 | 29.3 | 4.29 m/s | 21.7 |  | 2.12 | m/s |  | 4.29 | m/s | 16.7608 | 0.00898 | 19.1059 |  | -3 | 478 | 0.478 | 39.9704 | 8.2181 | 6.3409 | 0.025628 | 50.5553 | 0.9455
2025-05-20 03:03 | 2009 | Remove | 2025-05-20 | 3:03 | ST | GS | - | 117 | g | 0 | 115.2 | 11.007 | 1073 | 3978 | 16:46 | 28 | 2.11 m/s | 32.7 | 29.3 | 4.24 m/s | 22.5 |  | 2.11 | m/s |  | 4.24 | m/s | 16.7692 | 0.0089417 | 19.1148 |  | 1 | 479 | 0.479 | 39.9056 | 8.8984 | 6.5747 | 0.027618 | 50.5829 | 0.94696
2025-05-20 03:03 | 2010 | Remove | 2025-05-20 | 3:03 | ST | GS | - | 117 | g | 0 | 115.1 | 11.046 | 1078.7 | 3987 | 16:47 | 28 | 2.12 m/s | 29.8 | 29.3 | 4.26 m/s | 22.5 |  | 2.12 | m/s |  | 4.26 | m/s | 16.7775 | 0.0089892 | 19.1238 |  | 0 | 479 | 0.479 | 39.9244 | 8.1092 | 6.5747 | 0.025288 | 50.6082 | 0.94649
2025-05-20 03:04 | 2011 | Keep | 2025-05-20 | 3:04 | ST | GS | - | 118.5 | g | 0 | 115.1 | 11.046 | 1078.9 | 3996 | 16:47 | 28 | 1.98 m/s | 31.7 | 29.3 | 4.3 m/s | 22 |  | 1.98 | m/s |  | 4.3 | m/s | 16.7858 | 0.0089908 | 19.1328 |  | 1.5 | 480.5 | 0.4805 | 39.8185 | 8.6263 | 6.4286 | 0.025124 | 50.6333 | 0.94898
2025-05-20 03:04 | 2012 | Remove | 2025-05-20 | 3:04 | ST | GS | - | 119 | g | 0 | 115.1 | 11.074 | 1082.2 | 4005 | 16:48 | 28.1 | 2.04 m/s | 29.7 | 29.3 | 4.26 m/s | 22.3 |  | 2.04 | m/s |  | 4.26 | m/s | 16.7942 | 0.0090183 | 19.1418 |  | 0.5 | 481 | 0.481 | 39.7958 | 8.1266 | 6.5162 | 0.024386 | 50.6577 | 0.94951
2025-05-20 03:05 | 2013 | Remove | 2025-05-20 | 3:05 | ST | GS | - | 115.5 | g | 0 | 115.1 | 11.056 | 1079.2 | 4014 | 16:48 | 28.1 | 2.12 m/s | 29 | 29.3 | 4.21 m/s | 21.5 |  | 2.12 | m/s |  | 4.21 | m/s | 16.8025 | 0.0089933 | 19.1508 |  | -3.5 | 481 | 0.481 | 39.8145 | 7.9351 | 6.2825 | 0.024745 | 50.6824 | 0.94905
2025-05-20 03:05 | 2014 | Remove | 2025-05-20 | 3:05 | ST | GS | - | 116 | g | 0 | 115.1 | 11.03 | 1076.2 | 4023 | 16:49 | 28.1 | 2.02 m/s | 30.7 | 29.3 | 4.26 m/s | 22.2 |  | 2.02 | m/s |  | 4.26 | m/s | 16.8111 | 0.0089683 | 19.1598 |  | 0.5 | 481.5 | 0.4815 | 39.7918 | 8.4002 | 6.487 | 0.02496 | 50.7074 | 0.94957
2025-05-20 03:06 | 2015 | Remove | 2025-05-20 | 3:06 | US | GS | - | 119 | g | 0 | 115.1 | 11.015 | 1074.8 | 4032 | 16:49 | 28.1 | 2.08 m/s | 29.4 | 29.4 | 4.23 m/s | 22.3 |  | 2.08 | m/s |  | 4.23 | m/s | 16.8194 | 0.0089567 | 19.1687 |  | 3 | 484.5 | 0.4845 | 39.5639 | 8.0445 | 6.5518 | 0.024613 | 50.732 | 0.95502
2025-05-20 03:06 | 2016 | Remove | 2025-05-20 | 3:06 | ST | GS | - | 116 | g | 0 | 115.1 | 11.011 | 1073.6 | 4041 | 16:50 | 28.1 | 1.93 m/s | 29.7 | 29.4 | 4.3 m/s | 21.1 |  | 1.93 | m/s |  | 4.3 | m/s | 16.8278 | 0.0089467 | 19.1777 |  | -3 | 484.5 | 0.4845 | 39.5824 | 8.1266 | 6.1993 | 0.023071 | 50.7551 | 0.95458
2025-05-20 03:07 | 2017 | Remove | 2025-05-20 | 3:07 | ST | GS | - | 116 | g | 0 | 115.1 | 11.018 | 1074.2 | 4050 | 16:50 | 28 | 2.12 m/s | 28.6 | 29.4 | 4.2 m/s | 22 |  | 2.12 | m/s |  | 4.2 | m/s | 16.8361 | 0.0089517 | 19.1866 |  | 0 | 484.5 | 0.4845 | 39.6009 | 7.7827 | 6.4637 | 0.02427 | 50.7794 | 0.95413
2025-05-20 03:07 | 2018 | Remove | 2025-05-20 | 3:07 | ST | GS | - | 116.5 | g | 0 | 115.1 | 11.01 | 1073.1 | 4059 | 16:51 | 28 | 2.06 m/s | 28.3 | 29.3 | 4.23 m/s | 22 |  | 2.06 | m/s |  | 4.23 | m/s | 16.8444 | 0.0089425 | 19.1956 |  | 0.5 | 485 | 0.485 | 39.5785 | 7.701 | 6.4286 | 0.023336 | 50.8027 | 0.95467
2025-05-20 03:08 | 2019 | Remove | 2025-05-20 | 3:08 | ST | GS | - | 119.5 | g | 0 | 115.1 | 11.049 | 1079.2 | 4068 | 16:51 | 28 | 2.08 m/s | 28.4 | 29.3 | 4.26 m/s | 22.5 |  | 2.08 | m/s |  | 4.26 | m/s | 16.8528 | 0.0089933 | 19.2046 |  | 3 | 488 | 0.488 | 39.3536 | 7.7283 | 6.5747 | 0.023645 | 50.8263 | 0.96013
2025-05-20 03:08 | 2020 | Remove | 2025-05-20 | 3:08 | ST | GS | - | 116 | g | 0 | 115.1 | 11.042 | 1077.9 | 4077 | 16:52 | 28.1 | 2.09 m/s | 29.4 | 29.3 | 4.26 m/s | 21.6 |  | 2.09 | m/s |  | 4.26 | m/s | 16.8611 | 0.0089825 | 19.2135 |  | -3.5 | 488 | 0.488 | 39.372 | 8.0445 | 6.3117 | 0.024731 | 50.8511 | 0.95967
2025-05-20 03:09 | 2021 | Remove | 2025-05-20 | 3:09 | ST | GS | - | 116 | g | 0 | 115.1 | 11.013 | 1074.6 | 4086 | 16:52 | 28 | 2.08 m/s | 30.6 | 29.3 | 4.26 m/s | 21.8 |  | 2.08 | m/s |  | 4.26 | m/s | 16.8694 | 0.008955 | 19.2225 |  | 0 | 488 | 0.488 | 39.3904 | 8.3269 | 6.3701 | 0.025477 | 50.8765 | 0.95918
2025-05-20 03:09 | 2022 | Remove | 2025-05-20 | 3:09 | US | GS | - | 118.5 | g | 0 | 115.1 | 11.009 | 1073.2 | 4095 | 16:53 | 28 | 2.08 m/s | 29.8 | 29.3 | 4.29 m/s | 22.5 |  | 2.08 | m/s |  | 4.29 | m/s | 16.8778 | 0.0089433 | 19.2314 |  | 2.5 | 490.5 | 0.4905 | 39.2078 | 8.1092 | 6.5747 | 0.024811 | 50.9014 | 0.96363
2025-05-20 03:10 | 2023 | Remove | 2025-05-20 | 3:10 | ST | GS | - | 116.5 | g | 0 | 115.2 | 11.006 | 1072.9 | 4104 | 16:53 | 28 | 2.06 m/s | 29.9 | 29.3 | 4.21 m/s | 21.4 |  | 2.06 | m/s |  | 4.21 | m/s | 16.8861 | 0.0089408 | 19.2404 |  | -2 | 490.5 | 0.4905 | 39.226 | 8.1364 | 6.2532 | 0.024655 | 50.926 | 0.96316
2025-05-20 03:10 | 2024 | Remove | 2025-05-20 | 3:10 | ST | GS | - | 117 | g | 0 | 115.2 | 11.01 | 1074 | 4113 | 16:54 | 28 | 2.12 m/s | 28.6 | 29.3 | 4.29 m/s | 21.7 |  | 2.12 | m/s |  | 4.29 | m/s | 16.8944 | 0.00895 | 19.2493 |  | 0.5 | 491 | 0.491 | 39.2043 | 7.7827 | 6.3409 | 0.02427 | 50.9503 | 0.96368
2025-05-20 03:11 | 2025 | Remove | 2025-05-20 | 3:11 | ST | GS | - | 118 | g | 0 | 115.2 | 11.006 | 1073.5 | 4122 | 16:54 | 28 | 2.11 m/s | 29.2 | 29.3 | 4.26 m/s | 22.1 |  | 2.11 | m/s |  | 4.26 | m/s | 16.9028 | 0.0089458 | 19.2583 |  | 1 | 492 | 0.492 | 39.1428 | 7.946 | 6.4578 | 0.024662 | 50.9749 | 0.96518
2025-05-20 03:11 | 2026 | Remove | 2025-05-20 | 3:11 | ST | GS | - | 117.5 | g | 0 | 115.2 | 11.01 | 1074.1 | 4131 | 16:55 | 28 | 2.11 m/s | 30 | 29.3 | 4.26 m/s | 21.4 |  | 2.11 | m/s |  | 4.26 | m/s | 16.9111 | 0.0089508 | 19.2672 |  | -0.5 | 492 | 0.492 | 39.161 | 8.1637 | 6.2532 | 0.025338 | 51.0003 | 0.9647
2025-05-20 03:12 | 2027 | Remove | 2025-05-20 | 3:12 | ST | GS | - | 118 | g | 0 | 115.2 | 11.018 | 1074.8 | 4140 | 16:55 | 28 | 2.11 m/s | 29.8 | 29.3 | 4.24 m/s | 20.9 |  | 2.11 | m/s |  | 4.24 | m/s | 16.9194 | 0.0089567 | 19.2762 |  | 0.5 | 492.5 | 0.4925 | 39.1395 | 8.1092 | 6.1071 | 0.025169 | 51.0255 | 0.9652
2025-05-20 03:12 | 2028 | Remove | 2025-05-20 | 3:12 | ST | GS | - | 117.5 | g | 0 | 115.1 | 11.02 | 1074.5 | 4149 | 16:56 | 28 | 1.81 m/s | 28.8 | 29.3 | 4.24 m/s | 21 |  | 1.81 | m/s |  | 4.24 | m/s | 16.9278 | 0.0089542 | 19.2851 |  | -0.5 | 492.5 | 0.4925 | 39.1576 | 7.8371 | 6.1363 | 0.020866 | 51.0463 | 0.96481
2025-05-20 03:13 | 2029 | Remove | 2025-05-20 | 3:13 | ST | GS | - | 116.5 | g | 0 | 115.2 | 10.988 | 1070.9 | 4158 | 16:56 | 28 | 2.04 m/s | 29.2 | 29.3 | 4.27 m/s | 21.2 |  | 2.04 | m/s |  | 4.27 | m/s | 16.9361 | 0.0089242 | 19.2941 |  | -1 | 492.5 | 0.4925 | 39.1758 | 7.946 | 6.1948 | 0.023844 | 51.0702 | 0.96436
2025-05-20 03:13 | 2030 | Remove | 2025-05-20 | 3:13 | ST | GS | - | 119 | g | 0 | 115.1 | 11.036 | 1077 | 4167 | 16:57 | 28 | 2.08 m/s | 28 | 29.3 | 4.2 m/s | 20.7 |  | 2.08 | m/s |  | 4.2 | m/s | 16.9444 | 0.008975 | 19.303 |  | 2.5 | 495 | 0.495 | 38.996 | 7.6194 | 6.0487 | 0.023312 | 51.0935 | 0.96881
2025-05-20 03:14 | 2031 | Remove | 2025-05-20 | 3:14 | ST | GS | - | 116.5 | g | 0 | 115.2 | 10.993 | 1070.8 | 4176 | 16:57 | 28 | 2.12 m/s | 28.1 | 29.3 | 4.29 m/s | 21 |  | 2.12 | m/s |  | 4.29 | m/s | 16.9528 | 0.0089233 | 19.312 |  | -2.5 | 495 | 0.495 | 39.0141 | 7.6466 | 6.1363 | 0.023846 | 51.1173 | 0.96836
2025-05-20 03:14 | 2032 | Remove | 2025-05-20 | 3:14 | ST | GS | - | 118.5 | g | 0 | 115.2 | 11.055 | 1079.4 | 4185 | 16:58 | 28 | 1.97 m/s | 28.2 | 29.3 | 4.21 m/s | 20.6 |  | 1.97 | m/s |  | 4.21 | m/s | 16.9611 | 0.008995 | 19.321 |  | 2 | 497 | 0.497 | 38.8752 | 7.6738 | 6.0195 | 0.022237 | 51.1396 | 0.97185
2025-05-20 03:15 | 2033 | Remove | 2025-05-20 | 3:15 | ST | GS | - | 118.5 | g | 0 | 115.1 | 11.044 | 1078.5 | 4193 | 16:58 | 28 | 2.08 m/s | 28.1 | 29.3 | 4.26 m/s | 21.1 |  | 2.08 | m/s |  | 4.26 | m/s | 16.9694 | 0.0089875 | 19.3299 |  | 0 | 497 | 0.497 | 38.8932 | 7.6466 | 6.1656 | 0.023396 | 51.163 | 0.97141
2025-05-20 03:15 | 2034 | Remove | 2025-05-20 | 3:15 | ST | GS | - | 117.5 | g | 0 | 115.1 | 11.08 | 1083.1 | 4203 | 16:59 | 28 | 2.15 m/s | 27.4 | 29.3 | 4.26 m/s | 20 |  | 2.15 | m/s |  | 4.26 | m/s | 16.9781 | 0.0090258 | 19.339 |  | -1 | 497 | 0.497 | 38.9114 | 7.4561 | 5.8441 | 0.023581 | 51.1865 | 0.97096
2025-05-20 03:16 | 2035 | Remove | 2025-05-20 | 3:16 | ST | GS | - | 118.5 | g | 0 | 115.1 | 11.058 | 1080.1 | 4212 | 16:59 | 28.1 | 2.09 m/s | 27.1 | 29.3 | 4.27 m/s | 20.5 |  | 2.09 | m/s |  | 4.27 | m/s | 16.9864 | 0.0090008 | 19.348 |  | 1 | 498 | 0.498 | 38.8513 | 7.4152 | 5.9902 | 0.022797 | 51.2093 | 0.97248
2025-05-20 03:16 | 2036 | Remove | 2025-05-20 | 3:16 | ST | GS | - | 116 | g | 0 | 115.1 | 11.047 | 1078.9 | 4221 | 17:00 | 28.1 | 2.04 m/s | 27 | 29.3 | 4.22 m/s | 19.8 |  | 2.04 | m/s |  | 4.22 | m/s | 16.9947 | 0.0089908 | 19.357 |  | -2.5 | 498 | 0.498 | 38.8694 | 7.3878 | 5.7857 | 0.022169 | 51.2315 | 0.97206
2025-05-20 03:17 | 2037 | Remove | 2025-05-20 | 3:17 | ST | GS | - | 118.5 | g | 0 | 115.2 | 11.033 | 1076.8 | 4230 | 17:00 | 28.1 | 2.04 m/s | 27.2 | 29.4 | 4.27 m/s | 20.4 |  | 2.04 | m/s |  | 4.27 | m/s | 17.0031 | 0.0089733 | 19.3659 |  | 2.5 | 500.5 | 0.5005 | 38.6932 | 7.4426 | 5.9936 | 0.022333 | 51.2538 | 0.97651
2025-05-20 03:17 | 2038 | Remove | 2025-05-20 | 3:17 | ST | GS | - | 118 | g | 0 | 115.2 | 11.012 | 1074.3 | 4239 | 17:01 | 28.1 | 2.09 m/s | 27.2 | 29.4 | 4.23 m/s | 20 |  | 2.09 | m/s |  | 4.23 | m/s | 17.0114 | 0.0089525 | 19.3749 |  | -0.5 | 500.5 | 0.5005 | 38.7111 | 7.4426 | 5.8761 | 0.022881 | 51.2767 | 0.97608
2025-05-20 03:18 | 2039 | Remove | 2025-05-20 | 3:18 | ST | GS | - | 118.5 | g | 0 | 115.2 | 11.001 | 1072.9 | 4248 | 17:01 | 28 | 2.06 m/s | 27.7 | 29.4 | 4.27 m/s | 20.4 |  | 2.06 | m/s |  | 4.27 | m/s | 17.0197 | 0.0089408 | 19.3838 |  | 0.5 | 501 | 0.501 | 38.6903 | 7.5378 | 5.9936 | 0.022841 | 51.2996 | 0.97662
2025-05-20 03:18 | 2040 | Remove | 2025-05-20 | 3:18 | ST | GS | - | 117.5 | g | 0 | 115.1 | 11.019 | 1074.7 | 4257 | 17:02 | 28 | 2.06 m/s | 27.1 | 29.3 | 4.29 m/s | 20.3 |  | 2.06 | m/s |  | 4.29 | m/s | 17.0281 | 0.0089558 | 19.3928 |  | -1 | 501 | 0.501 | 38.7081 | 7.3745 | 5.9318 | 0.022346 | 51.3219 | 0.97619
2025-05-20 03:19 | 2041 | Keep | 2025-05-20 | 3:19 | ST | GS | - | 117.5 | g | 0 | 115.1 | 11.068 | 1081.6 | 4266 | 17:02 | 28 | 2.15 m/s | 28.3 | 29.3 | 4.29 m/s | 20 |  | 2.15 | m/s |  | 4.29 | m/s | 17.0364 | 0.0090133 | 19.4018 |  | 0 | 501 | 0.501 | 38.7261 | 7.701 | 5.8441 | 0.024355 | 51.3463 | 0.97573
2025-05-20 03:19 | 2042 | Remove | 2025-05-20 | 3:19 | ST | GS | - | 118.5 | g | 0 | 115.1 | 11.088 | 1083.6 | 4275 | 17:03 | 28.1 | 2.11 m/s | 26.6 | 29.3 | 4.46 m/s | 19.6 |  | 2.11 | m/s |  | 4.46 | m/s | 17.0447 | 0.00903 | 19.4108 |  | 1 | 502 | 0.502 | 38.667 | 7.2784 | 5.7273 | 0.02259 | 51.3688 | 0.97725
2025-05-20 03:20 | 2043 | Remove | 2025-05-20 | 3:20 | ST | GS | - | 118 | g | 0 | 115.3 | 11.057 | 1080.2 | 4284 | 17:03 | 28.1 | 2.06 m/s | 26.6 | 29.3 | 4.2 m/s | 20.1 |  | 2.06 | m/s |  | 4.2 | m/s | 17.0531 | 0.0090017 | 19.4198 |  | -0.5 | 502 | 0.502 | 38.6849 | 7.2784 | 5.8734 | 0.022055 | 51.3909 | 0.97683
2025-05-20 03:20 | 2044 | Remove | 2025-05-20 | 3:20 | ST | GS | - | 119 | g | 0 | 115.1 | 11.093 | 1085.1 | 4293 | 17:04 | 28.1 | 2.15 m/s | 27.3 | 29.4 | 4.32 m/s | 19.7 |  | 2.15 | m/s |  | 4.32 | m/s | 17.0614 | 0.0090425 | 19.4289 |  | 1 | 503 | 0.503 | 38.626 | 7.4699 | 5.7879 | 0.023624 | 51.4145 | 0.97832
2025-05-20 03:21 | 2045 | Remove | 2025-05-20 | 3:21 | ST | GS | - | 117 | g | 0 | 115.2 | 11.087 | 1083.7 | 4302 | 17:04 | 28.1 | 2.13 m/s | 26.6 | 29.4 | 4.26 m/s | 20.3 |  | 2.13 | m/s |  | 4.26 | m/s | 17.0697 | 0.0090308 | 19.4379 |  | -2 | 503 | 0.503 | 38.6439 | 7.2784 | 5.9642 | 0.022804 | 51.4373 | 0.97789
2025-05-20 03:21 | 2046 | Remove | 2025-05-20 | 3:21 | US | GS | - | 119 | g | 0 | 115.1 | 11.092 | 1084.4 | 4311 | 17:05 | 28.1 | 2.08 m/s | 26.8 | 29.4 | 4.3 m/s | 20.1 |  | 2.08 | m/s |  | 4.3 | m/s | 17.0781 | 0.0090367 | 19.4469 |  | 2 | 505 | 0.505 | 38.5088 | 7.3331 | 5.9055 | 0.022436 | 51.4598 | 0.98135
2025-05-20 03:22 | 2047 | Remove | 2025-05-20 | 3:22 | ST | GS | - | 117.5 | g | 0 | 115.1 | 11.129 | 1089.5 | 4320 | 17:05 | 28.1 | 2.11 m/s | 26.6 | 29.4 | 4.38 m/s | 20 |  | 2.11 | m/s |  | 4.38 | m/s | 17.0864 | 0.0090792 | 19.456 |  | -1.5 | 505 | 0.505 | 38.5268 | 7.2784 | 5.8761 | 0.02259 | 51.4824 | 0.98092
2025-05-20 03:22 | 2048 | Remove | 2025-05-20 | 3:22 | ST | GS | - | 119.5 | g | 0 | 115.1 | 11.095 | 1084.7 | 4329 | 17:06 | 28.2 | 2.13 m/s | 26.4 | 29.4 | 4.33 m/s | 19.6 |  | 2.13 | m/s |  | 4.33 | m/s | 17.0947 | 0.0090392 | 19.4651 |  | 2 | 507 | 0.507 | 38.3926 | 7.2635 | 5.7586 | 0.022758 | 51.5051 | 0.98437
2025-05-20 03:23 | 2049 | Remove | 2025-05-20 | 3:23 | ST | GS | - | 117.5 | g | 0 | 115.1 | 11.086 | 1083.6 | 4338 | 17:06 | 28.2 | 2.11 m/s | 26.6 | 29.4 | 4.44 m/s | 19.5 |  | 2.11 | m/s |  | 4.44 | m/s | 17.1031 | 0.00903 | 19.4741 |  | -2 | 507 | 0.507 | 38.4104 | 7.3185 | 5.7292 | 0.022715 | 51.5278 | 0.98393
2025-05-20 03:23 | 2050 | Remove | 2025-05-20 | 3:23 | ST | GS | - | 118 | g | 0 | 115.1 | 11.097 | 1085.2 | 4347 | 17:07 | 28.2 | 2.15 m/s | 26.1 | 29.4 | 4.24 m/s | 20 |  | 2.15 | m/s |  | 4.24 | m/s | 17.1114 | 0.0090433 | 19.4831 |  | 0.5 | 507.5 | 0.5075 | 38.3904 | 7.1809 | 5.8761 | 0.02271 | 51.5505 | 0.98447
2025-05-20 03:24 | 2051 | Remove | 2025-05-20 | 3:24 | ST | GS | - | 117 | g | 0 | 115.2 | 11.095 | 1085.1 | 4356 | 17:07 | 28.2 | 2.12 m/s | 26.8 | 29.4 | 4.3 m/s | 19.6 |  | 2.12 | m/s |  | 4.3 | m/s | 17.12 | 0.0090425 | 19.4922 |  | -1 | 507.5 | 0.5075 | 38.4082 | 7.3735 | 5.7586 | 0.022994 | 51.5735 | 0.98403
2025-05-20 03:24 | 2052 | Remove | 2025-05-20 | 3:24 | ST | GS | - | 118 | g | 0 | 115.1 | 11.094 | 1085.1 | 4365 | 17:08 | 28.2 | 2.06 m/s | 26.5 | 29.4 | 4.47 m/s | 20.1 |  | 2.06 | m/s |  | 4.47 | m/s | 17.1283 | 0.0090425 | 19.5012 |  | 1 | 508.5 | 0.5085 | 38.3505 | 7.291 | 5.9055 | 0.022093 | 51.5956 | 0.98555
2025-05-20 03:25 | 2053 | Remove | 2025-05-20 | 3:25 | US | GS | - | 117.5 | g | 0 | 115 | 11.114 | 1087.7 | 4374 | 17:08 | 28.2 | 2.13 m/s | 26.1 | 29.4 | 4.53 m/s | 19.5 |  | 2.13 | m/s |  | 4.53 | m/s | 17.1367 | 0.0090642 | 19.5103 |  | -0.5 | 508.5 | 0.5085 | 38.3683 | 7.1809 | 5.7292 | 0.022499 | 51.6181 | 0.98512
2025-05-20 03:25 | 2054 | Remove | 2025-05-20 | 3:25 | ST | GS | - | 118.5 | g | 0 | 115.1 | 11.083 | 1083.3 | 4383 | 17:09 | 28.2 | 2.01 m/s | 26.3 | 29.4 | 4.24 m/s | 20 |  | 2.01 | m/s |  | 4.24 | m/s | 17.145 | 0.0090275 | 19.5193 |  | 1 | 509.5 | 0.5095 | 38.3107 | 7.236 | 5.8761 | 0.021394 | 51.6395 | 0.98665
2025-05-20 03:26 | 2055 | Remove | 2025-05-20 | 3:26 | ST | GS | - | 116.5 | g | 0 | 115.1 | 11.072 | 1082.4 | 4392 | 17:09 | 28.2 | 2.12 m/s | 26.1 | 29.5 | 4.23 m/s | 19.5 |  | 2.12 | m/s |  | 4.23 | m/s | 17.1533 | 0.00902 | 19.5283 |  | -2 | 509.5 | 0.5095 | 38.3284 | 7.1809 | 5.7604 | 0.022393 | 51.6619 | 0.98622
2025-05-20 03:26 | 2056 | Remove | 2025-05-20 | 3:26 | US | GS | - | 118.5 | g | 0 | 115.1 | 11.106 | 1086.9 | 4402 | 17:10 | 28.2 | 2.09 m/s | 27 | 29.5 | 4.33 m/s | 19.4 |  | 2.09 | m/s |  | 4.33 | m/s | 17.1617 | 0.0090575 | 19.5374 |  | 2 | 511.5 | 0.5115 | 38.1962 | 7.4286 | 5.7309 | 0.022838 | 51.6848 | 0.98965
2025-05-20 03:27 | 2057 | Remove | 2025-05-20 | 3:27 | ST | GS | - | 116 | g | 0 | 115.1 | 11.093 | 1085.7 | 4411 | 17:10 | 28.2 | 2.18 m/s | 25.9 | 29.5 | 4.29 m/s | 19.1 |  | 2.18 | m/s |  | 4.29 | m/s | 17.17 | 0.0090475 | 19.5464 |  | -2.5 | 511.5 | 0.5115 | 38.2139 | 7.1259 | 5.6423 | 0.022851 | 51.7076 | 0.98922
2025-05-20 03:27 | 2058 | Remove | 2025-05-20 | 3:27 | ST | GS | - | 116.5 | g | 0 | 115.1 | 11.067 | 1081.3 | 4420 | 17:11 | 28.2 | 2.11 m/s | 26.5 | 29.5 | 4.3 m/s | 19.7 |  | 2.11 | m/s |  | 4.3 | m/s | 17.1783 | 0.0090108 | 19.5554 |  | 0.5 | 512 | 0.512 | 38.1942 | 7.291 | 5.8195 | 0.022629 | 51.7302 | 0.98975
2025-05-20 03:28 | 2059 | Remove | 2025-05-20 | 3:28 | US | GS | - | 117.5 | g | 0 | 115.1 | 11.1 | 1086.2 | 4429 | 17:11 | 28.1 | 2.02 m/s | 27 | 29.5 | 4.27 m/s | 20.1 |  | 2.02 | m/s |  | 4.27 | m/s | 17.1867 | 0.0090517 | 19.5645 |  | 1 | 513 | 0.513 | 38.1374 | 7.3878 | 5.9377 | 0.021952 | 51.7522 | 0.99126
2025-05-20 03:28 | 2060 | Remove | 2025-05-20 | 3:28 | ST | GS | - | 118 | g | 0 | 115.1 | 11.1 | 1086.3 | 4438 | 17:12 | 28.2 | 2.15 m/s | 26.2 | 29.5 | 4.33 m/s | 19.2 |  | 2.15 | m/s |  | 4.33 | m/s | 17.195 | 0.0090525 | 19.5735 |  | 0.5 | 513.5 | 0.5135 | 38.1179 | 7.2085 | 5.6718 | 0.022797 | 51.775 | 0.99179
2025-05-20 03:29 | 2061 | Remove | 2025-05-20 | 3:29 | ST | GS | - | 117 | g | 0 | 115.1 | 11.05 | 1078.9 | 4447 | 17:12 | 28.2 | 2.11 m/s | 25.8 | 29.5 | 4.2 m/s | 20 |  | 2.11 | m/s |  | 4.2 | m/s | 17.2033 | 0.0089908 | 19.5825 |  | -1 | 513.5 | 0.5135 | 38.1354 | 7.0984 | 5.9082 | 0.022032 | 51.797 | 0.99137
2025-05-20 03:29 | 2062 | Remove | 2025-05-20 | 3:29 | ST | GS | - | 117.5 | g | 0 | 115.1 | 11.024 | 1076.2 | 4456 | 17:13 | 28.1 | 2.06 m/s | 26.5 | 29.5 | 4.32 m/s | 20.2 |  | 2.06 | m/s |  | 4.32 | m/s | 17.2117 | 0.0089683 | 19.5915 |  | 0.5 | 514 | 0.514 | 38.1158 | 7.251 | 5.9672 | 0.021972 | 51.819 | 0.99191
2025-05-20 03:30 | 2063 | Remove | 2025-05-20 | 3:30 | ST | GS | - | 118 | g | 0 | 115.1 | 11.052 | 1079.2 | 4465 | 17:13 | 28.1 | 2.13 m/s | 26.8 | 29.4 | 4.3 m/s | 20.5 |  | 2.13 | m/s |  | 4.3 | m/s | 17.22 | 0.0089933 | 19.6005 |  | 0.5 | 514.5 | 0.5145 | 38.0962 | 7.3331 | 6.023 | 0.022976 | 51.842 | 0.99244
2025-05-20 03:30 | 2064 | Remove | 2025-05-20 | 3:30 | ST | GS | - | 117 | g | 0 | 115.1 | 11.031 | 1076 | 4474 | 17:14 | 28.1 | 2.05 m/s | 26.7 | 29.4 | 4.24 m/s | 19.7 |  | 2.05 | m/s |  | 4.24 | m/s | 17.2283 | 0.0089667 | 19.6095 |  | -1 | 514.5 | 0.5145 | 38.1136 | 7.3057 | 5.7879 | 0.02203 | 51.864 | 0.99202
2025-05-20 03:31 | 2065 | Remove | 2025-05-20 | 3:31 | ST | GS | - | 117.5 | g | 0 | 115.2 | 11.009 | 1072.8 | 4483 | 17:14 | 28.1 | 2.12 m/s | 26.5 | 29.4 | 4.27 m/s | 20.8 |  | 2.12 | m/s |  | 4.27 | m/s | 17.2367 | 0.00894 | 19.6184 |  | 0.5 | 515 | 0.515 | 38.094 | 7.251 | 6.1111 | 0.022612 | 51.8866 | 0.99255
2025-05-20 03:31 | 2066 | Remove | 2025-05-20 | 3:31 | ST | GS | - | 118 | g | 0 | 115.2 | 11.006 | 1073.5 | 4492 | 17:15 | 28 | 2.11 m/s | 28.1 | 29.4 | 4.29 m/s | 20.8 |  | 2.11 | m/s |  | 4.29 | m/s | 17.245 | 0.0089458 | 19.6273 |  | 0.5 | 515.5 | 0.5155 | 38.0744 | 7.6466 | 6.1111 | 0.023733 | 51.9103 | 0.99306
2025-05-20 03:32 | 2067 | Remove | 2025-05-20 | 3:32 | ST | GS | - | 119.5 | g | 0 | 115.1 | 11.021 | 1074.9 | 4501 | 17:15 | 28 | 2.06 m/s | 27 | 29.4 | 4.29 m/s | 20.2 |  | 2.06 | m/s |  | 4.29 | m/s | 17.2533 | 0.0089575 | 19.6363 |  | 1.5 | 517 | 0.517 | 37.9812 | 7.3473 | 5.9348 | 0.022264 | 51.9326 | 0.99552
2025-05-20 03:32 | 2068 | Remove | 2025-05-20 | 3:32 | ST | GS | - | 117.5 | g | 0 | 115.2 | 11.003 | 1072.7 | 4510 | 17:16 | 28 | 2.11 m/s | 27.9 | 29.3 | 4.24 m/s | 19.8 |  | 2.11 | m/s |  | 4.24 | m/s | 17.2619 | 0.0089392 | 19.6452 |  | -2 | 517 | 0.517 | 37.9985 | 7.5922 | 5.7857 | 0.023564 | 51.9562 | 0.99507
2025-05-20 03:33 | 2069 | Remove | 2025-05-20 | 3:33 | ST | GS | - | 118 | g | 0 | 115.2 | 10.998 | 1072.3 | 4519 | 17:16 | 28 | 2.11 m/s | 26.8 | 29.3 | 4.55 m/s | 21.1 |  | 2.11 | m/s |  | 4.55 | m/s | 17.2703 | 0.0089358 | 19.6542 |  | 0.5 | 517.5 | 0.5175 | 37.9791 | 7.2929 | 6.1656 | 0.022635 | 51.9788 | 0.9956
2025-05-20 03:33 | 2070 | Remove | 2025-05-20 | 3:33 | ST | GS | - | 119.5 | g | 0 | 115.2 | 11.058 | 1079.6 | 4528 | 17:17 | 28 | 2.08 m/s | 28 | 29.3 | 4.26 m/s | 20.9 |  | 2.08 | m/s |  | 4.26 | m/s | 17.2786 | 0.0089967 | 19.6632 |  | 1.5 | 519 | 0.519 | 37.8867 | 7.6194 | 6.1071 | 0.023312 | 52.0021 | 0.99804
2025-05-20 03:34 | 2071 | Keep | 2025-05-20 | 3:34 | ST | GS | - | 121.5 | g | 0 | 115.2 | 11.042 | 1078 | 4537 | 17:17 | 28.1 | 2.05 m/s | 28 | 29.3 | 4.23 m/s | 21.5 |  | 2.05 | m/s |  | 4.23 | m/s | 17.2869 | 0.0089833 | 19.6722 |  | 2 | 521 | 0.521 | 37.7585 | 7.6615 | 6.2825 | 0.023103 | 52.0252 | 1.0014
2025-05-20 03:34 | 2072 | Remove | 2025-05-20 | 3:34 | ST | GS | - | 118.5 | g | 0 | 115.1 | 11.075 | 1082.2 | 4546 | 17:18 | 28.1 | 2.11 m/s | 28 | 29.3 | 4.27 m/s | 20.5 |  | 2.11 | m/s |  | 4.27 | m/s | 17.2953 | 0.0090183 | 19.6812 |  | -3 | 521 | 0.521 | 37.7758 | 7.6615 | 5.9902 | 0.023779 | 52.049 | 1.001
2025-05-20 03:35 | 2073 | Remove | 2025-05-20 | 3:35 | ST | GS | - | 122.5 | g | 0 | 115.2 | 11.077 | 1082.7 | 4555 | 17:18 | 28.1 | 2.02 m/s | 29.1 | 29.4 | 4.32 m/s | 20.5 |  | 2.02 | m/s |  | 4.32 | m/s | 17.3036 | 0.0090225 | 19.6902 |  | 4 | 525 | 0.525 | 37.5051 | 7.9624 | 6.023 | 0.023659 | 52.0727 | 1.0082
2025-05-20 03:35 | 2074 | Remove | 2025-05-20 | 3:35 | ST | GS | - | 123 | g | 0 | 115.2 | 11.018 | 1074.8 | 4564 | 17:19 | 28.1 | 1.95 m/s | 27 | 29.4 | 4.27 m/s | 20 |  | 1.95 | m/s |  | 4.27 | m/s | 17.3119 | 0.0089567 | 19.6992 |  | 0.5 | 525.5 | 0.5255 | 37.4865 | 7.3878 | 5.8761 | 0.021191 | 52.0938 | 1.0088
2025-05-20 03:36 | 2075 | Remove | 2025-05-20 | 3:36 | US | GS | - | 120.5 | g | 0 | 115.2 | 11.029 | 1076 | 4573 | 17:19 | 28.1 | 1.95 m/s | 28.7 | 29.4 | 4.27 m/s | 22.3 |  | 1.95 | m/s |  | 4.27 | m/s | 17.3203 | 0.0089667 | 19.7081 |  | -2.5 | 525.5 | 0.5255 | 37.5036 | 7.853 | 6.5518 | 0.022525 | 52.1164 | 1.0083
2025-05-20 03:36 | 2076 | Remove | 2025-05-20 | 3:36 | ST | GS | - | 118 | g | 0 | 115.1 | 11.017 | 1074.3 | 4582 | 17:20 | 28.1 | 2.02 m/s | 31.3 | 29.4 | 4.27 m/s | 24.4 |  | 2.02 | m/s |  | 4.27 | m/s | 17.3286 | 0.0089525 | 19.7171 |  | -2.5 | 525.5 | 0.5255 | 37.5206 | 8.5644 | 7.1688 | 0.025448 | 52.1418 | 1.0078
2025-05-20 03:37 | 2077 | Remove | 2025-05-20 | 3:37 | ST | GS | - | 124.5 | g | 0 | 115.2 | 11.016 | 1073.7 | 4591 | 17:20 | 28.1 | 2.01 m/s | 29.4 | 29.4 | 4.27 m/s | 20.3 |  | 2.01 | m/s |  | 4.27 | m/s | 17.3369 | 0.0089475 | 19.726 |  | 6.5 | 532 | 0.532 | 37.079 | 8.0445 | 5.9642 | 0.023785 | 52.1656 | 1.0198
2025-05-20 03:37 | 2078 | Remove | 2025-05-20 | 3:37 | ST | GS | - | 120 | g | 0 | 115.1 | 11.06 | 1080.2 | 4600 | 17:21 | 28.1 | 2.11 m/s | 26.7 | 29.4 | 4.26 m/s | 20 |  | 2.11 | m/s |  | 4.26 | m/s | 17.3453 | 0.0090017 | 19.735 |  | -4.5 | 532 | 0.532 | 37.0959 | 7.3057 | 5.8761 | 0.022675 | 52.1883 | 1.0194
2025-05-20 03:38 | 2079 | Remove | 2025-05-20 | 3:38 | US | GS | - | 119 | g | 0 | 115.2 | 11.053 | 1078.5 | 4609 | 17:21 | 28.1 | 2.05 m/s | 28.1 | 29.4 | 4.27 m/s | 19.7 |  | 2.05 | m/s |  | 4.27 | m/s | 17.3536 | 0.0089875 | 19.744 |  | -1 | 532 | 0.532 | 37.1128 | 7.6888 | 5.7879 | 0.023185 | 52.2115 | 1.0189
2025-05-20 03:38 | 2080 | Remove | 2025-05-20 | 3:38 | ST | GS | - | 119 | g | 0 | 115.2 | 11.049 | 1078 | 4618 | 17:22 | 28.1 | 2.04 m/s | 26.8 | 29.4 | 4.27 m/s | 20.1 |  | 2.04 | m/s |  | 4.27 | m/s | 17.3619 | 0.0089833 | 19.753 |  | 0 | 532 | 0.532 | 37.1297 | 7.3331 | 5.9055 | 0.022005 | 52.2335 | 1.0185
2025-05-20 03:39 | 2081 | Remove | 2025-05-20 | 3:39 | ST | GS | - | 117.5 | g | 0 | 115.2 | 11.029 | 1076 | 4627 | 17:22 | 28.1 | 2.15 m/s | 27.7 | 29.4 | 4.29 m/s | 20.7 |  | 2.15 | m/s |  | 4.29 | m/s | 17.3703 | 0.0089667 | 19.762 |  | -1.5 | 532 | 0.532 | 37.1465 | 7.5794 | 6.0817 | 0.02397 | 52.2574 | 1.018
2025-05-20 03:39 | 2082 | Remove | 2025-05-20 | 3:39 | ST | GS | - | 118 | g | 0 | 115.3 | 11.007 | 1072.8 | 4636 | 17:23 | 28 | 2.12 m/s | 27.5 | 29.4 | 4.27 m/s | 21.1 |  | 2.12 | m/s |  | 4.27 | m/s | 17.3786 | 0.00894 | 19.7709 |  | 0.5 | 532.5 | 0.5325 | 37.1285 | 7.4833 | 6.1993 | 0.023336 | 52.2808 | 1.0185
2025-05-20 03:40 | 2083 | Remove | 2025-05-20 | 3:40 | ST | GS | - | 118 | g | 0 | 115.3 | 10.998 | 1071.9 | 4645 | 17:23 | 28 | 2.15 m/s | 26.8 | 29.3 | 4.24 m/s | 20.9 |  | 2.15 | m/s |  | 4.24 | m/s | 17.3869 | 0.0089325 | 19.7798 |  | 0 | 532.5 | 0.5325 | 37.1452 | 7.2929 | 6.1071 | 0.023064 | 52.3038 | 1.0181
2025-05-20 03:40 | 2084 | Remove | 2025-05-20 | 3:40 | ST | GS | - | 118 | g | 0 | 115.3 | 10.991 | 1070.1 | 4654 | 17:24 | 28 | 2.08 m/s | 27.4 | 29.3 | 4.32 m/s | 21.6 |  | 2.08 | m/s |  | 4.32 | m/s | 17.3953 | 0.0089175 | 19.7888 |  | 0 | 532.5 | 0.5325 | 37.162 | 7.4561 | 6.3117 | 0.022813 | 52.3266 | 1.0176
2025-05-20 03:41 | 2085 | Remove | 2025-05-20 | 3:41 | ST | GS | - | 118 | g | 0 | 115.3 | 10.98 | 1069.2 | 4663 | 17:24 | 28 | 2.12 m/s | 26.7 | 29.3 | 4.27 m/s | 21.1 |  | 2.12 | m/s |  | 4.27 | m/s | 17.4039 | 0.00891 | 19.7977 |  | 0 | 532.5 | 0.5325 | 37.1787 | 7.2657 | 6.1656 | 0.022658 | 52.3493 | 1.0172
2025-05-20 03:41 | 2086 | Remove | 2025-05-20 | 3:41 | ST | GS | - | 118 | g | 0 | 115.3 | 10.975 | 1068 | 4672 | 17:25 | 28 | 2.06 m/s | 29.7 | 29.3 | 4.24 m/s | 22 |  | 2.06 | m/s |  | 4.24 | m/s | 17.4122 | 0.0089 | 19.8066 |  | 0 | 532.5 | 0.5325 | 37.1954 | 8.082 | 6.4286 | 0.02449 | 52.3738 | 1.0167
2025-05-20 03:42 | 2087 | Remove | 2025-05-20 | 3:42 | ST | GS | - | 119 | g | 0 | 115.3 | 10.985 | 1069.8 | 4680 | 17:25 | 28 | 2.11 m/s | 27.1 | 29.3 | 4.27 m/s | 21.5 |  | 2.11 | m/s |  | 4.27 | m/s | 17.4206 | 0.008915 | 19.8155 |  | 1 | 533.5 | 0.5335 | 37.1424 | 7.3745 | 6.2825 | 0.022888 | 52.3967 | 1.0182
2025-05-20 03:42 | 2088 | Remove | 2025-05-20 | 3:42 | ST | GS | - | 118.5 | g | 0 | 115.3 | 10.977 | 1068.9 | 4689 | 17:26 | 28 | 2.05 m/s | 26.5 | 29.3 | 4.26 m/s | 20 |  | 2.05 | m/s |  | 4.26 | m/s | 17.4289 | 0.0089075 | 19.8244 |  | -0.5 | 533.5 | 0.5335 | 37.1591 | 7.2112 | 5.8441 | 0.021745 | 52.4184 | 1.0178
2025-05-20 03:43 | 2089 | Remove | 2025-05-20 | 3:43 | ST | GS | - | 118 | g | 0 | 115.2 | 10.979 | 1070.1 | 4698 | 17:26 | 28 | 2.11 m/s | 27.5 | 29.3 | 4.35 m/s | 20.4 |  | 2.11 | m/s |  | 4.35 | m/s | 17.4372 | 0.0089175 | 19.8333 |  | -0.5 | 533.5 | 0.5335 | 37.1758 | 7.4833 | 5.961 | 0.023226 | 52.4417 | 1.0173
2025-05-20 03:43 | 2090 | Remove | 2025-05-20 | 3:43 | US | GS | - | 117.5 | g | 0 | 115.3 | 11.008 | 1073.1 | 4707 | 17:27 | 28 | 2.02 m/s | 28.3 | 29.3 | 4.26 m/s | 21.2 |  | 2.02 | m/s |  | 4.26 | m/s | 17.4456 | 0.0089425 | 19.8422 |  | -0.5 | 533.5 | 0.5335 | 37.1926 | 7.701 | 6.1948 | 0.022882 | 52.4645 | 1.0169
2025-05-20 03:44 | 2091 | Remove | 2025-05-20 | 3:44 | ST | GS | - | 118 | g | 0 | 115.3 | 10.983 | 1069.8 | 4716 | 17:27 | 28 | 2.22 m/s | 28 | 29.3 | 4.24 m/s | 20.7 |  | 2.22 | m/s |  | 4.24 | m/s | 17.4539 | 0.008915 | 19.8512 |  | 0.5 | 534 | 0.534 | 37.1745 | 7.6194 | 6.0487 | 0.024881 | 52.4894 | 1.0173
2025-05-20 03:44 | 2092 | Remove | 2025-05-20 | 3:44 | ST | GS | - | 118 | g | 0 | 115.3 | 10.971 | 1067.2 | 4725 | 17:28 | 28 | 2.12 m/s | 27.4 | 29.3 | 4.27 m/s | 21.4 |  | 2.12 | m/s |  | 4.27 | m/s | 17.4622 | 0.0088933 | 19.8601 |  | 0 | 534 | 0.534 | 37.1911 | 7.4561 | 6.2532 | 0.023252 | 52.5127 | 1.0169
2025-05-20 03:45 | 2093 | Remove | 2025-05-20 | 3:45 | ST | GS | - | 118.5 | g | 0 | 115.3 | 10.966 | 1066.9 | 4734 | 17:28 | 28 | 2.09 m/s | 26.5 | 29.2 | 4.29 m/s | 20.7 |  | 2.09 | m/s |  | 4.29 | m/s | 17.4706 | 0.0088908 | 19.8689 |  | 0.5 | 534.5 | 0.5345 | 37.173 | 7.2112 | 6.0158 | 0.02217 | 52.5348 | 1.0174
2025-05-20 03:45 | 2094 | Remove | 2025-05-20 | 3:45 | ST | GS | - | 119 | g | 0 | 115.3 | 11.011 | 1072.7 | 4743 | 17:29 | 27.9 | 2.05 m/s | 27.5 | 29.2 | 4.23 m/s | 21 |  | 2.05 | m/s |  | 4.23 | m/s | 17.4789 | 0.0089392 | 19.8779 |  | 0.5 | 535 | 0.535 | 37.1549 | 7.4422 | 6.103 | 0.022442 | 52.5573 | 1.0179
2025-05-20 03:46 | 2095 | Remove | 2025-05-20 | 3:46 | ST | GS | - | 118.5 | g | 0 | 115.3 | 10.988 | 1070.7 | 4752 | 17:29 | 28 | 2.09 m/s | 27.3 | 29.2 | 4.32 m/s | 21.6 |  | 2.09 | m/s |  | 4.32 | m/s | 17.4872 | 0.0089225 | 19.8868 |  | -0.5 | 535 | 0.535 | 37.1716 | 7.4289 | 6.2773 | 0.022839 | 52.5801 | 1.0175
2025-05-20 03:46 | 2096 | Remove | 2025-05-20 | 3:46 | ST | GS | - | 118.5 | g | 0 | 115.4 | 10.965 | 1065.9 | 4761 | 17:30 | 27.9 | 2.09 m/s | 31.8 | 29.2 | 4.29 m/s | 22.9 |  | 2.09 | m/s |  | 4.29 | m/s | 17.4958 | 0.0088825 | 19.8957 |  | 0 | 535 | 0.535 | 37.1882 | 8.6059 | 6.6552 | 0.026457 | 52.6066 | 1.017
2025-05-20 03:47 | 2097 | Remove | 2025-05-20 | 3:47 | ST | GS | - | 118.5 | g | 0 | 115.4 | 10.976 | 1067.6 | 4770 | 17:30 | 27.9 | 2.15 m/s | 30.4 | 29.3 | 4.4 m/s | 22.5 |  | 2.15 | m/s |  | 4.4 | m/s | 17.5042 | 0.0088967 | 19.9046 |  | 0 | 535 | 0.535 | 37.2048 | 8.2271 | 6.5747 | 0.026019 | 52.6326 | 1.0165
2025-05-20 03:47 | 2098 | Remove | 2025-05-20 | 3:47 | ST | GS | - | 118.5 | g | 0 | 115.3 | 10.974 | 1068 | 4779 | 17:31 | 27.9 | 2.11 m/s | 30.1 | 29.2 | 4.27 m/s | 22.8 |  | 2.11 | m/s |  | 4.27 | m/s | 17.5125 | 0.0089 | 19.9135 |  | 0 | 535 | 0.535 | 37.2215 | 8.1459 | 6.6261 | 0.025283 | 52.6579 | 1.016
2025-05-20 03:48 | 2099 | Remove | 2025-05-20 | 3:48 | ST | GS | - | 119.5 | g | 0 | 115.3 | 10.96 | 1065.8 | 4788 | 17:31 | 27.9 | 2.11 m/s | 29.4 | 29.2 | 4.24 m/s | 22.3 |  | 2.11 | m/s |  | 4.24 | m/s | 17.5208 | 0.0088817 | 19.9224 |  | 1 | 536 | 0.536 | 37.1686 | 7.9564 | 6.4808 | 0.024695 | 52.6826 | 1.0174
2025-05-20 03:48 | 2100 | Remove | 2025-05-20 | 3:48 | ST | GS | - | 118.5 | g | 0 | 115.3 | 10.958 | 1066.1 | 4797 | 17:32 | 27.9 | 2.06 m/s | 29.9 | 29.2 | 4.24 m/s | 21.7 |  | 2.06 | m/s |  | 4.24 | m/s | 17.5292 | 0.0088842 | 19.9313 |  | -1 | 536 | 0.536 | 37.1852 | 8.0918 | 6.3064 | 0.02452 | 52.7071 | 1.0169
2025-05-20 03:49 | 2101 | Keep | 2025-05-20 | 3:49 | ST | GS | - | 119 | g | 0 | 115.3 | 10.965 | 1066.1 | 4806 | 17:32 | 27.9 | 2.11 m/s | 29.2 | 29.2 | 4.32 m/s | 22.5 |  | 2.11 | m/s |  | 4.32 | m/s | 17.5375 | 0.0088842 | 19.9401 |  | 0.5 | 536.5 | 0.5365 | 37.1671 | 7.9023 | 6.5389 | 0.024527 | 52.7316 | 1.0174
2025-05-20 03:49 | 2102 | Remove | 2025-05-20 | 3:49 | ST | GS | - | 118.5 | g | 0 | 115.3 | 10.954 | 1065.7 | 4815 | 17:33 | 27.9 | 2.15 m/s | 30.4 | 29.2 | 4.32 m/s | 22.9 |  | 2.15 | m/s |  | 4.32 | m/s | 17.5458 | 0.0088808 | 19.949 |  | -0.5 | 536.5 | 0.5365 | 37.1836 | 8.2271 | 6.6552 | 0.026019 | 52.7576 | 1.0169
2025-05-20 03:50 | 2103 | Remove | 2025-05-20 | 3:50 | ST | GS | - | 118.5 | g | 0 | 115.3 | 10.949 | 1064.4 | 4823 | 17:33 | 27.9 | 2.06 m/s | 32.4 | 29.2 | 4.29 m/s | 24.2 |  | 2.06 | m/s |  | 4.29 | m/s | 17.5542 | 0.00887 | 19.9579 |  | 0 | 536.5 | 0.5365 | 37.2002 | 8.7683 | 7.033 | 0.02657 | 52.7842 | 1.0164
2025-05-20 03:50 | 2104 | Remove | 2025-05-20 | 3:50 | ST | GS | - | 118.5 | g | 0 | 115.4 | 10.929 | 1061 | 4832 | 17:34 | 27.9 | 2.04 m/s | 32.2 | 29.2 | 4.26 m/s | 24.2 |  | 2.04 | m/s |  | 4.26 | m/s | 17.5625 | 0.0088417 | 19.9667 |  | 0 | 536.5 | 0.5365 | 37.2166 | 8.7142 | 7.033 | 0.026149 | 52.8104 | 1.0159
2025-05-20 03:51 | 2105 | Remove | 2025-05-20 | 3:51 | ST | GS | - | 119 | g | 0 | 115.4 | 10.935 | 1063.5 | 4841 | 17:34 | 27.9 | 2.13 m/s | 31.7 | 29.2 | 4.3 m/s | 23.9 |  | 2.13 | m/s |  | 4.3 | m/s | 17.5711 | 0.0088625 | 19.9756 |  | 0.5 | 537 | 0.537 | 37.1985 | 8.5789 | 6.9458 | 0.026879 | 52.8372 | 1.0163
2025-05-20 03:51 | 2106 | Remove | 2025-05-20 | 3:51 | ST | GS | - | 119 | g | 0 | 115.3 | 10.924 | 1060.7 | 4850 | 17:35 | 27.9 | 2.15 m/s | 30.7 | 29.2 | 4.29 m/s | 23.2 |  | 2.15 | m/s |  | 4.29 | m/s | 17.5794 | 0.0088392 | 19.9844 |  | 0 | 537 | 0.537 | 37.215 | 8.3083 | 6.7423 | 0.026275 | 52.8635 | 1.0158
2025-05-20 03:52 | 2107 | Remove | 2025-05-20 | 3:52 | ST | GS | - | 119.5 | g | 0 | 115.3 | 10.969 | 1067.3 | 4859 | 17:35 | 27.9 | 2.09 m/s | 29.6 | 29.2 | 4.24 m/s | 21.5 |  | 2.09 | m/s |  | 4.24 | m/s | 17.5878 | 0.0088942 | 19.9933 |  | 0.5 | 537.5 | 0.5375 | 37.1969 | 8.0106 | 6.2483 | 0.024627 | 52.8881 | 1.0163
2025-05-20 03:52 | 2108 | Remove | 2025-05-20 | 3:52 | ST | GS | - | 119 | g | 0 | 115.3 | 10.976 | 1067.8 | 4868 | 17:36 | 27.9 | 2.08 m/s | 30.5 | 29.2 | 4.26 m/s | 21.6 |  | 2.08 | m/s |  | 4.26 | m/s | 17.5961 | 0.0088983 | 20.0022 |  | -0.5 | 537.5 | 0.5375 | 37.2134 | 8.2541 | 6.2773 | 0.025254 | 52.9134 | 1.0158
2025-05-20 03:53 | 2109 | Remove | 2025-05-20 | 3:53 | ST | GS | - | 121.5 | g | 0 | 115.2 | 11.018 | 1073.7 | 4877 | 17:36 | 27.9 | 2.08 m/s | 30 | 29.2 | 4.32 m/s | 21.2 |  | 2.08 | m/s |  | 4.32 | m/s | 17.6044 | 0.0089475 | 20.0112 |  | 2.5 | 540 | 0.54 | 37.0577 | 8.1188 | 6.1611 | 0.02484 | 52.9382 | 1.0201
2025-05-20 03:53 | 2110 | Remove | 2025-05-20 | 3:53 | ST | GS | - | 119 | g | 0 | 115.3 | 10.966 | 1066 | 4886 | 17:37 | 27.9 | 2.13 m/s | 30.6 | 29.2 | 4.23 m/s | 23.9 |  | 2.13 | m/s |  | 4.23 | m/s | 17.6128 | 0.0088833 | 20.0201 |  | -2.5 | 540 | 0.54 | 37.0742 | 8.2812 | 6.9458 | 0.025946 | 52.9642 | 1.0196
2025-05-20 03:54 | 2111 | Remove | 2025-05-20 | 3:54 | ST | GS | - | 119 | g | 0 | 115.2 | 10.973 | 1067.6 | 4895 | 17:37 | 27.9 | 2.13 m/s | 31.1 | 29.2 | 4.29 m/s | 22 |  | 2.13 | m/s |  | 4.29 | m/s | 17.6211 | 0.0088967 | 20.0289 |  | 0 | 540 | 0.54 | 37.0906 | 8.4165 | 6.3936 | 0.02637 | 52.9906 | 1.019
2025-05-20 03:54 | 2112 | Remove | 2025-05-20 | 3:54 | ST | GS | - | 119 | g | 0 | 115.3 | 10.979 | 1068.5 | 4904 | 17:38 | 27.9 | 2.06 m/s | 29.1 | 29.2 | 4.27 m/s | 21.4 |  | 2.06 | m/s |  | 4.27 | m/s | 17.6294 | 0.0089042 | 20.0379 |  | 0 | 540 | 0.54 | 37.1071 | 7.8753 | 6.2192 | 0.023863 | 53.0144 | 1.0186
2025-05-20 03:55 | 2113 | Remove | 2025-05-20 | 3:55 | ST | GS | - | 119 | g | 0 | 115.3 | 10.953 | 1064.7 | 4913 | 17:38 | 27.9 | 2.12 m/s | 28.7 | 29.2 | 4.26 m/s | 21.8 |  | 2.12 | m/s |  | 4.26 | m/s | 17.6378 | 0.0088725 | 20.0467 |  | 0 | 540 | 0.54 | 37.1236 | 7.767 | 6.3355 | 0.024221 | 53.0386 | 1.0181
2025-05-20 03:55 | 2114 | Remove | 2025-05-20 | 3:55 | ST | GS | - | 119.5 | g | 0 | 115.2 | 10.936 | 1063.9 | 4921 | 17:39 | 27.9 | 2.08 m/s | 28.3 | 29.2 | 4.29 m/s | 21.6 |  | 2.08 | m/s |  | 4.29 | m/s | 17.6461 | 0.0088658 | 20.0556 |  | 0.5 | 540.5 | 0.5405 | 37.1056 | 7.6588 | 6.2773 | 0.023433 | 53.0621 | 1.0186
2025-05-20 03:56 | 2115 | Remove | 2025-05-20 | 3:56 | ST | GS | - | 119.5 | g | 0 | 115.3 | 10.929 | 1062.1 | 4930 | 17:39 | 27.9 | 2.11 m/s | 28.2 | 29.2 | 4.26 m/s | 22.8 |  | 2.11 | m/s |  | 4.26 | m/s | 17.6544 | 0.0088508 | 20.0644 |  | 0 | 540.5 | 0.5405 | 37.122 | 7.6317 | 6.6261 | 0.023687 | 53.0858 | 1.0182
2025-05-20 03:56 | 2116 | Remove | 2025-05-20 | 3:56 | ST | GS | - | 120 | g | 0 | 115.2 | 10.952 | 1065.2 | 4939 | 17:40 | 27.9 | 2.02 m/s | 28 | 29.2 | 4.24 m/s | 21.9 |  | 2.02 | m/s |  | 4.24 | m/s | 17.6628 | 0.0088767 | 20.0733 |  | 0.5 | 541 | 0.541 | 37.1041 | 7.5776 | 6.3645 | 0.022516 | 53.1083 | 1.0187
2025-05-20 03:57 | 2117 | Remove | 2025-05-20 | 3:57 | ST | GS | - | 119.5 | g | 0 | 115.2 | 10.984 | 1070.1 | 4948 | 17:40 | 27.9 | 2.02 m/s | 31.4 | 29.2 | 4.29 m/s | 21.9 |  | 2.02 | m/s |  | 4.29 | m/s | 17.6711 | 0.0089175 | 20.0822 |  | -0.5 | 541 | 0.541 | 37.1206 | 8.4977 | 6.3645 | 0.02525 | 53.1335 | 1.0182
2025-05-20 03:57 | 2118 | Remove | 2025-05-20 | 3:57 | ST | GS | - | 119.5 | g | 0 | 115.2 | 10.945 | 1064.1 | 4957 | 17:41 | 27.9 | 2.06 m/s | 29.6 | 29.2 | 4.24 m/s | 22.5 |  | 2.06 | m/s |  | 4.24 | m/s | 17.6794 | 0.0088675 | 20.0911 |  | 0 | 541 | 0.541 | 37.137 | 8.0106 | 6.5389 | 0.024274 | 53.1578 | 1.0177
2025-05-20 03:58 | 2119 | Remove | 2025-05-20 | 3:58 | ST | GS | - | 119.5 | g | 0 | 115.4 | 10.939 | 1062.8 | 4966 | 17:41 | 27.9 | 2.06 m/s | 29.6 | 29.2 | 4.27 m/s | 22.5 |  | 2.06 | m/s |  | 4.27 | m/s | 17.6878 | 0.0088567 | 20.1 |  | 0 | 541 | 0.541 | 37.1533 | 8.0106 | 6.5389 | 0.024274 | 53.1821 | 1.0173
2025-05-20 03:58 | 2120 | Remove | 2025-05-20 | 3:58 | ST | GS | - | 120.5 | g | 0 | 115.2 | 10.948 | 1065.3 | 4975 | 17:42 | 27.9 | 2.09 m/s | 30.1 | 29.2 | 4.26 m/s | 23 |  | 2.09 | m/s |  | 4.26 | m/s | 17.6961 | 0.0088775 | 20.1088 |  | 1 | 542 | 0.542 | 37.1012 | 8.1459 | 6.6842 | 0.025043 | 53.2071 | 1.0187
2025-05-20 03:59 | 2121 | Remove | 2025-05-20 | 3:59 | ST | GS | - | 120 | g | 0 | 115.3 | 10.926 | 1061.5 | 4984 | 17:42 | 27.9 | 2.04 m/s | 31.3 | 29.2 | 4.26 m/s | 23.2 |  | 2.04 | m/s |  | 4.26 | m/s | 17.7044 | 0.0088458 | 20.1177 |  | -0.5 | 542 | 0.542 | 37.1175 | 8.4706 | 6.7423 | 0.025418 | 53.2325 | 1.0182
2025-05-20 03:59 | 2122 | Remove | 2025-05-20 | 3:59 | ST | GS | - | 121.5 | g | 0 | 115.3 | 10.953 | 1065.5 | 4993 | 17:43 | 27.9 | 2.11 m/s | 30.3 | 29.2 | 4.27 m/s | 22.1 |  | 2.11 | m/s |  | 4.27 | m/s | 17.7131 | 0.0088792 | 20.1266 |  | 1.5 | 543.5 | 0.5435 | 37.0314 | 8.2 | 6.4227 | 0.025451 | 53.258 | 1.0205
2025-05-20 04:00 | 2123 | Remove | 2025-05-20 | 4:00 | ST | GS | - | 119.5 | g | 0 | 115.4 | 10.948 | 1064.7 | 5001 | 17:43 | 27.9 | 2.01 m/s | 31.6 | 29.2 | 4.29 m/s | 22.5 |  | 2.01 | m/s |  | 4.29 | m/s | 17.7214 | 0.0088725 | 20.1354 |  | -2 | 543.5 | 0.5435 | 37.0477 | 8.5518 | 6.5389 | 0.025285 | 53.2833 | 1.02
2025-05-20 04:00 | 2124 | Remove | 2025-05-20 | 4:00 | ST | GS | - | 119.5 | g | 0 | 115.3 | 10.923 | 1061 | 5010 | 17:44 | 27.9 | 2.11 m/s | 28.3 | 29.2 | 4.26 m/s | 22.3 |  | 2.11 | m/s |  | 4.26 | m/s | 17.7297 | 0.0088417 | 20.1443 |  | 0 | 543.5 | 0.5435 | 37.064 | 7.6588 | 6.4808 | 0.023771 | 53.307 | 1.0196
2025-05-20 04:01 | 2125 | Remove | 2025-05-20 | 4:01 | ST | GS | - | 120 | g | 0 | 115.3 | 10.934 | 1062.5 | 5019 | 17:44 | 27.9 | 2.09 m/s | 27.2 | 29.2 | 4.24 m/s | 22.7 |  | 2.09 | m/s |  | 4.24 | m/s | 17.7381 | 0.0088542 | 20.1531 |  | 0.5 | 544 | 0.544 | 37.0462 | 7.3611 | 6.597 | 0.02263 | 53.3297 | 1.0201
2025-05-20 04:01 | 2126 | Remove | 2025-05-20 | 4:01 | US | GS | - | 121.5 | g | 0 | 115.3 | 10.959 | 1066.6 | 5028 | 17:45 | 27.9 | 2.0 m/s | 28.4 | 29.1 | 4.32 m/s | 22 |  | 2 | m/s |  | 4.32 | m/s | 17.7464 | 0.0088883 | 20.162 |  | 1.5 | 545.5 | 0.5455 | 36.9606 | 7.6858 | 6.3588 | 0.022611 | 53.3523 | 1.0224
2025-05-20 04:02 | 2127 | Remove | 2025-05-20 | 4:02 | ST | GS | - | 119.5 | g | 0 | 115.2 | 10.971 | 1067.8 | 5037 | 17:45 | 27.9 | 2.06 m/s | 28.8 | 29.1 | 4.27 m/s | 21.8 |  | 2.06 | m/s |  | 4.27 | m/s | 17.7547 | 0.0088983 | 20.1709 |  | -2 | 545.5 | 0.5455 | 36.9769 | 7.7941 | 6.301 | 0.023617 | 53.3759 | 1.022
2025-05-20 04:02 | 2128 | Remove | 2025-05-20 | 4:02 | ST | GS | - | 120.5 | g | 0 | 115.3 | 10.978 | 1068.6 | 5046 | 17:46 | 27.9 | 2.11 m/s | 29.7 | 29.2 | 4.33 m/s | 22.1 |  | 2.11 | m/s |  | 4.33 | m/s | 17.7631 | 0.008905 | 20.1798 |  | 1 | 546.5 | 0.5465 | 36.9256 | 8.0376 | 6.4227 | 0.024947 | 53.4008 | 1.0234
2025-05-20 04:03 | 2129 | Remove | 2025-05-20 | 4:03 | ST | GS | - | 122 | g | 0 | 115.3 | 10.991 | 1071 | 5055 | 17:46 | 27.9 | 2.09 m/s | 28.6 | 29.2 | 4.27 m/s | 21 |  | 2.09 | m/s |  | 4.27 | m/s | 17.7714 | 0.008925 | 20.1887 |  | 1.5 | 548 | 0.548 | 36.8408 | 7.7399 | 6.103 | 0.023795 | 53.4246 | 1.0257
2025-05-20 04:03 | 2130 | Remove | 2025-05-20 | 4:03 | ST | GS | - | 119.5 | g | 0 | 115.2 | 10.982 | 1069.7 | 5064 | 17:47 | 27.9 | 2.06 m/s | 28.9 | 29.2 | 4.26 m/s | 21.2 |  | 2.06 | m/s |  | 4.26 | m/s | 17.7797 | 0.0089142 | 20.1977 |  | -2.5 | 548 | 0.548 | 36.857 | 7.8211 | 6.1611 | 0.023699 | 53.4483 | 1.0253
2025-05-20 04:04 | 2131 | Keep | 2025-05-20 | 4:04 | ST | GS | - | 120 | g | 0 | 115.2 | 10.948 | 1064.9 | 5073 | 17:47 | 27.9 | 2.12 m/s | 31.7 | 29.2 | 4.2 m/s | 22.8 |  | 2.12 | m/s |  | 4.2 | m/s | 17.7881 | 0.0088742 | 20.2065 |  | 0.5 | 548.5 | 0.5485 | 36.8396 | 8.5789 | 6.6261 | 0.026753 | 53.4751 | 1.0257
2025-05-20 04:04 | 2132 | Remove | 2025-05-20 | 4:04 | ST | GS | - | 119.5 | g | 0 | 115.3 | 10.944 | 1065.1 | 5082 | 17:48 | 27.9 | 2.05 m/s | 30.8 | 29.2 | 4.21 m/s | 22.3 |  | 2.05 | m/s |  | 4.21 | m/s | 17.7964 | 0.0088758 | 20.2154 |  | -0.5 | 548.5 | 0.5485 | 36.8558 | 8.3353 | 6.4808 | 0.025135 | 53.5002 | 1.0252
2025-05-20 04:05 | 2133 | Remove | 2025-05-20 | 4:05 | ST | GS | - | 119.5 | g | 0 | 115.2 | 10.989 | 1069.4 | 5091 | 17:48 | 27.9 | 2.05 m/s | 30.5 | 29.2 | 4.24 m/s | 22.2 |  | 2.05 | m/s |  | 4.24 | m/s | 17.8047 | 0.0089117 | 20.2243 |  | 0 | 548.5 | 0.5485 | 36.8721 | 8.2541 | 6.4517 | 0.02489 | 53.5251 | 1.0248
2025-05-20 04:05 | 2134 | Remove | 2025-05-20 | 4:05 | ST | GS | - | 120.5 | g | 0 | 115.3 | 10.954 | 1065 | 5099 | 17:49 | 27.9 | 1.98 m/s | 28.7 | 29.2 | 4.24 m/s | 21.4 |  | 1.98 | m/s |  | 4.24 | m/s | 17.8131 | 0.008875 | 20.2332 |  | 1 | 549.5 | 0.5495 | 36.8211 | 7.767 | 6.2192 | 0.022621 | 53.5477 | 1.0262
2025-05-20 04:06 | 2135 | Remove | 2025-05-20 | 4:06 | US | GS | - | 125 | g | 0 | 115.2 | 10.947 | 1064.8 | 5108 | 17:49 | 27.9 | 2.11 m/s | 28.7 | 29.2 | 4.29 m/s | 21.3 |  | 2.11 | m/s |  | 4.29 | m/s | 17.8214 | 0.0088733 | 20.2421 |  | 4.5 | 554 | 0.554 | 36.538 | 7.767 | 6.1902 | 0.024107 | 53.5718 | 1.0341
2025-05-20 04:06 | 2136 | Remove | 2025-05-20 | 4:06 | ST | GS | - | 121 | g | 0 | 115.2 | 10.946 | 1064.9 | 5117 | 17:50 | 27.9 | 2.09 m/s | 29.5 | 29.2 | 4.21 m/s | 21 |  | 2.09 | m/s |  | 4.21 | m/s | 17.8297 | 0.0088742 | 20.2509 |  | -4 | 554 | 0.554 | 36.5541 | 7.9835 | 6.103 | 0.024544 | 53.5964 | 1.0337
2025-05-20 04:07 | 2137 | Remove | 2025-05-20 | 4:07 | ST | GS | - | 120 | g | 0 | 115.2 | 10.926 | 1061.9 | 5126 | 17:50 | 27.9 | 2.12 m/s | 28.2 | 29.2 | 4.29 m/s | 22.1 |  | 2.12 | m/s |  | 4.29 | m/s | 17.8381 | 0.0088492 | 20.2598 |  | -1 | 554 | 0.554 | 36.57 | 7.6317 | 6.4227 | 0.023799 | 53.6202 | 1.0332
2025-05-20 04:07 | 2138 | Remove | 2025-05-20 | 4:07 | ST | GS | - | 120 | g | 0 | 115.2 | 10.916 | 1060 | 5135 | 17:51 | 27.9 | 2.19 m/s | 28.2 | 29.2 | 4.27 m/s | 22.7 |  | 2.19 | m/s |  | 4.27 | m/s | 17.8464 | 0.0088333 | 20.2686 |  | 0 | 554 | 0.554 | 36.586 | 7.6317 | 6.597 | 0.024585 | 53.6448 | 1.0327
2025-05-20 04:08 | 2139 | Remove | 2025-05-20 | 4:08 | ST | GS | - | 122.5 | g | 0 | 115.2 | 10.951 | 1065.2 | 5144 | 17:51 | 27.9 | 2.09 m/s | 28 | 29.2 | 4.27 m/s | 21.2 |  | 2.09 | m/s |  | 4.27 | m/s | 17.855 | 0.0088767 | 20.2775 |  | 2.5 | 556.5 | 0.5565 | 36.4376 | 7.5776 | 6.1611 | 0.023296 | 53.6681 | 1.0369
2025-05-20 04:08 | 2140 | Remove | 2025-05-20 | 4:08 | ST | GS | - | 123.5 | g | 0 | 115.2 | 10.981 | 1068.9 | 5153 | 17:52 | 27.9 | 2.09 m/s | 28.9 | 29.2 | 4.26 m/s | 21.4 |  | 2.09 | m/s |  | 4.26 | m/s | 17.8633 | 0.0089075 | 20.2864 |  | 1 | 557.5 | 0.5575 | 36.3882 | 7.8211 | 6.2192 | 0.024045 | 53.6921 | 1.0383
2025-05-20 04:09 | 2141 | Remove | 2025-05-20 | 4:09 | US | GS | - | 122.5 | g | 0 | 115.2 | 10.974 | 1068.9 | 5162 | 17:52 | 27.9 | 2.05 m/s | 27.4 | 29.2 | 4.26 m/s | 20.6 |  | 2.05 | m/s |  | 4.26 | m/s | 17.8717 | 0.0089075 | 20.2953 |  | -1 | 557.5 | 0.5575 | 36.4042 | 7.4152 | 5.9867 | 0.02236 | 53.7145 | 1.0379
2025-05-20 04:10 | 2142 | Remove | 2025-05-20 | 4:10 | US | GS | - | 122 | g | 0 | 115.2 | 10.986 | 1069.4 | 5171 | 17:53 | 27.9 | 1.98 m/s | 29.7 | 29.2 | 4.3 m/s | 22.6 |  | 1.98 | m/s |  | 4.3 | m/s | 17.88 | 0.0089117 | 20.3042 |  | -0.5 | 557.5 | 0.5575 | 36.4201 | 8.0376 | 6.568 | 0.02341 | 53.7379 | 1.0374
2025-05-20 04:10 | 2143 | Remove | 2025-05-20 | 4:10 | ST | GS | - | 120 | g | 0 | 115.2 | 10.981 | 1068.8 | 5180 | 17:53 | 27.9 | 2.02 m/s | 28.7 | 29.2 | 4.26 m/s | 22.7 |  | 2.02 | m/s |  | 4.26 | m/s | 17.8883 | 0.0089067 | 20.3131 |  | -2 | 557.5 | 0.5575 | 36.4361 | 7.767 | 6.597 | 0.023078 | 53.761 | 1.037
2025-05-20 04:10 | 2144 | Remove | 2025-05-20 | 4:10 | ST | GS | - | 121 | g | 0 | 115.1 | 11.009 | 1072.8 | 5189 | 17:54 | 27.9 | 2.04 m/s | 30 | 29.2 | 4.24 m/s | 21.7 |  | 2.04 | m/s |  | 4.24 | m/s | 17.8967 | 0.00894 | 20.3221 |  | 1 | 558.5 | 0.5585 | 36.3869 | 8.1188 | 6.3064 | 0.024363 | 53.7853 | 1.0384
2025-05-20 04:11 | 2145 | Remove | 2025-05-20 | 4:11 | ST | GS | - | 119.5 | g | 0 | 115.2 | 10.979 | 1067.9 | 5198 | 17:54 | 27.9 | 2.05 m/s | 29.6 | 29.2 | 4.26 m/s | 22 |  | 2.05 | m/s |  | 4.26 | m/s | 17.905 | 0.0088992 | 20.331 |  | -1.5 | 558.5 | 0.5585 | 36.4028 | 8.0106 | 6.3936 | 0.024156 | 53.8095 | 1.0379
2025-05-20 04:12 | 2146 | Remove | 2025-05-20 | 4:12 | ST | GS | - | 120.5 | g | 0 | 115.3 | 10.946 | 1064.5 | 5207 | 17:55 | 27.9 | 2.0 m/s | 30.2 | 29.2 | 4.26 m/s | 21.8 |  | 2 | m/s |  | 4.26 | m/s | 17.9133 | 0.0088708 | 20.3398 |  | 1 | 559.5 | 0.5595 | 36.3536 | 8.1729 | 6.3355 | 0.024044 | 53.8335 | 1.0393
2025-05-20 04:12 | 2147 | Remove | 2025-05-20 | 4:12 | ST | GS | - | 120.5 | g | 0 | 115.1 | 10.919 | 1060.6 | 5215 | 17:55 | 27.9 | 2.09 m/s | 27.7 | 29.2 | 4.3 m/s | 22.2 |  | 2.09 | m/s |  | 4.3 | m/s | 17.9217 | 0.0088383 | 20.3487 |  | 0 | 559.5 | 0.5595 | 36.3694 | 7.4964 | 6.4517 | 0.023046 | 53.8566 | 1.0389
2025-05-20 04:12 | 2148 | Remove | 2025-05-20 | 4:12 | ST | GS | - | 120.5 | g | 0 | 115.2 | 10.95 | 1064.9 | 5224 | 17:56 | 27.9 | 2.11 m/s | 29.7 | 29.2 | 4.21 m/s | 21.3 |  | 2.11 | m/s |  | 4.21 | m/s | 17.93 | 0.0088742 | 20.3576 |  | 0 | 559.5 | 0.5595 | 36.3853 | 8.0376 | 6.1902 | 0.024947 | 53.8815 | 1.0384
2025-05-20 04:13 | 2149 | Remove | 2025-05-20 | 4:13 | ST | GS | - | 120.5 | g | 0 | 115.2 | 10.96 | 1066 | 5233 | 17:56 | 27.9 | 2.04 m/s | 29.3 | 29.2 | 4.29 m/s | 21.2 |  | 2.04 | m/s |  | 4.29 | m/s | 17.9383 | 0.0088833 | 20.3664 |  | 0 | 559.5 | 0.5595 | 36.4012 | 7.9294 | 6.1611 | 0.023794 | 53.9053 | 1.0379
2025-05-20 04:14 | 2150 | Remove | 2025-05-20 | 4:14 | ST | GS | - | 121.5 | g | 0 | 115.1 | 10.984 | 1070.4 | 5242 | 17:57 | 27.9 | 2.18 m/s | 30.3 | 29.2 | 4.24 m/s | 20.8 |  | 2.18 | m/s |  | 4.24 | m/s | 17.9467 | 0.00892 | 20.3754 |  | 1 | 560.5 | 0.5605 | 36.3521 | 8.2 | 6.0449 | 0.026295 | 53.9316 | 1.0393
2025-05-20 04:14 | 2151 | Remove | 2025-05-20 | 4:14 | ST | GS | - | 124 | g | 0 | 115.1 | 10.986 | 1069.4 | 5251 | 17:57 | 27.9 | 2.05 m/s | 27.9 | 29.2 | 4.23 m/s | 20 |  | 2.05 | m/s |  | 4.23 | m/s | 17.955 | 0.0089117 | 20.3843 |  | 2.5 | 563 | 0.563 | 36.2065 | 7.5505 | 5.8124 | 0.022768 | 53.9544 | 1.0435
2025-05-20 04:14 | 2152 | Remove | 2025-05-20 | 4:15 | ST | GS | - | 121 | g | 0 | 115 | 10.954 | 1066.7 | 5260 | 17:58 | 27.9 | 2.15 m/s | 28.5 | 29.2 | 4.24 m/s | 20.9 |  | 2.15 | m/s |  | 4.24 | m/s | 17.9633 | 0.0088892 | 20.3932 |  | -3 | 563 | 0.563 | 36.2223 | 7.7129 | 6.0739 | 0.024393 | 53.9788 | 1.043
2025-05-20 04:15 | 2153 | Remove | 2025-05-20 | 4:15 | ST | GS | - | 122.5 | g | 0 | 115.2 | 10.929 | 1062.8 | 5269 | 17:58 | 27.9 | 2.06 m/s | 28.7 | 29.2 | 4.24 m/s | 20.8 |  | 2.06 | m/s |  | 4.24 | m/s | 17.9717 | 0.0088567 | 20.402 |  | 1.5 | 564.5 | 0.5645 | 36.1418 | 7.767 | 6.0449 | 0.023535 | 54.0023 | 1.0453
2025-05-20 04:16 | 2154 | Remove | 2025-05-20 | 4:16 | ST | GS | - | 124 | g | 0 | 115.2 | 10.997 | 1071.4 | 5278 | 17:59 | 27.9 | 2.08 m/s | 27.4 | 29.2 | 4.26 m/s | 19.5 |  | 2.08 | m/s |  | 4.26 | m/s | 17.98 | 0.0089283 | 20.411 |  | 1.5 | 566 | 0.566 | 36.0618 | 7.4152 | 5.6671 | 0.022688 | 54.025 | 1.0477
2025-05-20 04:16 | 2155 | Remove | 2025-05-20 | 4:16 | ST | GS | - | 123 | g | 0 | 115.1 | 10.978 | 1068.6 | 5287 | 17:59 | 27.9 | 2.04 m/s | 27 | 29.2 | 4.33 m/s | 20 |  | 2.04 | m/s |  | 4.33 | m/s | 17.9883 | 0.008905 | 20.4199 |  | -1 | 566 | 0.566 | 36.0775 | 7.3069 | 5.8124 | 0.021926 | 54.0469 | 1.0472
2025-05-20 04:16 | 2156 | Remove | 2025-05-20 | 4:16 | ST | GS | - | 121.5 | g | 0 | 115.1 | 10.995 | 1071.1 | 5296 | 18:00 | 28 | 2.15 m/s | 27.2 | 29.2 | 4.29 m/s | 20 |  | 2.15 | m/s |  | 4.29 | m/s | 17.9967 | 0.0089258 | 20.4288 |  | -1.5 | 566 | 0.566 | 36.0933 | 7.4017 | 5.8124 | 0.023408 | 54.0703 | 1.0468
2025-05-20 04:17 | 2157 | Remove | 2025-05-20 | 4:17 | ST | GS | - | 119.5 | g | 0 | 115.1 | 11.009 | 1072.9 | 5305 | 18:00 | 28 | 2.12 m/s | 26.8 | 29.2 | 4.26 m/s | 20.4 |  | 2.12 | m/s |  | 4.26 | m/s | 18.0053 | 0.0089408 | 20.4377 |  | -2 | 566 | 0.566 | 36.1091 | 7.2929 | 5.9286 | 0.022742 | 54.0931 | 1.0463
2025-05-20 04:18 | 2158 | Remove | 2025-05-20 | 4:18 | ST | GS | - | 120 | g | 0 | 115.1 | 11.009 | 1073.1 | 5314 | 18:01 | 28 | 2.06 m/s | 27 | 29.2 | 4.52 m/s | 19.4 |  | 2.06 | m/s |  | 4.52 | m/s | 18.0136 | 0.0089425 | 20.4467 |  | 0.5 | 566.5 | 0.5665 | 36.093 | 7.3473 | 5.638 | 0.022264 | 54.1153 | 1.0468
2025-05-20 04:18 | 2159 | Remove | 2025-05-20 | 4:18 | ST | GS | - | 123.5 | g | 0 | 115.1 | 11.021 | 1074.9 | 5323 | 18:01 | 28 | 2.04 m/s | 26 | 29.3 | 4.44 m/s | 19.5 |  | 2.04 | m/s |  | 4.44 | m/s | 18.0219 | 0.0089575 | 20.4556 |  | 3.5 | 570 | 0.57 | 35.8871 | 7.0752 | 5.698 | 0.021231 | 54.1366 | 1.0529
2025-05-20 04:19 | 2160 | Remove | 2025-05-20 | 4:19 | ST | GS | - | 121.5 | g | 0 | 115.1 | 11.024 | 1074.7 | 5332 | 18:02 | 28 | 2.11 m/s | 26 | 29.3 | 4.24 m/s | 19.3 |  | 2.11 | m/s |  | 4.24 | m/s | 18.0303 | 0.0089558 | 20.4646 |  | -2 | 570 | 0.57 | 35.9028 | 7.0752 | 5.6396 | 0.021959 | 54.1585 | 1.0525
2025-05-20 04:19 | 2161 | Keep | 2025-05-20 | 4:19 | ST | GS | - | 122 | g | 0 | 115.1 | 11.034 | 1076.1 | 5341 | 18:02 | 28 | 2.08 m/s | 26.2 | 29.3 | 4.27 m/s | 19.4 |  | 2.08 | m/s |  | 4.27 | m/s | 18.0386 | 0.0089675 | 20.4735 |  | 0.5 | 570.5 | 0.5705 | 35.887 | 7.1296 | 5.6688 | 0.021814 | 54.1803 | 1.053
2025-05-20 04:20 | 2162 | Remove | 2025-05-20 | 4:20 | ST | GS | - | 123.5 | g | 0 | 115.1 | 11.023 | 1074.5 | 5350 | 18:03 | 28 | 2.15 m/s | 25.9 | 29.3 | 4.27 m/s | 19.5 |  | 2.15 | m/s |  | 4.27 | m/s | 18.0469 | 0.0089542 | 20.4825 |  | 1.5 | 572 | 0.572 | 35.8086 | 7.048 | 5.698 | 0.02229 | 54.2026 | 1.0553
2025-05-20 04:20 | 2163 | Remove | 2025-05-20 | 4:20 | ST | GS | - | 122 | g | 0 | 115.1 | 11.025 | 1075.6 | 5359 | 18:03 | 28.1 | 2.05 m/s | 26 | 29.3 | 4.49 m/s | 19.3 |  | 2.05 | m/s |  | 4.49 | m/s | 18.0553 | 0.0089633 | 20.4915 |  | -1.5 | 572 | 0.572 | 35.8242 | 7.1142 | 5.6396 | 0.021453 | 54.2241 | 1.0549
2025-05-20 04:21 | 2164 | Remove | 2025-05-20 | 4:21 | ST | GS | - | 122.5 | g | 0 | 115.1 | 11.029 | 1076.7 | 5368 | 18:04 | 28.1 | 2.08 m/s | 25.8 | 29.3 | 4.36 m/s | 19.1 |  | 2.08 | m/s |  | 4.36 | m/s | 18.0636 | 0.0089725 | 20.5004 |  | 0.5 | 572.5 | 0.5725 | 35.8086 | 7.0595 | 5.5812 | 0.021599 | 54.2457 | 1.0554
2025-05-20 04:21 | 2165 | Remove | 2025-05-20 | 4:21 | US | GS | - | 122 | g | 0 | 115.1 | 11.019 | 1074.9 | 5377 | 18:04 | 28.1 | 2.18 m/s | 25.5 | 29.3 | 4.29 m/s | 19 |  | 2.18 | m/s |  | 4.29 | m/s | 18.0719 | 0.0089575 | 20.5094 |  | -0.5 | 572.5 | 0.5725 | 35.8243 | 6.9774 | 5.5519 | 0.022374 | 54.268 | 1.0549
2025-05-20 04:22 | 2166 | Remove | 2025-05-20 | 4:22 | ST | GS | - | 120.5 | g | 0 | 115.1 | 10.992 | 1071.2 | 5385 | 18:05 | 28.1 | 2.05 m/s | 25.4 | 29.3 | 4.21 m/s | 19.1 |  | 2.05 | m/s |  | 4.21 | m/s | 18.0803 | 0.0089267 | 20.5183 |  | -1.5 | 572.5 | 0.5725 | 35.8399 | 6.95 | 5.5812 | 0.020958 | 54.289 | 1.0545
2025-05-20 04:22 | 2167 | Remove | 2025-05-20 | 4:22 | ST | GS | - | 124 | g | 0 | 115.1 | 11.003 | 1072.2 | 5394 | 18:05 | 28 | 2.08 m/s | 26.3 | 29.3 | 4.24 m/s | 20.1 |  | 2.08 | m/s |  | 4.24 | m/s | 18.0886 | 0.008935 | 20.5273 |  | 3.5 | 576 | 0.576 | 35.6376 | 7.1568 | 5.8734 | 0.021897 | 54.3109 | 1.0606
2025-05-20 04:23 | 2168 | Remove | 2025-05-20 | 4:23 | ST | GS | - | 121.5 | g | 0 | 115.1 | 11.013 | 1074.2 | 5403 | 18:06 | 28 | 2.16 m/s | 26.1 | 29.3 | 4.29 m/s | 19.2 |  | 2.16 | m/s |  | 4.29 | m/s | 18.0969 | 0.0089517 | 20.5362 |  | -2.5 | 576 | 0.576 | 35.6531 | 7.1024 | 5.6104 | 0.022566 | 54.3335 | 1.0601
2025-05-20 04:23 | 2169 | Remove | 2025-05-20 | 4:23 | ST | GS | - | 123.5 | g | 0 | 115.1 | 10.999 | 1071.8 | 5412 | 18:06 | 28 | 1.98 m/s | 26 | 29.3 | 4.56 m/s | 19.7 |  | 1.98 | m/s |  | 4.56 | m/s | 18.1053 | 0.0089317 | 20.5451 |  | 2 | 578 | 0.578 | 35.5452 | 7.0752 | 5.7565 | 0.020606 | 54.3541 | 1.0634
2025-05-20 04:24 | 2170 | Remove | 2025-05-20 | 4:24 | ST | GS | - | 122.5 | g | 0 | 115.1 | 11.011 | 1074.1 | 5421 | 18:07 | 28 | 2.13 m/s | 26.1 | 29.3 | 4.35 m/s | 19.7 |  | 2.13 | m/s |  | 4.35 | m/s | 18.1136 | 0.0089508 | 20.5541 |  | -1 | 578 | 0.578 | 35.5607 | 7.1024 | 5.7565 | 0.022253 | 54.3763 | 1.063
2025-05-20 04:24 | 2171 | Remove | 2025-05-20 | 4:24 | ST | GS | - | 121.5 | g | 0 | 115 | 11.02 | 1074.3 | 5430 | 18:07 | 28 | 2.06 m/s | 26.8 | 29.3 | 4.32 m/s | 20 |  | 2.06 | m/s |  | 4.32 | m/s | 18.1219 | 0.0089525 | 20.563 |  | -1 | 578 | 0.578 | 35.5762 | 7.2929 | 5.8441 | 0.022099 | 54.3984 | 1.0625
2025-05-20 04:25 | 2172 | Remove | 2025-05-20 | 4:25 | ST | GS | - | 120.5 | g | 0 | 115.2 | 11.009 | 1072.7 | 5439 | 18:08 | 28 | 2.04 m/s | 26.4 | 29.3 | 4.33 m/s | 20 |  | 2.04 | m/s |  | 4.33 | m/s | 18.1303 | 0.0089392 | 20.572 |  | -1 | 578 | 0.578 | 35.5917 | 7.184 | 5.8441 | 0.021558 | 54.42 | 1.0621
2025-05-20 04:25 | 2173 | Remove | 2025-05-20 | 4:25 | ST | GS | - | 121 | g | 0 | 115.8 | 11.038 | 1075.3 | 5448 | 18:08 | 28 | 2.05 m/s | 26.9 | 29.3 | 4.29 m/s | 19.5 |  | 2.05 | m/s |  | 4.29 | m/s | 18.1386 | 0.0089608 | 20.5809 |  | 0.5 | 578.5 | 0.5785 | 35.5764 | 7.3201 | 5.698 | 0.022074 | 54.4421 | 1.0626
2025-05-20 04:26 | 2174 | Remove | 2025-05-20 | 4:26 | ST | GS | - | 122 | g | 0 | 115.8 | 11.037 | 1075.3 | 5457 | 18:09 | 28 | 2.08 m/s | 26.1 | 29.3 | 4.27 m/s | 19.6 |  | 2.08 | m/s |  | 4.27 | m/s | 18.1472 | 0.0089608 | 20.5899 |  | 1 | 579.5 | 0.5795 | 35.5305 | 7.1024 | 5.7273 | 0.02173 | 54.4638 | 1.064
2025-05-20 04:26 | 2175 | Remove | 2025-05-20 | 4:26 | US | GS | - | 123 | g | 0 | 115.9 | 11.041 | 1074.8 | 5466 | 18:09 | 28 | 2.09 m/s | 26.3 | 29.3 | 4.3 m/s | 19.7 |  | 2.09 | m/s |  | 4.3 | m/s | 18.1556 | 0.0089567 | 20.5989 |  | 1 | 580.5 | 0.5805 | 35.4847 | 7.1568 | 5.7565 | 0.022002 | 54.4858 | 1.0654
2025-05-20 04:27 | 2176 | Remove | 2025-05-20 | 4:27 | ST | GS | - | 121.5 | g | 0 | 115.9 | 11.032 | 1072.9 | 5475 | 18:10 | 28 | 2.12 m/s | 27.3 | 29.3 | 4.32 m/s | 19.7 |  | 2.12 | m/s |  | 4.32 | m/s | 18.1639 | 0.0089408 | 20.6078 |  | -1.5 | 580.5 | 0.5805 | 35.5001 | 7.4289 | 5.7565 | 0.023167 | 54.509 | 1.065
2025-05-20 04:27 | 2177 | Remove | 2025-05-20 | 4:27 | ST | GS | - | 123 | g | 0 | 115.9 | 11.007 | 1071 | 5484 | 18:10 | 28 | 2.04 m/s | 27.2 | 29.3 | 4.38 m/s | 20.4 |  | 2.04 | m/s |  | 4.38 | m/s | 18.1722 | 0.008925 | 20.6167 |  | 1.5 | 582 | 0.582 | 35.4239 | 7.4017 | 5.961 | 0.022211 | 54.5312 | 1.0673
2025-05-20 04:28 | 2178 | Remove | 2025-05-20 | 4:28 | ST | GS | - | 123 | g | 0 | 115.9 | 11.051 | 1076.7 | 5493 | 18:11 | 28 | 2.09 m/s | 27.5 | 29.3 | 4.4 m/s | 19.8 |  | 2.09 | m/s |  | 4.4 | m/s | 18.1806 | 0.0089725 | 20.6257 |  | 0 | 582 | 0.582 | 35.4393 | 7.4833 | 5.7857 | 0.023006 | 54.5542 | 1.0668
2025-05-20 04:28 | 2179 | Remove | 2025-05-20 | 4:28 | ST | GS | - | 122.5 | g | 0 | 115.9 | 11.048 | 1076.2 | 5502 | 18:11 | 28 | 2.12 m/s | 26.3 | 29.3 | 4.47 m/s | 20 |  | 2.12 | m/s |  | 4.47 | m/s | 18.1889 | 0.0089683 | 20.6347 |  | -0.5 | 582 | 0.582 | 35.4548 | 7.1568 | 5.8441 | 0.022318 | 54.5765 | 1.0664
2025-05-20 04:29 | 2180 | Remove | 2025-05-20 | 4:29 | ST | GS | - | 121.5 | g | 0 | 115.8 | 11.044 | 1076.4 | 5511 | 18:12 | 28 | 2.08 m/s | 26.5 | 29.3 | 4.23 m/s | 20 |  | 2.08 | m/s |  | 4.23 | m/s | 18.1972 | 0.00897 | 20.6436 |  | -1 | 582 | 0.582 | 35.4702 | 7.2112 | 5.8441 | 0.022064 | 54.5986 | 1.066
2025-05-20 04:29 | 2181 | Remove | 2025-05-20 | 4:29 | ST | GS | - | 121.5 | g | 0 | 115.8 | 11.042 | 1075.6 | 5520 | 18:12 | 28 | 2.08 m/s | 27.1 | 29.3 | 4.4 m/s | 19.7 |  | 2.08 | m/s |  | 4.4 | m/s | 18.2056 | 0.0089633 | 20.6526 |  | 0 | 582 | 0.582 | 35.4856 | 7.3745 | 5.7565 | 0.022563 | 54.6211 | 1.0655
2025-05-20 04:30 | 2182 | Remove | 2025-05-20 | 4:30 | US | GS | - | 121.5 | g | 0 | 115.8 | 11.057 | 1077.3 | 5529 | 18:13 | 28 | 2.15 m/s | 26.3 | 29.3 | 4.32 m/s | 19.6 |  | 2.15 | m/s |  | 4.32 | m/s | 18.2139 | 0.0089775 | 20.6616 |  | 0 | 582 | 0.582 | 35.501 | 7.1568 | 5.7273 | 0.022634 | 54.6438 | 1.0651
2025-05-20 04:30 | 2183 | Remove | 2025-05-20 | 4:30 | ST | GS | - | 124 | g | 0 | 115.7 | 11.053 | 1077.2 | 5538 | 18:13 | 28 | 2.05 m/s | 26.3 | 29.3 | 4.35 m/s | 19.8 |  | 2.05 | m/s |  | 4.35 | m/s | 18.2222 | 0.0089767 | 20.6706 |  | 2.5 | 584.5 | 0.5845 | 35.3645 | 7.1568 | 5.7857 | 0.021581 | 54.6653 | 1.0692
2025-05-20 04:31 | 2184 | Remove | 2025-05-20 | 4:31 | US | GS | - | 122.5 | g | 0 | 115.8 | 11.062 | 1077.4 | 5547 | 18:14 | 28 | 2.08 m/s | 28.1 | 29.3 | 4.43 m/s | 20 |  | 2.08 | m/s |  | 4.43 | m/s | 18.2306 | 0.0089783 | 20.6795 |  | -1.5 | 584.5 | 0.5845 | 35.3799 | 7.6466 | 5.8441 | 0.023396 | 54.6887 | 1.0688
2025-05-20 04:31 | 2185 | Remove | 2025-05-20 | 4:31 | ST | GS | - | 123 | g | 0 | 115.8 | 11.033 | 1073.7 | 5556 | 18:14 | 28 | 2.15 m/s | 26.6 | 29.3 | 4.32 m/s | 19.6 |  | 2.15 | m/s |  | 4.32 | m/s | 18.2389 | 0.0089475 | 20.6885 |  | 0.5 | 585 | 0.585 | 35.3649 | 7.2384 | 5.7273 | 0.022892 | 54.7116 | 1.0692
2025-05-20 04:32 | 2186 | Remove | 2025-05-20 | 4:32 | ST | GS | - | 122 | g | 0 | 115.8 | 10.992 | 1068.1 | 5565 | 18:15 | 28 | 2.02 m/s | 26.8 | 29.3 | 4.24 m/s | 20.2 |  | 2.02 | m/s |  | 4.24 | m/s | 18.2472 | 0.0089008 | 20.6974 |  | -1 | 585 | 0.585 | 35.3801 | 7.2929 | 5.9026 | 0.02167 | 54.7333 | 1.0688
2025-05-20 04:32 | 2187 | Remove | 2025-05-20 | 4:32 | ST | GS | - | 125 | g | 0 | 115.9 | 11.036 | 1075.2 | 5574 | 18:15 | 28 | 2.08 m/s | 27 | 29.3 | 4.3 m/s | 19.7 |  | 2.08 | m/s |  | 4.3 | m/s | 18.2556 | 0.00896 | 20.7063 |  | 3 | 588 | 0.588 | 35.2149 | 7.3473 | 5.7565 | 0.02248 | 54.7558 | 1.0739
2025-05-20 04:33 | 2188 | Remove | 2025-05-20 | 4:33 | ST | GS | - | 122.5 | g | 0 | 115.8 | 10.968 | 1065.5 | 5583 | 18:16 | 28 | 2.06 m/s | 28 | 29.3 | 4.27 m/s | 20.9 |  | 2.06 | m/s |  | 4.27 | m/s | 18.2639 | 0.0088792 | 20.7152 |  | -2.5 | 588 | 0.588 | 35.23 | 7.6194 | 6.1071 | 0.023088 | 54.7789 | 1.0734
2025-05-20 04:33 | 2189 | Remove | 2025-05-20 | 4:33 | US | GS | - | 124 | g | 0 | 115.8 | 11.001 | 1069.4 | 5592 | 18:16 | 27.9 | 2.02 m/s | 27.7 | 29.3 | 4.3 m/s | 20.2 |  | 2.02 | m/s |  | 4.3 | m/s | 18.2722 | 0.0089117 | 20.7241 |  | 1.5 | 589.5 | 0.5895 | 35.1554 | 7.4964 | 5.9026 | 0.022274 | 54.8011 | 1.0757
2025-05-20 04:34 | 2190 | Remove | 2025-05-20 | 4:34 | ST | GS | - | 126 | g | 0 | 115.9 | 10.999 | 1068.9 | 5601 | 18:17 | 27.9 | 2.0 m/s | 27.6 | 29.3 | 4.32 m/s | 20.7 |  | 2 | m/s |  | 4.32 | m/s | 18.2806 | 0.0089075 | 20.733 |  | 2 | 591.5 | 0.5915 | 35.0516 | 7.4693 | 6.0487 | 0.021974 | 54.8231 | 1.0789
2025-05-20 04:34 | 2191 | Keep | 2025-05-20 | 4:34 | ST | GS | - | 124.5 | g | 0 | 115.8 | 11.007 | 1070.9 | 5610 | 18:17 | 27.9 | 2.08 m/s | 28.3 | 29.2 | 4.26 m/s | 20.3 |  | 2.08 | m/s |  | 4.26 | m/s | 18.2889 | 0.0089242 | 20.742 |  | -1.5 | 591.5 | 0.5915 | 35.0667 | 7.6588 | 5.8995 | 0.023433 | 54.8465 | 1.0785
2025-05-20 04:35 | 2192 | Remove | 2025-05-20 | 4:35 | ST | GS | - | 123 | g | 0 | 115.8 | 11.025 | 1073.5 | 5619 | 18:18 | 27.9 | 2.09 m/s | 27.9 | 29.2 | 4.27 m/s | 20.3 |  | 2.09 | m/s |  | 4.27 | m/s | 18.2975 | 0.0089458 | 20.7509 |  | -1.5 | 591.5 | 0.5915 | 35.0818 | 7.5505 | 5.8995 | 0.023213 | 54.8698 | 1.078
2025-05-20 04:35 | 2193 | Remove | 2025-05-20 | 4:35 | ST | GS | - | 124 | g | 0 | 115.8 | 11.006 | 1070.7 | 5628 | 18:18 | 27.9 | 2.11 m/s | 28.1 | 29.2 | 4.35 m/s | 20.8 |  | 2.11 | m/s |  | 4.35 | m/s | 18.3058 | 0.0089225 | 20.7598 |  | 1 | 592.5 | 0.5925 | 35.0377 | 7.6046 | 6.0449 | 0.023603 | 54.8934 | 1.0794
2025-05-20 04:36 | 2194 | Remove | 2025-05-20 | 4:36 | ST | GS | - | 121.5 | g | 0 | 115.9 | 10.985 | 1068.3 | 5637 | 18:19 | 27.9 | 2.06 m/s | 27.8 | 29.2 | 4.26 m/s | 21.4 |  | 2.06 | m/s |  | 4.26 | m/s | 18.3142 | 0.0089025 | 20.7687 |  | -2.5 | 592.5 | 0.5925 | 35.0527 | 7.5234 | 6.2192 | 0.022797 | 54.9162 | 1.0789
2025-05-20 04:36 | 2195 | Remove | 2025-05-20 | 4:36 | ST | GS | - | 125.5 | g | 0 | 115.8 | 11.009 | 1070.9 | 5646 | 18:19 | 27.9 | 2.15 m/s | 28.4 | 29.2 | 4.35 m/s | 21.1 |  | 2.15 | m/s |  | 4.35 | m/s | 18.3225 | 0.0089242 | 20.7777 |  | 4 | 596.5 | 0.5965 | 34.8326 | 7.6858 | 6.132 | 0.024307 | 54.9405 | 1.0857
2025-05-20 04:37 | 2196 | Remove | 2025-05-20 | 4:37 | US | GS | - | 122.5 | g | 0 | 115.9 | 10.975 | 1066.6 | 5655 | 18:20 | 27.9 | 2.02 m/s | 29.2 | 29.2 | 4.36 m/s | 20.8 |  | 2.02 | m/s |  | 4.36 | m/s | 18.3308 | 0.0088883 | 20.7865 |  | -3 | 596.5 | 0.5965 | 34.8475 | 7.9023 | 6.0449 | 0.023481 | 54.9639 | 1.0853
2025-05-20 04:37 | 2197 | Remove | 2025-05-20 | 4:37 | ST | GS | - | 122 | g | 0 | 115.7 | 10.976 | 1066.6 | 5663 | 18:20 | 27.9 | 2.08 m/s | 28.9 | 29.2 | 4.29 m/s | 21.8 |  | 2.08 | m/s |  | 4.29 | m/s | 18.3392 | 0.0088883 | 20.7954 |  | -0.5 | 596.5 | 0.5965 | 34.8624 | 7.8211 | 6.3355 | 0.02393 | 54.9879 | 1.0848
2025-05-20 04:38 | 2198 | Remove | 2025-05-20 | 4:38 | ST | GS | - | 121.5 | g | 0 | 115.8 | 10.974 | 1066.8 | 5672 | 18:21 | 27.9 | 1.95 m/s | 29.6 | 29.2 | 4.27 m/s | 21.4 |  | 1.95 | m/s |  | 4.27 | m/s | 18.3475 | 0.00889 | 20.8043 |  | -0.5 | 596.5 | 0.5965 | 34.8773 | 8.0106 | 6.2192 | 0.022977 | 55.0108 | 1.0843
2025-05-20 04:38 | 2199 | Remove | 2025-05-20 | 4:38 | ST | GS | - | 122 | g | 0 | 115.8 | 10.981 | 1067.7 | 5681 | 18:21 | 27.9 | 2.09 m/s | 29.7 | 29.2 | 4.27 m/s | 21.2 |  | 2.09 | m/s |  | 4.27 | m/s | 18.3558 | 0.0088975 | 20.8132 |  | 0.5 | 597 | 0.597 | 34.863 | 8.0376 | 6.1611 | 0.02471 | 55.0356 | 1.0848
2025-05-20 04:39 | 2200 | Remove | 2025-05-20 | 4:39 | ST | GS | - | 122 | g | 0 | 115.7 | 10.976 | 1067.4 | 5690 | 18:22 | 27.9 | 2.06 m/s | 30.7 | 29.1 | 4.33 m/s | 22 |  | 2.06 | m/s |  | 4.33 | m/s | 18.3642 | 0.008895 | 20.8221 |  | 0 | 597 | 0.597 | 34.8779 | 8.3083 | 6.3588 | 0.025176 | 55.0607 | 1.0843
2025-05-20 04:39 | 2201 | Remove | 2025-05-20 | 4:39 | ST | GS | - | 123.5 | g | 0 | 115.8 | 11.01 | 1071.6 | 5699 | 18:22 | 27.9 | 2.13 m/s | 29.9 | 29.1 | 4.36 m/s | 21.7 |  | 2.13 | m/s |  | 4.36 | m/s | 18.3725 | 0.00893 | 20.831 |  | 1.5 | 598.5 | 0.5985 | 34.8054 | 8.0918 | 6.2721 | 0.025353 | 55.0861 | 1.0865
2025-05-20 04:40 | 2202 | Remove | 2025-05-20 | 4:40 | ST | GS | - | 122.5 | g | 0 | 115.8 | 11.025 | 1073.4 | 5708 | 18:23 | 27.9 | 2.19 m/s | 28 | 29.2 | 4.55 m/s | 20.2 |  | 2.19 | m/s |  | 4.55 | m/s | 18.3808 | 0.008945 | 20.84 |  | -1 | 598.5 | 0.5985 | 34.8204 | 7.5776 | 5.8705 | 0.02441 | 55.1105 | 1.086
2025-05-20 04:40 | 2203 | Remove | 2025-05-20 | 4:40 | US | GS | - | 124 | g | 0 | 115.8 | 10.996 | 1069.2 | 5717 | 18:23 | 27.9 | 2.02 m/s | 26.9 | 29.2 | 4.26 m/s | 20.8 |  | 2.02 | m/s |  | 4.26 | m/s | 18.3892 | 0.00891 | 20.8489 |  | 1.5 | 600 | 0.6 | 34.7482 | 7.2799 | 6.0449 | 0.021631 | 55.1321 | 1.0883
2025-05-20 04:41 | 2204 | Remove | 2025-05-20 | 4:41 | ST | GS | - | 122.5 | g | 0 | 115.8 | 10.986 | 1067.1 | 5726 | 18:24 | 27.9 | 2.11 m/s | 28.9 | 29.2 | 4.27 m/s | 20.1 |  | 2.11 | m/s |  | 4.27 | m/s | 18.3975 | 0.0088925 | 20.8578 |  | -1.5 | 600 | 0.6 | 34.763 | 7.8211 | 5.8414 | 0.024275 | 55.1564 | 1.0878
2025-05-20 04:41 | 2205 | Remove | 2025-05-20 | 4:41 | ST | GS | - | 123.5 | g | 0 | 115.7 | 10.952 | 1063.8 | 5735 | 18:24 | 27.9 | 2.0 m/s | 27.7 | 29.2 | 4.41 m/s | 20.9 |  | 2 | m/s |  | 4.41 | m/s | 18.4058 | 0.008865 | 20.8667 |  | 1 | 601 | 0.601 | 34.7199 | 7.4964 | 6.0739 | 0.022054 | 55.1785 | 1.0892
2025-05-20 04:42 | 2206 | Remove | 2025-05-20 | 4:42 | ST | GS | - | 125 | g | 0 | 115.8 | 10.986 | 1068.1 | 5744 | 18:25 | 27.9 | 2.12 m/s | 27.6 | 29.2 | 4.35 m/s | 20.1 |  | 2.12 | m/s |  | 4.35 | m/s | 18.4142 | 0.0089008 | 20.8756 |  | 1.5 | 602.5 | 0.6025 | 34.6482 | 7.4693 | 5.8414 | 0.023293 | 55.2018 | 1.0915
2025-05-20 04:42 | 2207 | Remove | 2025-05-20 | 4:42 | ST | GS | - | 122.5 | g | 0 | 115.8 | 11.011 | 1071.9 | 5753 | 18:25 | 27.9 | 2.13 m/s | 26.8 | 29.2 | 4.3 m/s | 20 |  | 2.13 | m/s |  | 4.3 | m/s | 18.4225 | 0.0089325 | 20.8845 |  | -2.5 | 602.5 | 0.6025 | 34.6631 | 7.2528 | 5.8124 | 0.022724 | 55.2245 | 1.091
2025-05-20 04:43 | 2208 | Remove | 2025-05-20 | 4:43 | ST | GS | - | 123 | g | 0 | 115.8 | 11.019 | 1071.7 | 5762 | 18:26 | 27.9 | 2.11 m/s | 27.6 | 29.2 | 4.35 m/s | 20 |  | 2.11 | m/s |  | 4.35 | m/s | 18.4308 | 0.0089308 | 20.8934 |  | 0.5 | 603 | 0.603 | 34.6491 | 7.4693 | 5.8124 | 0.023183 | 55.2477 | 1.0914
2025-05-20 04:43 | 2209 | Remove | 2025-05-20 | 4:43 | US | GS | - | 125 | g | 0 | 115.7 | 11.015 | 1071.8 | 5771 | 18:26 | 28 | 2.12 m/s | 26.6 | 29.2 | 4.32 m/s | 19.8 |  | 2.12 | m/s |  | 4.32 | m/s | 18.4394 | 0.0089317 | 20.9024 |  | 2 | 605 | 0.605 | 34.5493 | 7.2384 | 5.7542 | 0.022573 | 55.2702 | 1.0946
2025-05-20 04:44 | 2210 | Remove | 2025-05-20 | 4:44 | ST | GS | - | 123.5 | g | 0 | 115.8 | 10.966 | 1066.1 | 5780 | 18:27 | 27.9 | 2.11 m/s | 26.4 | 29.2 | 4.41 m/s | 20.7 |  | 2.11 | m/s |  | 4.41 | m/s | 18.4478 | 0.0088842 | 20.9112 |  | -1.5 | 605 | 0.605 | 34.564 | 7.1446 | 6.0158 | 0.022175 | 55.2924 | 1.0942
2025-05-20 04:44 | 2211 | Remove | 2025-05-20 | 4:44 | ST | GS | - | 123.5 | g | 0 | 115.8 | 10.986 | 1067.8 | 5788 | 18:27 | 27.9 | 2.02 m/s | 27.5 | 29.2 | 4.26 m/s | 20.6 |  | 2.02 | m/s |  | 4.26 | m/s | 18.4561 | 0.0088983 | 20.9201 |  | 0 | 605 | 0.605 | 34.5787 | 7.4422 | 5.9867 | 0.022114 | 55.3145 | 1.0937
2025-05-20 04:45 | 2212 | Remove | 2025-05-20 | 4:45 | ST | GS | - | 122.5 | g | 0 | 115.7 | 10.997 | 1069.7 | 5797 | 18:28 | 27.9 | 2.09 m/s | 27.2 | 29.2 | 4.32 m/s | 20.3 |  | 2.09 | m/s |  | 4.32 | m/s | 18.4644 | 0.0089142 | 20.9291 |  | -1 | 605 | 0.605 | 34.5935 | 7.3611 | 5.8995 | 0.02263 | 55.3371 | 1.0933
2025-05-20 04:45 | 2213 | Remove | 2025-05-20 | 4:45 | ST | GS | - | 124 | g | 0 | 115.7 | 10.998 | 1070.1 | 5806 | 18:28 | 27.9 | 2.12 m/s | 27.2 | 29.2 | 4.29 m/s | 20.2 |  | 2.12 | m/s |  | 4.29 | m/s | 18.4728 | 0.0089175 | 20.938 |  | 1.5 | 606.5 | 0.6065 | 34.5226 | 7.3611 | 5.8705 | 0.022955 | 55.3601 | 1.0956
2025-05-20 04:46 | 2214 | Remove | 2025-05-20 | 4:46 | ST | GS | - | 124 | g | 0 | 115.8 | 11.003 | 1070.1 | 5815 | 18:29 | 27.9 | 2.15 m/s | 27.1 | 29.2 | 4.3 m/s | 20 |  | 2.15 | m/s |  | 4.3 | m/s | 18.4811 | 0.0089175 | 20.9469 |  | 0 | 606.5 | 0.6065 | 34.5373 | 7.334 | 5.8124 | 0.023194 | 55.3833 | 1.0951
2025-05-20 04:46 | 2215 | Remove | 2025-05-20 | 4:46 | US | GS | - | 124.5 | g | 0 | 115.7 | 10.979 | 1066.8 | 5824 | 18:29 | 27.9 | 2.09 m/s | 29.3 | 29.2 | 4.38 m/s | 20.3 |  | 2.09 | m/s |  | 4.38 | m/s | 18.4894 | 0.00889 | 20.9558 |  | 0.5 | 607 | 0.607 | 34.5235 | 7.9294 | 5.8995 | 0.024377 | 55.4077 | 1.0955
2025-05-20 04:47 | 2216 | Remove | 2025-05-20 | 4:47 | ST | GS | - | 123 | g | 0 | 115.8 | 10.997 | 1069.7 | 5833 | 18:30 | 27.9 | 2.12 m/s | 26.9 | 29.2 | 4.46 m/s | 20 |  | 2.12 | m/s |  | 4.46 | m/s | 18.4978 | 0.0089142 | 20.9647 |  | -1.5 | 607 | 0.607 | 34.5382 | 7.2799 | 5.8124 | 0.022702 | 55.4304 | 1.0951
2025-05-20 04:47 | 2217 | Remove | 2025-05-20 | 4:47 | ST | GS | - | 124 | g | 0 | 115.7 | 11.028 | 1073.9 | 5842 | 18:30 | 27.9 | 2.2 m/s | 26.9 | 29.2 | 4.27 m/s | 20 |  | 2.2 | m/s |  | 4.27 | m/s | 18.5061 | 0.0089492 | 20.9736 |  | 1 | 608 | 0.608 | 34.4961 | 7.2799 | 5.8124 | 0.023559 | 55.4539 | 1.0964
2025-05-20 04:48 | 2218 | Remove | 2025-05-20 | 4:48 | US | GS | - | 126.5 | g | 0 | 115.7 | 10.964 | 1064.4 | 5851 | 18:31 | 27.9 | 2.11 m/s | 27.4 | 29.2 | 4.33 m/s | 20.7 |  | 2.11 | m/s |  | 4.33 | m/s | 18.5144 | 0.00887 | 20.9825 |  | 2.5 | 610.5 | 0.6105 | 34.3694 | 7.4152 | 6.0158 | 0.023015 | 55.477 | 1.1005
2025-05-20 04:48 | 2219 | Remove | 2025-05-20 | 4:48 | ST | GS | - | 125.5 | g | 0 | 115.7 | 10.999 | 1069.9 | 5860 | 18:31 | 27.9 | 2.12 m/s | 27.2 | 29.2 | 4.23 m/s | 19.7 |  | 2.12 | m/s |  | 4.23 | m/s | 18.5228 | 0.0089158 | 20.9914 |  | -1 | 610.5 | 0.6105 | 34.384 | 7.3611 | 5.7252 | 0.022955 | 55.4999 | 1.1
2025-05-20 04:49 | 2220 | Remove | 2025-05-20 | 4:49 | ST | GS | - | 122.5 | g | 0 | 115.7 | 10.94 | 1062.1 | 5869 | 18:32 | 27.9 | 2.08 m/s | 27.3 | 29.2 | 4.33 m/s | 21.4 |  | 2.08 | m/s |  | 4.33 | m/s | 18.5311 | 0.0088508 | 21.0003 |  | -3 | 610.5 | 0.6105 | 34.3985 | 7.3881 | 6.2192 | 0.022605 | 55.5225 | 1.0996
2025-05-20 04:49 | 2221 | Keep | 2025-05-20 | 4:49 | ST | GS | - | 124 | g | 0 | 115.7 | 10.947 | 1062.4 | 5878 | 18:32 | 27.9 | 2.06 m/s | 29.1 | 29.2 | 4.32 m/s | 21 |  | 2.06 | m/s |  | 4.32 | m/s | 18.5394 | 0.0088533 | 21.0091 |  | 1.5 | 612 | 0.612 | 34.3286 | 7.8753 | 6.103 | 0.023863 | 55.5464 | 1.1018
2025-05-20 04:50 | 2222 | Remove | 2025-05-20 | 4:50 | ST | GS | - | 123.5 | g | 0 | 115.7 | 11.001 | 1070.4 | 5887 | 18:33 | 27.9 | 2.19 m/s | 28 | 29.2 | 4.33 m/s | 20.7 |  | 2.19 | m/s |  | 4.33 | m/s | 18.5478 | 0.00892 | 21.018 |  | -0.5 | 612 | 0.612 | 34.3432 | 7.5776 | 6.0158 | 0.02441 | 55.5708 | 1.1013
2025-05-20 04:50 | 2223 | Remove | 2025-05-20 | 4:50 | ST | GS | - | 122.5 | g | 0 | 115.7 | 10.957 | 1063.5 | 5896 | 18:33 | 27.9 | 2.09 m/s | 27.5 | 29.2 | 4.38 m/s | 22.9 |  | 2.09 | m/s |  | 4.38 | m/s | 18.5561 | 0.0088625 | 21.0269 |  | -1 | 612 | 0.612 | 34.3577 | 7.4422 | 6.6552 | 0.02288 | 55.5937 | 1.1008
2025-05-20 04:51 | 2224 | Remove | 2025-05-20 | 4:51 | ST | GS | - | 124 | g | 0 | 115.7 | 10.994 | 1069.4 | 5905 | 18:34 | 27.9 | 2.06 m/s | 29.9 | 29.2 | 4.32 m/s | 20.9 |  | 2.06 | m/s |  | 4.32 | m/s | 18.5644 | 0.0089117 | 21.0358 |  | 1.5 | 613.5 | 0.6135 | 34.2882 | 8.0918 | 6.0739 | 0.02452 | 55.6182 | 1.1031
2025-05-20 04:51 | 2225 | Remove | 2025-05-20 | 4:51 | ST | GS | - | 125.5 | g | 0 | 115.7 | 10.985 | 1067.6 | 5913 | 18:34 | 27.9 | 2.08 m/s | 28.4 | 29.2 | 4.32 m/s | 20.9 |  | 2.08 | m/s |  | 4.32 | m/s | 18.5728 | 0.0088967 | 21.0447 |  | 1.5 | 615 | 0.615 | 34.2191 | 7.6858 | 6.0739 | 0.023516 | 55.6417 | 1.1053
2025-05-20 04:52 | 2226 | Remove | 2025-05-20 | 4:52 | ST | GS | - | 127 | g | 0 | 115.7 | 10.987 | 1069 | 5922 | 18:35 | 27.9 | 2.09 m/s | 28.5 | 29.2 | 4.29 m/s | 20.6 |  | 2.09 | m/s |  | 4.29 | m/s | 18.5814 | 0.0089083 | 21.0536 |  | 1.5 | 616.5 | 0.6165 | 34.1503 | 7.7129 | 5.9867 | 0.023712 | 55.6654 | 1.1075
2025-05-20 04:52 | 2227 | Remove | 2025-05-20 | 4:52 | US | GS | - | 127 | g | 0 | 115.6 | 10.964 | 1065 | 5931 | 18:35 | 27.9 | 2.04 m/s | 28.3 | 29.2 | 4.38 m/s | 20.7 |  | 2.04 | m/s |  | 4.38 | m/s | 18.5897 | 0.008875 | 21.0625 |  | 0 | 616.5 | 0.6165 | 34.1646 | 7.6588 | 6.0158 | 0.022982 | 55.6884 | 1.1071
2025-05-20 04:53 | 2228 | Remove | 2025-05-20 | 4:53 | US | GS | - | 126 | g | 0 | 115.8 | 10.966 | 1065.1 | 5940 | 18:36 | 27.9 | 2.05 m/s | 28.1 | 29.2 | 4.29 m/s | 21.4 |  | 2.05 | m/s |  | 4.29 | m/s | 18.5981 | 0.0088758 | 21.0714 |  | -1 | 616.5 | 0.6165 | 34.179 | 7.6046 | 6.2192 | 0.022932 | 55.7113 | 1.1066
2025-05-20 04:53 | 2229 | Remove | 2025-05-20 | 4:53 | US | GS | - | 127 | g | 0 | 115.7 | 10.961 | 1064.8 | 5949 | 18:36 | 27.9 | 2.04 m/s | 30.2 | 29.2 | 4.29 m/s | 20.9 |  | 2.04 | m/s |  | 4.29 | m/s | 18.6064 | 0.0088733 | 21.0803 |  | 1 | 617.5 | 0.6175 | 34.1381 | 8.1729 | 6.0739 | 0.024525 | 55.7359 | 1.1079
2025-05-20 04:54 | 2230 | Remove | 2025-05-20 | 4:54 | US | GS | - | 130.5 | g | 0 | 115.7 | 10.965 | 1065.9 | 5958 | 18:37 | 27.9 | 2.02 m/s | 28.7 | 29.2 | 4.33 m/s | 20.7 |  | 2.02 | m/s |  | 4.33 | m/s | 18.6147 | 0.0088825 | 21.0891 |  | 3.5 | 621 | 0.621 | 33.96 | 7.767 | 6.0158 | 0.023078 | 55.7589 | 1.1137
2025-05-20 04:54 | 2231 | Remove | 2025-05-20 | 4:54 | ST | GS | - | 129 | g | 0 | 115.7 | 10.962 | 1065.1 | 5967 | 18:37 | 27.9 | 2.01 m/s | 28.1 | 29.2 | 4.33 m/s | 20.7 |  | 2.01 | m/s |  | 4.33 | m/s | 18.6231 | 0.0088758 | 21.098 |  | -1.5 | 621 | 0.621 | 33.9743 | 7.6046 | 6.0158 | 0.022484 | 55.7814 | 1.1133
2025-05-20 04:55 | 2232 | Remove | 2025-05-20 | 4:55 | ST | GS | - | 127.5 | g | 0 | 115.7 | 10.956 | 1064.5 | 5976 | 18:38 | 27.9 | 2.01 m/s | 29.3 | 29.2 | 4.27 m/s | 20.5 |  | 2.01 | m/s |  | 4.27 | m/s | 18.6314 | 0.0088708 | 21.1069 |  | -1.5 | 621 | 0.621 | 33.9885 | 7.9294 | 5.9577 | 0.023444 | 55.8049 | 1.1128
2025-05-20 04:55 | 2233 | Remove | 2025-05-20 | 4:55 | ST | GS | - | 122.5 | g | 0 | 115.7 | 10.948 | 1063.4 | 5985 | 18:38 | 27.9 | 1.94 m/s | 29.7 | 29.2 | 4.3 m/s | 20.7 |  | 1.94 | m/s |  | 4.3 | m/s | 18.6397 | 0.0088617 | 21.1157 |  | -5 | 621 | 0.621 | 34.0028 | 8.0376 | 6.0158 | 0.022937 | 55.8278 | 1.1123
2025-05-20 04:56 | 2234 | Remove | 2025-05-20 | 4:56 | ST | GS | - | 128.5 | g | 0 | 115.7 | 10.956 | 1064.7 | 5994 | 18:39 | 27.9 | 2.13 m/s | 29 | 29.2 | 4.29 m/s | 21.3 |  | 2.13 | m/s |  | 4.29 | m/s | 18.6481 | 0.0088725 | 21.1246 |  | 6 | 627 | 0.627 | 33.6916 | 7.8482 | 6.1902 | 0.02459 | 55.8524 | 1.1226
2025-05-20 04:56 | 2235 | Remove | 2025-05-20 | 4:56 | ST | GS | - | 125 | g | 0 | 115.7 | 10.963 | 1065 | 6003 | 18:39 | 27.9 | 2.08 m/s | 28.9 | 29.2 | 4.33 m/s | 21.8 |  | 2.08 | m/s |  | 4.33 | m/s | 18.6564 | 0.008875 | 21.1335 |  | -3.5 | 627 | 0.627 | 33.7057 | 7.8211 | 6.3355 | 0.02393 | 55.8763 | 1.1221
2025-05-20 04:57 | 2236 | Remove | 2025-05-20 | 4:57 | ST | GS | - | 124 | g | 0 | 115.7 | 10.912 | 1058.7 | 6011 | 18:40 | 27.8 | 2.11 m/s | 28.2 | 29.2 | 4.31 m/s | 20.8 |  | 2.11 | m/s |  | 4.31 | m/s | 18.6647 | 0.0088225 | 21.1423 |  | -1 | 627 | 0.627 | 33.7198 | 7.5897 | 6.0449 | 0.023557 | 55.8999 | 1.1216
2025-05-20 04:57 | 2237 | Remove | 2025-05-20 | 4:57 | ST | GS | - | 125.5 | g | 0 | 115.7 | 10.95 | 1062.6 | 6020 | 18:40 | 27.8 | 2.08 m/s | 29.3 | 29.2 | 4.29 m/s | 21.6 |  | 2.08 | m/s |  | 4.29 | m/s | 18.6731 | 0.008855 | 21.1512 |  | 1.5 | 628.5 | 0.6285 | 33.6534 | 7.8858 | 6.2773 | 0.024127 | 55.924 | 1.1238
2025-05-20 04:58 | 2238 | Remove | 2025-05-20 | 4:58 | ST | GS | - | 124.5 | g | 0 | 115.8 | 10.948 | 1063.3 | 6029 | 18:41 | 27.8 | 2.06 m/s | 28.5 | 29.1 | 4.27 m/s | 21.2 |  | 2.06 | m/s |  | 4.27 | m/s | 18.6814 | 0.0088608 | 21.16 |  | -1 | 628.5 | 0.6285 | 33.6675 | 7.6705 | 6.1276 | 0.023243 | 55.9472 | 1.1234
2025-05-20 04:58 | 2239 | Remove | 2025-05-20 | 4:58 | ST | GS | - | 123 | g | 0 | 115.8 | 10.935 | 1061.9 | 6038 | 18:41 | 27.8 | 2.06 m/s | 28.8 | 29.1 | 4.36 m/s | 21.1 |  | 2.06 | m/s |  | 4.36 | m/s | 18.6897 | 0.0088492 | 21.1689 |  | -1.5 | 628.5 | 0.6285 | 33.6816 | 7.7512 | 6.0987 | 0.023488 | 55.9707 | 1.1229
2025-05-20 04:59 | 2240 | Remove | 2025-05-20 | 4:59 | ST | GS | - | 124.5 | g | 0 | 115.7 | 10.944 | 1062.7 | 6047 | 18:42 | 27.8 | 2.06 m/s | 29.8 | 29.1 | 4.27 m/s | 21.3 |  | 2.06 | m/s |  | 4.27 | m/s | 18.6981 | 0.0088558 | 21.1777 |  | 1.5 | 630 | 0.63 | 33.6155 | 8.0204 | 6.1565 | 0.024303 | 55.995 | 1.1251
2025-05-20 04:59 | 2241 | Remove | 2025-05-20 | 4:59 | US | GS | - | 124 | g | 0 | 115.7 | 10.95 | 1063.9 | 6056 | 18:42 | 27.8 | 2.13 m/s | 29.1 | 29.1 | 4.26 m/s | 21.1 |  | 2.13 | m/s |  | 4.26 | m/s | 18.7064 | 0.0088658 | 21.1866 |  | -0.5 | 630 | 0.63 | 33.6295 | 7.832 | 6.0987 | 0.024539 | 56.0196 | 1.1246
2025-05-20 05:00 | 2242 | Remove | 2025-05-20 | 5:00 | ST | GS | - | 124 | g | 0 | 115.7 | 10.903 | 1057.1 | 6065 | 18:43 | 27.8 | 2.13 m/s | 28.7 | 29.1 | 4.36 m/s | 21.7 |  | 2.13 | m/s |  | 4.36 | m/s | 18.7147 | 0.0088092 | 21.1954 |  | 0 | 630 | 0.63 | 33.6435 | 7.7243 | 6.2721 | 0.024201 | 56.0438 | 1.1241
2025-05-20 05:00 | 2243 | Remove | 2025-05-20 | 5:00 | ST | GS | - | 125 | g | 0 | 115.6 | 10.922 | 1059.3 | 6074 | 18:43 | 27.8 | 2.08 m/s | 30.2 | 29.1 | 4.26 m/s | 21.6 |  | 2.08 | m/s |  | 4.26 | m/s | 18.7233 | 0.0088275 | 21.2042 |  | 1 | 631 | 0.631 | 33.6042 | 8.128 | 6.2432 | 0.024869 | 56.0686 | 1.1254
2025-05-20 05:01 | 2244 | Remove | 2025-05-20 | 5:01 | ST | GS | - | 125 | g | 0 | 115.6 | 11.001 | 1070.3 | 6082 | 18:44 | 27.8 | 2.13 m/s | 28 | 29.1 | 4.38 m/s | 21.3 |  | 2.13 | m/s |  | 4.38 | m/s | 18.7317 | 0.0089192 | 21.2132 |  | 0 | 631 | 0.631 | 33.6183 | 7.5359 | 6.1565 | 0.023611 | 56.0923 | 1.1249
2025-05-20 05:01 | 2245 | Remove | 2025-05-20 | 5:01 | ST | GS | - | 125 | g | 0 | 115.6 | 10.957 | 1064.5 | 6091 | 18:44 | 27.9 | 2.15 m/s | 27.5 | 29.1 | 4.4 m/s | 20.5 |  | 2.15 | m/s |  | 4.4 | m/s | 18.74 | 0.0088708 | 21.222 |  | 0 | 631 | 0.631 | 33.6324 | 7.4422 | 5.9252 | 0.023537 | 56.1158 | 1.1245
2025-05-20 05:02 | 2246 | Remove | 2025-05-20 | 5:02 | ST | GS | - | 126 | g | 0 | 115.6 | 10.97 | 1065.5 | 6100 | 18:45 | 27.9 | 2.02 m/s | 27.3 | 29.1 | 4.55 m/s | 20.4 |  | 2.02 | m/s |  | 4.55 | m/s | 18.7486 | 0.0088792 | 21.2309 |  | 1 | 632 | 0.632 | 33.5932 | 7.3881 | 5.8963 | 0.021953 | 56.1377 | 1.1258
2025-05-20 05:02 | 2247 | Remove | 2025-05-20 | 5:02 | ST | GS | - | 123 | g | 0 | 115.5 | 10.936 | 1062.2 | 6109 | 18:45 | 27.9 | 2.19 m/s | 27.3 | 29.2 | 4.35 m/s | 20.1 |  | 2.19 | m/s |  | 4.35 | m/s | 18.7569 | 0.0088517 | 21.2398 |  | -3 | 632 | 0.632 | 33.6072 | 7.3881 | 5.8414 | 0.0238 | 56.1615 | 1.1253
2025-05-20 05:03 | 2248 | Remove | 2025-05-20 | 5:03 | ST | GS | - | 124 | g | 0 | 115.6 | 10.918 | 1059.4 | 6118 | 18:46 | 27.9 | 2.11 m/s | 27.2 | 29.2 | 4.36 m/s | 21.7 |  | 2.11 | m/s |  | 4.36 | m/s | 18.7653 | 0.0088283 | 21.2486 |  | 1 | 633 | 0.633 | 33.5681 | 7.3611 | 6.3064 | 0.022847 | 56.1844 | 1.1266
2025-05-20 05:03 | 2249 | Remove | 2025-05-20 | 5:03 | US | GS | - | 127.5 | g | 0 | 115.6 | 10.961 | 1065.1 | 6127 | 18:46 | 27.8 | 2.13 m/s | 28.3 | 29.2 | 4.49 m/s | 21.1 |  | 2.13 | m/s |  | 4.49 | m/s | 18.7736 | 0.0088758 | 21.2575 |  | 3.5 | 636.5 | 0.6365 | 33.3974 | 7.6167 | 6.132 | 0.023864 | 56.2083 | 1.1324
2025-05-20 05:04 | 2250 | Remove | 2025-05-20 | 5:04 | ST | GS | - | 125 | g | 0 | 115.5 | 10.96 | 1065 | 6136 | 18:47 | 27.9 | 2.11 m/s | 26.7 | 29.1 | 4.49 m/s | 20.2 |  | 2.11 | m/s |  | 4.49 | m/s | 18.7819 | 0.008875 | 21.2663 |  | -2.5 | 636.5 | 0.6365 | 33.4114 | 7.2257 | 5.8385 | 0.022427 | 56.2307 | 1.1319
2025-05-20 05:04 | 2251 | Keep | 2025-05-20 | 5:04 | ST | GS | - | 124 | g | 0 | 115.5 | 10.968 | 1066.5 | 6145 | 18:47 | 27.9 | 2.05 m/s | 27.4 | 29.2 | 4.44 m/s | 20.2 |  | 2.05 | m/s |  | 4.44 | m/s | 18.7903 | 0.0088875 | 21.2752 |  | -1 | 636.5 | 0.6365 | 33.4253 | 7.4152 | 5.8705 | 0.02236 | 56.253 | 1.1315
2025-05-20 05:05 | 2252 | Remove | 2025-05-20 | 5:05 | ST | GS | - | 123 | g | 0 | 115.6 | 10.955 | 1063.3 | 6154 | 18:48 | 27.9 | 2.11 m/s | 26.8 | 29.2 | 4.49 m/s | 20.2 |  | 2.11 | m/s |  | 4.49 | m/s | 18.7986 | 0.0088608 | 21.2841 |  | -1 | 636.5 | 0.6365 | 33.4393 | 7.2528 | 5.8705 | 0.022511 | 56.2755 | 1.131
2025-05-20 05:05 | 2253 | Remove | 2025-05-20 | 5:05 | ST | GS | - | 125 | g | 0 | 115.4 | 10.955 | 1064.5 | 6163 | 18:48 | 27.9 | 2.06 m/s | 28.1 | 29.2 | 4.43 m/s | 20.7 |  | 2.06 | m/s |  | 4.43 | m/s | 18.8069 | 0.0088708 | 21.293 |  | 2 | 638.5 | 0.6385 | 33.3484 | 7.6046 | 6.0158 | 0.023043 | 56.2986 | 1.1341
2025-05-20 05:06 | 2254 | Remove | 2025-05-20 | 5:06 | ST | GS | - | 125.5 | g | 0 | 115.5 | 10.974 | 1066.3 | 6171 | 18:49 | 27.9 | 2.08 m/s | 28.1 | 29.2 | 4.43 m/s | 20.4 |  | 2.08 | m/s |  | 4.43 | m/s | 18.8153 | 0.0088858 | 21.3018 |  | 0.5 | 639 | 0.639 | 33.3362 | 7.6046 | 5.9286 | 0.023267 | 56.3219 | 1.1346
2025-05-20 05:06 | 2255 | Remove | 2025-05-20 | 5:06 | ST | GS | - | 125 | g | 0 | 115.4 | 10.971 | 1066.5 | 6180 | 18:49 | 27.9 | 2.09 m/s | 27.2 | 29.2 | 4.27 m/s | 20.5 |  | 2.09 | m/s |  | 4.27 | m/s | 18.8236 | 0.0088875 | 21.3107 |  | -0.5 | 639 | 0.639 | 33.3501 | 7.3611 | 5.9577 | 0.02263 | 56.3445 | 1.1341
2025-05-20 05:07 | 2256 | Remove | 2025-05-20 | 5:07 | ST | GS | - | 123.5 | g | 0 | 115.6 | 10.926 | 1060.7 | 6189 | 18:50 | 27.9 | 2.12 m/s | 27.5 | 29.2 | 4.32 m/s | 20.5 |  | 2.12 | m/s |  | 4.32 | m/s | 18.8319 | 0.0088392 | 21.3196 |  | -1.5 | 639 | 0.639 | 33.364 | 7.4422 | 5.9577 | 0.023208 | 56.3677 | 1.1336
2025-05-20 05:07 | 2257 | Remove | 2025-05-20 | 5:07 | ST | GS | - | 124 | g | 0 | 115.5 | 10.982 | 1067.8 | 6198 | 18:50 | 27.9 | 2.11 m/s | 27.1 | 29.2 | 4.35 m/s | 20.4 |  | 2.11 | m/s |  | 4.35 | m/s | 18.8403 | 0.0088983 | 21.3285 |  | 0.5 | 639.5 | 0.6395 | 33.3518 | 7.334 | 5.9286 | 0.022763 | 56.3905 | 1.1341
2025-05-20 05:08 | 2258 | Remove | 2025-05-20 | 5:08 | ST | GS | - | 123 | g | 0 | 115.5 | 10.933 | 1061.9 | 6207 | 18:51 | 27.9 | 2.09 m/s | 27.2 | 29.2 | 4.29 m/s | 20.4 |  | 2.09 | m/s |  | 4.29 | m/s | 18.8486 | 0.0088492 | 21.3373 |  | -1 | 639.5 | 0.6395 | 33.3656 | 7.3611 | 5.9286 | 0.02263 | 56.4131 | 1.1336
2025-05-20 05:08 | 2259 | Remove | 2025-05-20 | 5:08 | US | GS | - | 123.5 | g | 0 | 115.5 | 10.941 | 1061.7 | 6216 | 18:51 | 27.9 | 2.15 m/s | 27.8 | 29.2 | 4.3 m/s | 20.8 |  | 2.15 | m/s |  | 4.3 | m/s | 18.8569 | 0.0088475 | 21.3462 |  | 0.5 | 640 | 0.64 | 33.3534 | 7.5234 | 6.0449 | 0.023793 | 56.4369 | 1.134
2025-05-20 05:09 | 2260 | Remove | 2025-05-20 | 5:09 | ST | GS | - | 123.5 | g | 0 | 115.6 | 10.878 | 1054.1 | 6225 | 18:52 | 27.8 | 2.04 m/s | 30.5 | 29.2 | 4.23 m/s | 21.1 |  | 2.04 | m/s |  | 4.23 | m/s | 18.8653 | 0.0087842 | 21.3549 |  | 0 | 640 | 0.64 | 33.3671 | 8.2088 | 6.132 | 0.024633 | 56.4615 | 1.1335
2025-05-20 05:09 | 2261 | Remove | 2025-05-20 | 5:09 | ST | GS | - | 128.5 | g | 0 | 115.6 | 10.932 | 1061.7 | 6234 | 18:52 | 27.8 | 2.16 m/s | 27.8 | 29.1 | 4.32 m/s | 20.8 |  | 2.16 | m/s |  | 4.32 | m/s | 18.8739 | 0.0088475 | 21.3638 |  | 5 | 645 | 0.645 | 33.1222 | 7.4821 | 6.012 | 0.023773 | 56.4853 | 1.1419
2025-05-20 05:10 | 2262 | Remove | 2025-05-20 | 5:10 | ST | GS | - | 125 | g | 0 | 115.5 | 10.936 | 1063.2 | 6242 | 18:53 | 27.8 | 2.06 m/s | 27.6 | 29.1 | 4.33 m/s | 20.4 |  | 2.06 | m/s |  | 4.33 | m/s | 18.8822 | 0.00886 | 21.3727 |  | -3.5 | 645 | 0.645 | 33.1359 | 7.4283 | 5.8963 | 0.022509 | 56.5078 | 1.1414
2025-05-20 05:10 | 2263 | Remove | 2025-05-20 | 5:10 | ST | GS | - | 124 | g | 0 | 115.4 | 10.907 | 1058.4 | 6251 | 18:53 | 27.8 | 2.13 m/s | 29.9 | 29.1 | 4.23 m/s | 20.9 |  | 2.13 | m/s |  | 4.23 | m/s | 18.8906 | 0.00882 | 21.3815 |  | -1 | 645 | 0.645 | 33.1496 | 8.0473 | 6.0409 | 0.025213 | 56.533 | 1.1409
2025-05-20 05:11 | 2264 | Remove | 2025-05-20 | 5:11 | ST | GS | - | 126.5 | g | 0 | 115.5 | 10.911 | 1058.4 | 6260 | 18:54 | 27.8 | 2.04 m/s | 29.4 | 29.1 | 4.24 m/s | 22.5 |  | 2.04 | m/s |  | 4.24 | m/s | 18.8989 | 0.00882 | 21.3903 |  | 2.5 | 647.5 | 0.6475 | 33.0352 | 7.9127 | 6.5033 | 0.023744 | 56.5568 | 1.1449
2025-05-20 05:11 | 2265 | Remove | 2025-05-20 | 5:11 | ST | GS | - | 124 | g | 0 | 115.5 | 10.877 | 1054.3 | 6269 | 18:54 | 27.8 | 2.06 m/s | 30.1 | 29.1 | 4.29 m/s | 21.7 |  | 2.06 | m/s |  | 4.29 | m/s | 18.9072 | 0.0087858 | 21.3991 |  | -2.5 | 647.5 | 0.6475 | 33.0488 | 8.1011 | 6.2721 | 0.024548 | 56.5813 | 1.1444
2025-05-20 05:12 | 2266 | Remove | 2025-05-20 | 5:12 | ST | GS | - | 130.5 | g | 0 | 115.6 | 10.901 | 1057.9 | 6278 | 18:55 | 27.8 | 2.01 m/s | 30.6 | 29.1 | 4.27 m/s | 22 |  | 2.01 | m/s |  | 4.27 | m/s | 18.9156 | 0.0088158 | 21.4079 |  | 6.5 | 654 | 0.654 | 32.7338 | 8.2357 | 6.3588 | 0.02435 | 56.6057 | 1.1554
2025-05-20 05:12 | 2267 | Remove | 2025-05-20 | 5:12 | ST | GS | - | 126 | g | 0 | 115.7 | 10.877 | 1054.5 | 6287 | 18:55 | 27.7 | 2.16 m/s | 32.9 | 29.1 | 4.24 m/s | 21.6 |  | 2.16 | m/s |  | 4.24 | m/s | 18.9239 | 0.0087875 | 21.4167 |  | -4.5 | 654 | 0.654 | 32.7472 | 8.806 | 6.2432 | 0.027979 | 56.6336 | 1.1548
2025-05-20 05:13 | 2268 | Remove | 2025-05-20 | 5:13 | ST | GS | - | 126.5 | g | 0 | 115.6 | 10.898 | 1057.2 | 6296 | 18:56 | 27.7 | 2.06 m/s | 30.3 | 29.1 | 4.29 m/s | 22 |  | 2.06 | m/s |  | 4.29 | m/s | 18.9322 | 0.00881 | 21.4255 |  | 0.5 | 654.5 | 0.6545 | 32.7357 | 8.1101 | 6.3588 | 0.024575 | 56.6582 | 1.1552
2025-05-20 05:13 | 2269 | Remove | 2025-05-20 | 5:13 | ST | GS | - | 124 | g | 0 | 115.6 | 10.901 | 1057.1 | 6304 | 18:56 | 27.8 | 2.05 m/s | 29.5 | 29.1 | 4.35 m/s | 21.4 |  | 2.05 | m/s |  | 4.35 | m/s | 18.9406 | 0.0088092 | 21.4343 |  | -2.5 | 654.5 | 0.6545 | 32.7491 | 7.9396 | 6.1854 | 0.023942 | 56.6822 | 1.1547
2025-05-20 05:14 | 2270 | Remove | 2025-05-20 | 5:14 | ST | GS | - | 125.5 | g | 0 | 115.6 | 10.898 | 1057.3 | 6313 | 18:57 | 27.8 | 2.09 m/s | 30.2 | 29.1 | 4.43 m/s | 22.9 |  | 2.09 | m/s |  | 4.43 | m/s | 18.9489 | 0.0088108 | 21.4431 |  | 1.5 | 656 | 0.656 | 32.6877 | 8.128 | 6.6189 | 0.024988 | 56.7071 | 1.1568
2025-05-20 05:14 | 2271 | Remove | 2025-05-20 | 5:14 | ST | GS | - | 126.5 | g | 0 | 115.6 | 10.882 | 1054.8 | 6322 | 18:57 | 27.8 | 2.02 m/s | 29.7 | 29.1 | 4.32 m/s | 22.3 |  | 2.02 | m/s |  | 4.32 | m/s | 18.9572 | 0.00879 | 21.4519 |  | 1 | 657 | 0.657 | 32.6513 | 7.9935 | 6.4455 | 0.023751 | 56.7309 | 1.1581
2025-05-20 05:15 | 2272 | Remove | 2025-05-20 | 5:15 | ST | GS | - | 129 | g | 0 | 115.6 | 10.918 | 1059.4 | 6331 | 18:58 | 27.7 | 2.08 m/s | 30 | 29.1 | 4.36 m/s | 22 |  | 2.08 | m/s |  | 4.36 | m/s | 18.9656 | 0.0088283 | 21.4607 |  | 2.5 | 659.5 | 0.6595 | 32.5409 | 8.0298 | 6.3588 | 0.024568 | 56.7555 | 1.162
2025-05-20 05:15 | 2273 | Remove | 2025-05-20 | 5:15 | ST | GS | - | 124 | g | 0 | 115.6 | 10.87 | 1053.5 | 6340 | 18:58 | 27.8 | 1.9 m/s | 29.4 | 29.1 | 4.35 m/s | 21.3 |  | 1.9 | m/s |  | 4.35 | m/s | 18.9739 | 0.0087792 | 21.4695 |  | -5 | 659.5 | 0.6595 | 32.5542 | 7.9127 | 6.1565 | 0.022115 | 56.7776 | 1.1616
2025-05-20 05:16 | 2274 | Remove | 2025-05-20 | 5:16 | ST | GS | - | 131.5 | g | 0 | 115.6 | 10.868 | 1053.5 | 6349 | 18:59 | 27.7 | 2.08 m/s | 30.3 | 29.1 | 4.24 m/s | 21.4 |  | 2.08 | m/s |  | 4.24 | m/s | 18.9822 | 0.0087792 | 21.4783 |  | 7.5 | 667 | 0.667 | 32.2013 | 8.1101 | 6.1854 | 0.024814 | 56.8024 | 1.1742
2025-05-20 05:16 | 2275 | Remove | 2025-05-20 | 5:16 | US | GS | - | 124 | g | 0 | 115.6 | 10.872 | 1052.9 | 6357 | 18:59 | 27.7 | 2.06 m/s | 31.5 | 29.1 | 4.38 m/s | 22.9 |  | 2.06 | m/s |  | 4.38 | m/s | 18.9906 | 0.0087742 | 21.4871 |  | -7.5 | 667 | 0.667 | 32.2145 | 8.4313 | 6.6189 | 0.025548 | 56.8279 | 1.1737
2025-05-20 05:17 | 2276 | Remove | 2025-05-20 | 5:17 | ST | GS | - | 130 | g | 0 | 115.5 | 10.909 | 1059.2 | 6366 | 19:00 | 27.7 | 2.08 m/s | 30.4 | 29 | 4.29 m/s | 22.9 |  | 2.08 | m/s |  | 4.29 | m/s | 18.9989 | 0.0088267 | 21.4959 |  | 6 | 673 | 0.673 | 31.9404 | 8.1368 | 6.5829 | 0.024896 | 56.8528 | 1.1838
2025-05-20 05:17 | 2277 | Remove | 2025-05-20 | 5:17 | ST | GS | - | 127 | g | 0 | 115.6 | 10.906 | 1058.7 | 6375 | 19:00 | 27.7 | 2.04 m/s | 30 | 29 | 4.23 m/s | 21.1 |  | 2.04 | m/s |  | 4.23 | m/s | 19.0072 | 0.0088225 | 21.5047 |  | -3 | 673 | 0.673 | 31.9535 | 8.0298 | 6.0655 | 0.024096 | 56.8769 | 1.1833
2025-05-20 05:18 | 2278 | Remove | 2025-05-20 | 5:18 | US | GS | - | 129 | g | 0 | 115.6 | 10.88 | 1054.8 | 6384 | 19:01 | 27.7 | 2.06 m/s | 31.7 | 29 | 4.24 m/s | 21.2 |  | 2.06 | m/s |  | 4.24 | m/s | 19.0158 | 0.00879 | 21.5135 |  | 2 | 675 | 0.675 | 31.8719 | 8.4848 | 6.0942 | 0.025711 | 56.9026 | 1.1862
2025-05-20 05:18 | 2279 | Remove | 2025-05-20 | 5:18 | ST | GS | - | 126.5 | g | 0 | 115.5 | 10.917 | 1059.7 | 6393 | 19:01 | 27.7 | 2.06 m/s | 28.6 | 29 | 4.35 m/s | 20.7 |  | 2.06 | m/s |  | 4.35 | m/s | 19.0242 | 0.0088308 | 21.5223 |  | -2.5 | 675 | 0.675 | 31.8849 | 7.6551 | 5.9505 | 0.023196 | 56.9258 | 1.1858
2025-05-20 05:19 | 2280 | Remove | 2025-05-20 | 5:19 | US | GS | - | 127 | g | 0 | 115.6 | 10.884 | 1055.1 | 6401 | 19:02 | 27.7 | 2.06 m/s | 29.2 | 29.1 | 4.29 m/s | 21.2 |  | 2.06 | m/s |  | 4.29 | m/s | 19.0325 | 0.0087925 | 21.5311 |  | 0.5 | 675.5 | 0.6755 | 31.8744 | 7.8157 | 6.1276 | 0.023683 | 56.9495 | 1.1861
2025-05-20 05:19 | 2281 | Keep | 2025-05-20 | 5:19 | ST | GS | - | 128 | g | 0 | 115.6 | 10.908 | 1057.9 | 6410 | 19:02 | 27.7 | 2.04 m/s | 30.9 | 29.1 | 4.29 m/s | 21.2 |  | 2.04 | m/s |  | 4.29 | m/s | 19.0408 | 0.0088158 | 21.5399 |  | 1 | 676.5 | 0.6765 | 31.8403 | 8.2707 | 6.1276 | 0.024818 | 56.9743 | 1.1874
2025-05-20 05:20 | 2282 | Remove | 2025-05-20 | 5:20 | ST | GS | - | 127 | g | 0 | 115.5 | 10.945 | 1064 | 6419 | 19:03 | 27.8 | 2.11 m/s | 27.9 | 29.1 | 4.69 m/s | 20.5 |  | 2.11 | m/s |  | 4.69 | m/s | 19.0492 | 0.0088667 | 21.5488 |  | -1 | 676.5 | 0.6765 | 31.8534 | 7.509 | 5.9252 | 0.023306 | 56.9976 | 1.1869
2025-05-20 05:20 | 2283 | Remove | 2025-05-20 | 5:20 | ST | GS | - | 125.5 | g | 0 | 115.5 | 10.924 | 1061.3 | 6428 | 19:03 | 27.8 | 2.22 m/s | 27.8 | 29.1 | 4.44 m/s | 20.7 |  | 2.22 | m/s |  | 4.44 | m/s | 19.0575 | 0.0088442 | 21.5577 |  | -1.5 | 676.5 | 0.6765 | 31.8665 | 7.4821 | 5.9831 | 0.024433 | 57.0221 | 1.1864
2025-05-20 05:21 | 2284 | Remove | 2025-05-20 | 5:21 | ST | GS | - | 127 | g | 0 | 115.5 | 10.931 | 1062 | 6437 | 19:04 | 27.8 | 2.16 m/s | 27.4 | 29.1 | 4.3 m/s | 20.4 |  | 2.16 | m/s |  | 4.3 | m/s | 19.0658 | 0.00885 | 21.5665 |  | 1.5 | 678 | 0.678 | 31.809 | 7.3744 | 5.8963 | 0.023431 | 57.0455 | 1.1885
2025-05-20 05:21 | 2285 | Remove | 2025-05-20 | 5:21 | ST | GS | - | 124.5 | g | 0 | 115.6 | 10.889 | 1055.6 | 6446 | 19:04 | 27.8 | 2.13 m/s | 27.5 | 29.1 | 4.6 m/s | 20.7 |  | 2.13 | m/s |  | 4.6 | m/s | 19.0742 | 0.0087967 | 21.5753 |  | -2.5 | 678 | 0.678 | 31.822 | 7.4013 | 5.9831 | 0.02319 | 57.0687 | 1.188
2025-05-20 05:22 | 2286 | Remove | 2025-05-20 | 5:22 | US | GS | - | 124.5 | g | 0 | 115.5 | 10.939 | 1062.3 | 6455 | 19:05 | 27.8 | 2.12 m/s | 27.6 | 29.1 | 4.32 m/s | 21.2 |  | 2.12 | m/s |  | 4.32 | m/s | 19.0825 | 0.0088525 | 21.5842 |  | 0 | 678 | 0.678 | 31.835 | 7.4283 | 6.1276 | 0.023165 | 57.0919 | 1.1876
2025-05-20 05:22 | 2287 | Remove | 2025-05-20 | 5:22 | US | GS | - | 127 | g | 0 | 115.4 | 10.916 | 1060.1 | 6464 | 19:05 | 27.8 | 2.11 m/s | 27.9 | 29.1 | 4.23 m/s | 20.7 |  | 2.11 | m/s |  | 4.23 | m/s | 19.0908 | 0.0088342 | 21.593 |  | 2.5 | 680.5 | 0.6805 | 31.7311 | 7.509 | 5.9831 | 0.023306 | 57.1152 | 1.1915
2025-05-20 05:23 | 2288 | Remove | 2025-05-20 | 5:23 | ST | GS | - | 126 | g | 0 | 115.5 | 10.932 | 1062.9 | 6472 | 19:06 | 27.8 | 2.05 m/s | 27.4 | 29.1 | 4.41 m/s | 20.5 |  | 2.05 | m/s |  | 4.41 | m/s | 19.0992 | 0.0088575 | 21.6018 |  | -1 | 680.5 | 0.6805 | 31.7441 | 7.3744 | 5.9252 | 0.022237 | 57.1374 | 1.191
2025-05-20 05:23 | 2289 | Remove | 2025-05-20 | 5:23 | ST | GS | - | 127.5 | g | 0 | 115.5 | 10.935 | 1062.7 | 6481 | 19:06 | 27.8 | 2.09 m/s | 27.9 | 29.1 | 4.29 m/s | 20.1 |  | 2.09 | m/s |  | 4.29 | m/s | 19.1075 | 0.0088558 | 21.6107 |  | 1.5 | 682 | 0.682 | 31.6872 | 7.509 | 5.8096 | 0.023085 | 57.1605 | 1.1931
2025-05-20 05:24 | 2290 | Remove | 2025-05-20 | 5:24 | ST | GS | - | 127 | g | 0 | 115.5 | 10.95 | 1063.9 | 6490 | 19:07 | 27.9 | 2.06 m/s | 27.3 | 29.1 | 4.33 m/s | 20.2 |  | 2.06 | m/s |  | 4.33 | m/s | 19.1158 | 0.0088658 | 21.6196 |  | -0.5 | 682 | 0.682 | 31.7002 | 7.3881 | 5.8385 | 0.022387 | 57.1829 | 1.1927
2025-05-20 05:24 | 2291 | Remove | 2025-05-20 | 5:24 | ST | GS | - | 124.5 | g | 0 | 115.5 | 10.938 | 1062.9 | 6499 | 19:07 | 27.9 | 2.16 m/s | 27.2 | 29.1 | 4.9 m/s | 20 |  | 2.16 | m/s |  | 4.9 | m/s | 19.1242 | 0.0088575 | 21.6284 |  | -2.5 | 682 | 0.682 | 31.7132 | 7.3611 | 5.7807 | 0.023388 | 57.2063 | 1.1922
2025-05-20 05:25 | 2292 | Remove | 2025-05-20 | 5:25 | ST | GS | - | 124.5 | g | 0 | 115.6 | 10.889 | 1056.3 | 6508 | 19:08 | 27.8 | 2.11 m/s | 27.1 | 29.2 | 4.33 m/s | 20.3 |  | 2.11 | m/s |  | 4.33 | m/s | 19.1325 | 0.0088025 | 21.6372 |  | 0 | 682 | 0.682 | 31.7261 | 7.2937 | 5.8995 | 0.022638 | 57.2289 | 1.1917
2025-05-20 05:25 | 2293 | Remove | 2025-05-20 | 5:25 | ST | GS | - | 127.5 | g | 0 | 115.4 | 10.946 | 1063.4 | 6517 | 19:08 | 27.8 | 2.05 m/s | 27.9 | 29.1 | 4.38 m/s | 21.6 |  | 2.05 | m/s |  | 4.38 | m/s | 19.1408 | 0.0088617 | 21.6461 |  | 3 | 685 | 0.685 | 31.6001 | 7.509 | 6.2432 | 0.022643 | 57.2515 | 1.1965
2025-05-20 05:26 | 2294 | Remove | 2025-05-20 | 5:26 | ST | GS | - | 126.5 | g | 0 | 115.5 | 10.959 | 1065.6 | 6526 | 19:09 | 27.8 | 2.09 m/s | 27.5 | 29.1 | 4.35 m/s | 20.3 |  | 2.09 | m/s |  | 4.35 | m/s | 19.1492 | 0.00888 | 21.655 |  | -1 | 685 | 0.685 | 31.6131 | 7.4013 | 5.8674 | 0.022754 | 57.2743 | 1.196
2025-05-20 05:26 | 2295 | Remove | 2025-05-20 | 5:26 | ST | GS | - | 124.5 | g | 0 | 115.5 | 10.932 | 1063 | 6535 | 19:09 | 27.9 | 2.18 m/s | 27.6 | 29.1 | 4.35 m/s | 20.5 |  | 2.18 | m/s |  | 4.35 | m/s | 19.1578 | 0.0088583 | 21.6638 |  | -2 | 685 | 0.685 | 31.626 | 7.4693 | 5.9252 | 0.023952 | 57.2982 | 1.1955
2025-05-20 05:27 | 2296 | Remove | 2025-05-20 | 5:27 | US | GS | - | 126 | g | 0 | 115.4 | 10.952 | 1064.7 | 6544 | 19:10 | 27.9 | 2.06 m/s | 27 | 29.1 | 4.4 m/s | 20.5 |  | 2.06 | m/s |  | 4.4 | m/s | 19.1661 | 0.0088725 | 21.6727 |  | 1.5 | 686.5 | 0.6865 | 31.5698 | 7.3069 | 5.9252 | 0.022141 | 57.3204 | 1.1977
2025-05-20 05:27 | 2297 | Remove | 2025-05-20 | 5:27 | ST | GS | - | 128 | g | 0 | 115.4 | 10.935 | 1063.3 | 6552 | 19:10 | 27.9 | 2.08 m/s | 27.2 | 29.2 | 4.3 m/s | 20.2 |  | 2.08 | m/s |  | 4.3 | m/s | 19.1744 | 0.0088608 | 21.6816 |  | 2 | 688.5 | 0.6885 | 31.491 | 7.3611 | 5.8705 | 0.022522 | 57.3429 | 1.2007
2025-05-20 05:28 | 2298 | Remove | 2025-05-20 | 5:28 | ST | GS | - | 127.5 | g | 0 | 115.5 | 10.968 | 1067.5 | 6561 | 19:11 | 27.9 | 2.09 m/s | 27.1 | 29.2 | 4.3 m/s | 20.4 |  | 2.09 | m/s |  | 4.3 | m/s | 19.1828 | 0.0088958 | 21.6905 |  | -0.5 | 688.5 | 0.6885 | 31.5039 | 7.334 | 5.9286 | 0.022547 | 57.3655 | 1.2002
2025-05-20 05:28 | 2299 | Remove | 2025-05-20 | 5:28 | ST | GS | - | 125.5 | g | 0 | 115.3 | 10.962 | 1066.4 | 6570 | 19:11 | 27.9 | 2.09 m/s | 26.8 | 29.2 | 4.44 m/s | 20 |  | 2.09 | m/s |  | 4.44 | m/s | 19.1911 | 0.0088867 | 21.6993 |  | -2 | 688.5 | 0.6885 | 31.5168 | 7.2528 | 5.8124 | 0.022297 | 57.3878 | 1.1997
2025-05-20 05:29 | 2300 | Remove | 2025-05-20 | 5:29 | US | GS | - | 127 | g | 0 | 115.5 | 10.912 | 1059.8 | 6579 | 19:12 | 27.9 | 2.11 m/s | 28.2 | 29.2 | 4.32 m/s | 20.6 |  | 2.11 | m/s |  | 4.32 | m/s | 19.1994 | 0.0088317 | 21.7082 |  | 1.5 | 690 | 0.69 | 31.4611 | 7.6317 | 5.9867 | 0.023687 | 57.4114 | 1.2019
2025-05-20 05:29 | 2301 | Remove | 2025-05-20 | 5:29 | ST | GS | - | 125 | g | 0 | 115.6 | 10.9 | 1057.1 | 6588 | 19:12 | 27.8 | 2.12 m/s | 27.5 | 29.2 | 4.35 m/s | 20.7 |  | 2.12 | m/s |  | 4.35 | m/s | 19.2078 | 0.0088092 | 21.717 |  | -2 | 690 | 0.69 | 31.4739 | 7.4013 | 6.0158 | 0.023081 | 57.4345 | 1.2014
2025-05-20 05:30 | 2302 | Remove | 2025-05-20 | 5:30 | ST | GS | - | 125.5 | g | 0 | 115.5 | 10.864 | 1053.3 | 6597 | 19:13 | 27.8 | 2.13 m/s | 27.6 | 29.2 | 4.29 m/s | 20.5 |  | 2.13 | m/s |  | 4.29 | m/s | 19.2161 | 0.0087775 | 21.7258 |  | 0.5 | 690.5 | 0.6905 | 31.4638 | 7.4283 | 5.9577 | 0.023274 | 57.4578 | 1.2018
2025-05-20 05:30 | 2303 | Remove | 2025-05-20 | 5:30 | ST | GS | - | 125.5 | g | 0 | 115.4 | 10.863 | 1052.3 | 6606 | 19:13 | 27.8 | 2.02 m/s | 28.8 | 29.1 | 4.29 m/s | 21.5 |  | 2.02 | m/s |  | 4.29 | m/s | 19.2244 | 0.0087692 | 21.7345 |  | 0 | 690.5 | 0.6905 | 31.4765 | 7.7512 | 6.2143 | 0.023032 | 57.4808 | 1.2013
2025-05-20 05:31 | 2304 | Remove | 2025-05-20 | 5:31 | US | GS | - | 128.5 | g | 0 | 115.5 | 10.908 | 1059.1 | 6614 | 19:14 | 27.8 | 2.16 m/s | 27.6 | 29.1 | 4.36 m/s | 20.9 |  | 2.16 | m/s |  | 4.36 | m/s | 19.2328 | 0.0088258 | 21.7434 |  | 3 | 693.5 | 0.6935 | 31.3531 | 7.4283 | 6.0409 | 0.023602 | 57.5044 | 1.206
2025-05-20 05:31 | 2305 | Remove | 2025-05-20 | 5:31 | US | GS | - | 128.5 | g | 0 | 115.5 | 10.894 | 1057.3 | 6623 | 19:14 | 27.8 | 2.06 m/s | 28.4 | 29.1 | 4.47 m/s | 20.7 |  | 2.06 | m/s |  | 4.47 | m/s | 19.2411 | 0.0088108 | 21.7522 |  | 0 | 693.5 | 0.6935 | 31.3658 | 7.6436 | 5.9831 | 0.023161 | 57.5276 | 1.2055
2025-05-20 05:32 | 2306 | Remove | 2025-05-20 | 5:32 | ST | GS | - | 128 | g | 0 | 115.3 | 10.905 | 1059.4 | 6632 | 19:15 | 27.8 | 1.98 m/s | 28.2 | 29.1 | 4.3 m/s | 20.7 |  | 1.98 | m/s |  | 4.3 | m/s | 19.2494 | 0.0088283 | 21.761 |  | -0.5 | 693.5 | 0.6935 | 31.3785 | 7.5897 | 5.9831 | 0.022105 | 57.5497 | 1.205
2025-05-20 05:32 | 2307 | Remove | 2025-05-20 | 5:32 | ST | GS | - | 126 | g | 0 | 115.4 | 10.9 | 1057.6 | 6641 | 19:15 | 27.8 | 2.05 m/s | 28 | 29.1 | 4.35 m/s | 20.7 |  | 2.05 | m/s |  | 4.35 | m/s | 19.2578 | 0.0088133 | 21.7698 |  | -2 | 693.5 | 0.6935 | 31.3912 | 7.5359 | 5.9831 | 0.022724 | 57.5724 | 1.2046
2025-05-20 05:33 | 2308 | Remove | 2025-05-20 | 5:33 | ST | GS | - | 125.5 | g | 0 | 115.3 | 10.887 | 1056.4 | 6650 | 19:16 | 27.8 | 2.13 m/s | 28.7 | 29.1 | 4.32 m/s | 20.9 |  | 2.13 | m/s |  | 4.32 | m/s | 19.2661 | 0.0088033 | 21.7786 |  | -0.5 | 693.5 | 0.6935 | 31.4039 | 7.7243 | 6.0409 | 0.024201 | 57.5966 | 1.2041
2025-05-20 05:33 | 2309 | Remove | 2025-05-20 | 5:33 | ST | GS | - | 125.5 | g | 0 | 115.3 | 10.874 | 1055.6 | 6659 | 19:16 | 27.8 | 2.11 m/s | 28 | 29.1 | 4.72 m/s | 20.7 |  | 2.11 | m/s |  | 4.72 | m/s | 19.2744 | 0.0087967 | 21.7874 |  | 0 | 693.5 | 0.6935 | 31.4166 | 7.5359 | 5.9831 | 0.023389 | 57.62 | 1.2036
2025-05-20 05:34 | 2310 | Remove | 2025-05-20 | 5:34 | ST | GS | - | 128.5 | g | 0 | 115.3 | 10.863 | 1053.6 | 6667 | 19:17 | 27.8 | 2.08 m/s | 29 | 29.1 | 4.27 m/s | 22 |  | 2.08 | m/s |  | 4.27 | m/s | 19.2828 | 0.00878 | 21.7962 |  | 3 | 696.5 | 0.6965 | 31.2939 | 7.8051 | 6.3588 | 0.02388 | 57.6439 | 1.2083
2025-05-20 05:34 | 2311 | Keep | 2025-05-20 | 5:34 | US | GS | - | 128.5 | g | 0 | 115.4 | 10.869 | 1053.8 | 6676 | 19:17 | 27.8 | 2.04 m/s | 28.6 | 29.1 | 4.27 m/s | 20.4 |  | 2.04 | m/s |  | 4.27 | m/s | 19.2911 | 0.0087817 | 21.805 |  | 0 | 696.5 | 0.6965 | 31.3065 | 7.6974 | 5.8963 | 0.023098 | 57.667 | 1.2078
2025-05-20 05:35 | 2312 | Remove | 2025-05-20 | 5:35 | ST | GS | - | 127.5 | g | 0 | 115.3 | 10.904 | 1058.3 | 6685 | 19:18 | 27.7 | 2.09 m/s | 29.6 | 29.1 | 4.32 m/s | 21.3 |  | 2.09 | m/s |  | 4.32 | m/s | 19.2997 | 0.0088192 | 21.8138 |  | -1 | 696.5 | 0.6965 | 31.3192 | 7.9227 | 6.1565 | 0.024357 | 57.6913 | 1.2073
2025-05-20 05:35 | 2313 | Remove | 2025-05-20 | 5:35 | ST | GS | - | 128.5 | g | 0 | 115.4 | 10.915 | 1060.1 | 6694 | 19:18 | 27.8 | 2.19 m/s | 27.9 | 29 | 4.29 m/s | 20.6 |  | 2.19 | m/s |  | 4.29 | m/s | 19.3081 | 0.0088342 | 21.8226 |  | 1 | 697.5 | 0.6975 | 31.2869 | 7.509 | 5.9217 | 0.02419 | 57.7155 | 1.2085
2025-05-20 05:36 | 2314 | Remove | 2025-05-20 | 5:36 | ST | GS | - | 128.5 | g | 0 | 115.4 | 10.89 | 1057.5 | 6703 | 19:19 | 27.8 | 2.09 m/s | 28.5 | 29 | 4.32 m/s | 20.4 |  | 2.09 | m/s |  | 4.32 | m/s | 19.3164 | 0.0088125 | 21.8314 |  | 0 | 697.5 | 0.6975 | 31.2996 | 7.6705 | 5.8642 | 0.023582 | 57.7391 | 1.208
2025-05-20 05:36 | 2315 | Remove | 2025-05-20 | 5:36 | ST | GS | - | 126.5 | g | 0 | 115.3 | 10.904 | 1058.9 | 6712 | 19:19 | 27.8 | 2.16 m/s | 27.4 | 29.1 | 4.35 m/s | 20.5 |  | 2.16 | m/s |  | 4.35 | m/s | 19.3247 | 0.0088242 | 21.8403 |  | -2 | 697.5 | 0.6975 | 31.3122 | 7.3744 | 5.9252 | 0.023431 | 57.7626 | 1.2075
2025-05-20 05:37 | 2316 | Remove | 2025-05-20 | 5:37 | ST | GS | - | 126.5 | g | 0 | 115.3 | 10.942 | 1064.2 | 6720 | 19:20 | 27.8 | 2.15 m/s | 27.2 | 29.1 | 4.35 m/s | 20.3 |  | 2.15 | m/s |  | 4.35 | m/s | 19.3331 | 0.0088683 | 21.8491 |  | 0 | 697.5 | 0.6975 | 31.3249 | 7.3206 | 5.8674 | 0.023152 | 57.7857 | 1.207
2025-05-20 05:37 | 2317 | Remove | 2025-05-20 | 5:37 | ST | GS | - | 125.5 | g | 0 | 115.3 | 10.906 | 1059.5 | 6729 | 19:20 | 27.8 | 2.06 m/s | 28.6 | 29.1 | 4.24 m/s | 20.8 |  | 2.06 | m/s |  | 4.24 | m/s | 19.3414 | 0.0088292 | 21.858 |  | -1 | 697.5 | 0.6975 | 31.3376 | 7.6974 | 6.012 | 0.023325 | 57.809 | 1.2066
2025-05-20 05:38 | 2318 | Remove | 2025-05-20 | 5:38 | ST | GS | - | 125.5 | g | 0 | 115.4 | 10.857 | 1052.3 | 6738 | 19:21 | 27.8 | 2.06 m/s | 28.3 | 29.1 | 4.33 m/s | 21 |  | 2.06 | m/s |  | 4.33 | m/s | 19.3497 | 0.0087692 | 21.8667 |  | 0 | 697.5 | 0.6975 | 31.3501 | 7.6167 | 6.0698 | 0.02308 | 57.8321 | 1.2061
2025-05-20 05:38 | 2319 | Remove | 2025-05-20 | 5:38 | ST | GS | - | 128.5 | g | 0 | 115.3 | 10.88 | 1056.2 | 6747 | 19:21 | 27.8 | 2.11 m/s | 28.1 | 29.1 | 4.32 m/s | 21.2 |  | 2.11 | m/s |  | 4.32 | m/s | 19.3581 | 0.0088017 | 21.8755 |  | 3 | 700.5 | 0.7005 | 31.2284 | 7.5628 | 6.1276 | 0.023473 | 57.8556 | 1.2108
2025-05-20 05:39 | 2320 | Remove | 2025-05-20 | 5:39 | ST | GS | - | 125 | g | 0 | 115.3 | 10.894 | 1058 | 6756 | 19:22 | 27.8 | 2.08 m/s | 27.5 | 29.1 | 4.33 m/s | 20.5 |  | 2.08 | m/s |  | 4.33 | m/s | 19.3664 | 0.0088167 | 21.8843 |  | -3.5 | 700.5 | 0.7005 | 31.241 | 7.4013 | 5.9252 | 0.022645 | 57.8782 | 1.2103
2025-05-20 05:39 | 2321 | Remove | 2025-05-20 | 5:39 | ST | GS | - | 128 | g | 0 | 115.2 | 10.929 | 1062.4 | 6765 | 19:22 | 27.8 | 2.09 m/s | 27.9 | 29.1 | 4.36 m/s | 20.7 |  | 2.09 | m/s |  | 4.36 | m/s | 19.3747 | 0.0088533 | 21.8932 |  | 3 | 703.5 | 0.7035 | 31.1204 | 7.509 | 5.9831 | 0.023085 | 57.9013 | 1.215
2025-05-20 05:40 | 2322 | Remove | 2025-05-20 | 5:40 | ST | GS | - | 126 | g | 0 | 115.4 | 10.868 | 1054.3 | 6774 | 19:23 | 27.8 | 2.06 m/s | 28 | 29.1 | 4.33 m/s | 20.9 |  | 2.06 | m/s |  | 4.33 | m/s | 19.3831 | 0.0087858 | 21.902 |  | -2 | 703.5 | 0.7035 | 31.1329 | 7.5359 | 6.0409 | 0.022835 | 57.9241 | 1.2145
2025-05-20 05:40 | 2323 | Remove | 2025-05-20 | 5:40 | ST | GS | - | 127.5 | g | 0 | 115.3 | 10.862 | 1052.9 | 6782 | 19:23 | 27.8 | 2.05 m/s | 28.3 | 29.1 | 4.29 m/s | 21 |  | 2.05 | m/s |  | 4.29 | m/s | 19.3914 | 0.0087742 | 21.9108 |  | 1.5 | 705 | 0.705 | 31.0791 | 7.6167 | 6.0698 | 0.022968 | 57.9471 | 1.2166
2025-05-20 05:41 | 2324 | Remove | 2025-05-20 | 5:41 | ST | GS | - | 127.5 | g | 0 | 115.3 | 10.867 | 1054.1 | 6791 | 19:24 | 27.7 | 2.16 m/s | 29.3 | 29.1 | 4.3 m/s | 21.4 |  | 2.16 | m/s |  | 4.3 | m/s | 19.3997 | 0.0087842 | 21.9195 |  | 0 | 705 | 0.705 | 31.0916 | 7.8424 | 6.1854 | 0.024918 | 57.972 | 1.2161
2025-05-20 05:41 | 2325 | Remove | 2025-05-20 | 5:41 | ST | GS | - | 127 | g | 0 | 115.3 | 10.928 | 1062.4 | 6800 | 19:24 | 27.8 | 2.15 m/s | 28.1 | 29.1 | 4.38 m/s | 21.2 |  | 2.15 | m/s |  | 4.38 | m/s | 19.4081 | 0.0088533 | 21.9284 |  | -0.5 | 705 | 0.705 | 31.1041 | 7.5628 | 6.1276 | 0.023918 | 57.9959 | 1.2156
2025-05-20 05:42 | 2326 | Remove | 2025-05-20 | 5:42 | ST | GS | - | 125.5 | g | 0 | 115.4 | 10.865 | 1054.1 | 6809 | 19:25 | 27.8 | 2.06 m/s | 28 | 29.1 | 4.6 m/s | 20.8 |  | 2.06 | m/s |  | 4.6 | m/s | 19.4164 | 0.0087842 | 21.9372 |  | -1.5 | 705 | 0.705 | 31.1166 | 7.5359 | 6.012 | 0.022835 | 58.0188 | 1.2151
2025-05-20 05:42 | 2327 | Remove | 2025-05-20 | 5:42 | ST | GS | - | 129 | g | 0 | 115.2 | 10.89 | 1057.5 | 6818 | 19:25 | 27.8 | 2.09 m/s | 28.4 | 29.1 | 4.35 m/s | 21.7 |  | 2.09 | m/s |  | 4.35 | m/s | 19.4247 | 0.0088125 | 21.946 |  | 3.5 | 708.5 | 0.7085 | 30.9753 | 7.6436 | 6.2721 | 0.023499 | 58.0423 | 1.2207
2025-05-20 05:43 | 2328 | Remove | 2025-05-20 | 5:43 | US | GS | - | 128 | g | 0 | 115.4 | 10.901 | 1059.1 | 6827 | 19:26 | 27.8 | 2.09 m/s | 28.7 | 29.1 | 4.29 m/s | 20.7 |  | 2.09 | m/s |  | 4.29 | m/s | 19.4331 | 0.0088258 | 21.9548 |  | -1 | 708.5 | 0.7085 | 30.9877 | 7.7243 | 5.9831 | 0.023747 | 58.066 | 1.2202
2025-05-20 05:43 | 2329 | Remove | 2025-05-20 | 5:43 | ST | GS | - | 128 | g | 0 | 115.3 | 10.901 | 1059.2 | 6835 | 19:26 | 27.8 | 2.12 m/s | 29 | 29.1 | 4.32 m/s | 21.1 |  | 2.12 | m/s |  | 4.32 | m/s | 19.4417 | 0.0088267 | 21.9636 |  | 0 | 708.5 | 0.7085 | 31.0002 | 7.8051 | 6.0987 | 0.02434 | 58.0904 | 1.2197
2025-05-20 05:44 | 2330 | Remove | 2025-05-20 | 5:44 | ST | GS | - | 127 | g | 0 | 115.3 | 10.897 | 1058.2 | 6844 | 19:27 | 27.8 | 2.05 m/s | 28.6 | 29.1 | 4.32 m/s | 21.1 |  | 2.05 | m/s |  | 4.32 | m/s | 19.45 | 0.0088183 | 21.9725 |  | -1 | 708.5 | 0.7085 | 31.0127 | 7.6974 | 6.0987 | 0.023211 | 58.1136 | 1.2192
2025-05-20 05:44 | 2331 | Remove | 2025-05-20 | 5:44 | ST | GS | - | 127 | g | 0 | 115.2 | 10.937 | 1063.7 | 6853 | 19:28 | 27.8 | 2.19 m/s | 28.5 | 29.1 | 4.4 m/s | 21.5 |  | 2.19 | m/s |  | 4.4 | m/s | 19.4583 | 0.0088642 | 21.9813 |  | 0 | 708.5 | 0.7085 | 31.0252 | 7.6705 | 6.2143 | 0.02471 | 58.1383 | 1.2186
2025-05-20 05:45 | 2332 | Remove | 2025-05-20 | 5:45 | ST | GS | - | 127 | g | 0 | 115.3 | 10.924 | 1062.4 | 6862 | 19:28 | 27.8 | 2.15 m/s | 27.9 | 29.1 | 4.49 m/s | 21.3 |  | 2.15 | m/s |  | 4.49 | m/s | 19.4667 | 0.0088533 | 21.9902 |  | 0 | 708.5 | 0.7085 | 31.0377 | 7.509 | 6.1565 | 0.023748 | 58.162 | 1.2181
2025-05-20 05:45 | 2333 | Remove | 2025-05-20 | 5:45 | ST | GS | - | 127.5 | g | 0 | 115.2 | 10.922 | 1061.4 | 6871 | 19:28 | 27.9 | 2.12 m/s | 27.8 | 29.1 | 4.46 m/s | 20.7 |  | 2.12 | m/s |  | 4.46 | m/s | 19.475 | 0.008845 | 21.999 |  | 0.5 | 709 | 0.709 | 31.0282 | 7.5234 | 5.9831 | 0.023461 | 58.1855 | 1.2185
2025-05-20 05:46 | 2334 | Remove | 2025-05-20 | 5:46 | ST | GS | - | 127 | g | 0 | 115.2 | 10.932 | 1062.8 | 6880 | 19:29 | 27.9 | 2.16 m/s | 28 | 29.1 | 4.44 m/s | 20.7 |  | 2.16 | m/s |  | 4.44 | m/s | 19.4833 | 0.0088567 | 22.0079 |  | -0.5 | 709 | 0.709 | 31.0407 | 7.5776 | 5.9831 | 0.024076 | 58.2096 | 1.218
2025-05-20 05:46 | 2335 | Remove | 2025-05-20 | 5:46 | ST | GS | - | 126 | g | 0 | 115.4 | 10.89 | 1056.1 | 6889 | 19:30 | 27.8 | 2.02 m/s | 28.1 | 29.1 | 4.35 m/s | 21.2 |  | 2.02 | m/s |  | 4.35 | m/s | 19.4917 | 0.0088008 | 22.0167 |  | -1 | 709 | 0.709 | 31.0532 | 7.5628 | 6.1276 | 0.022472 | 58.232 | 1.2175
2025-05-20 05:47 | 2336 | Remove | 2025-05-20 | 5:47 | ST | GS | - | 129.5 | g | 0 | 115.3 | 10.918 | 1060.7 | 6897 | 19:30 | 27.8 | 2.15 m/s | 28 | 29.1 | 4.36 m/s | 21 |  | 2.15 | m/s |  | 4.36 | m/s | 19.5 | 0.0088392 | 22.0255 |  | 3.5 | 712.5 | 0.7125 | 30.913 | 7.5359 | 6.0698 | 0.023833 | 58.2559 | 1.2231
2025-05-20 05:47 | 2337 | Remove | 2025-05-20 | 5:47 | ST | GS | - | 127.5 | g | 0 | 115.3 | 10.927 | 1061.2 | 6906 | 19:30 | 27.8 | 2.15 m/s | 27.6 | 29.1 | 4.33 m/s | 20.6 |  | 2.15 | m/s |  | 4.33 | m/s | 19.5083 | 0.0088433 | 22.0344 |  | -2 | 712.5 | 0.7125 | 30.9254 | 7.4283 | 5.9541 | 0.023492 | 58.2794 | 1.2226
2025-05-20 05:48 | 2338 | Remove | 2025-05-20 | 5:48 | ST | GS | - | 127 | g | 0 | 115.3 | 10.91 | 1058.7 | 6915 | 19:31 | 27.8 | 2.16 m/s | 27.7 | 29.1 | 4.29 m/s | 20.6 |  | 2.16 | m/s |  | 4.29 | m/s | 19.5167 | 0.0088225 | 22.0432 |  | -0.5 | 712.5 | 0.7125 | 30.9378 | 7.4552 | 5.9541 | 0.023687 | 58.3031 | 1.2221
2025-05-20 05:48 | 2339 | Remove | 2025-05-20 | 5:48 | ST | GS | - | 127 | g | 0 | 115.3 | 10.93 | 1060.8 | 6924 | 19:32 | 27.8 | 2.19 m/s | 27.3 | 29.1 | 4.33 m/s | 20.4 |  | 2.19 | m/s |  | 4.33 | m/s | 19.525 | 0.00884 | 22.052 |  | 0 | 712.5 | 0.7125 | 30.9502 | 7.3475 | 5.8963 | 0.023669 | 58.3267 | 1.2216
2025-05-20 05:49 | 2340 | Remove | 2025-05-20 | 5:49 | ST | GS | - | 126.5 | g | 0 | 115.2 | 10.855 | 1051.8 | 6933 | 19:32 | 27.8 | 2.12 m/s | 27.7 | 29.1 | 4.43 m/s | 20.9 |  | 2.12 | m/s |  | 4.43 | m/s | 19.5333 | 0.008765 | 22.0608 |  | -0.5 | 712.5 | 0.7125 | 30.9625 | 7.4552 | 6.0409 | 0.023249 | 58.35 | 1.2211
2025-05-20 05:49 | 2341 | Keep | 2025-05-20 | 5:49 | ST | GS | - | 127 | g | 0 | 115.3 | 10.846 | 1051 | 6942 | 19:32 | 27.8 | 1.93 m/s | 28.3 | 29.1 | 4.24 m/s | 21.3 |  | 1.93 | m/s |  | 4.24 | m/s | 19.5417 | 0.0087583 | 22.0696 |  | 0.5 | 713 | 0.713 | 30.9531 | 7.6167 | 6.1565 | 0.021623 | 58.3716 | 1.2215
2025-05-20 05:50 | 2342 | Remove | 2025-05-20 | 5:50 | ST | GS | - | 127 | g | 0 | 115.3 | 10.857 | 1052.5 | 6950 | 19:33 | 27.8 | 2.05 m/s | 29.4 | 29.1 | 4.35 m/s | 21.7 |  | 2.05 | m/s |  | 4.35 | m/s | 19.55 | 0.0087708 | 22.0783 |  | 0 | 713 | 0.713 | 30.9654 | 7.9127 | 6.2721 | 0.023861 | 58.3955 | 1.221
2025-05-20 05:50 | 2343 | Remove | 2025-05-20 | 5:50 | ST | GS | - | 126.5 | g | 0 | 115.3 | 10.811 | 1046.3 | 6959 | 19:34 | 27.7 | 2.09 m/s | 28.7 | 29.1 | 4.3 m/s | 21.5 |  | 2.09 | m/s |  | 4.3 | m/s | 19.5583 | 0.0087192 | 22.087 |  | -0.5 | 713 | 0.713 | 30.9776 | 7.6818 | 6.2143 | 0.023616 | 58.4191 | 1.2205
2025-05-20 05:51 | 2344 | Remove | 2025-05-20 | 5:51 | ST | GS | - | 126.5 | g | 0 | 115.4 | 10.822 | 1048.1 | 6968 | 19:34 | 27.7 | 2.11 m/s | 29 | 29.1 | 4.3 m/s | 21.7 |  | 2.11 | m/s |  | 4.3 | m/s | 19.5667 | 0.0087342 | 22.0958 |  | 0 | 713 | 0.713 | 30.9899 | 7.7621 | 6.2721 | 0.024092 | 58.4432 | 1.22
2025-05-20 05:51 | 2345 | Remove | 2025-05-20 | 5:51 | ST | GS | - | 127 | g | 0 | 115.3 | 10.816 | 1046 | 6977 | 19:34 | 27.7 | 2.15 m/s | 29.4 | 29 | 4.33 m/s | 22.1 |  | 2.15 | m/s |  | 4.33 | m/s | 19.575 | 0.0087167 | 22.1045 |  | 0.5 | 713.5 | 0.7135 | 30.9804 | 7.8692 | 6.3529 | 0.024887 | 58.4681 | 1.2203
2025-05-20 05:52 | 2346 | Remove | 2025-05-20 | 5:52 | ST | GS | - | 127 | g | 0 | 115.3 | 10.78 | 1041.6 | 6985 | 19:35 | 27.7 | 2.11 m/s | 29.6 | 29 | 4.29 m/s | 22.8 |  | 2.11 | m/s |  | 4.29 | m/s | 19.5836 | 0.00868 | 22.1132 |  | 0 | 713.5 | 0.7135 | 30.9925 | 7.9227 | 6.5541 | 0.02459 | 58.4926 | 1.2198
2025-05-20 05:52 | 2347 | Remove | 2025-05-20 | 5:52 | ST | GS | - | 126.5 | g | 0 | 115.4 | 10.78 | 1041.2 | 6994 | 19:36 | 27.6 | 2.09 m/s | 30 | 29 | 4.35 m/s | 23.4 |  | 2.09 | m/s |  | 4.35 | m/s | 19.5919 | 0.0086767 | 22.1219 |  | -0.5 | 713.5 | 0.7135 | 31.0047 | 7.9856 | 6.7266 | 0.02455 | 58.5172 | 1.2193
2025-05-20 05:53 | 2348 | Remove | 2025-05-20 | 5:53 | ST | GS | - | 127.5 | g | 0 | 115.3 | 10.813 | 1046.5 | 7003 | 19:36 | 27.6 | 2.08 m/s | 30.6 | 29 | 4.3 m/s | 23 |  | 2.08 | m/s |  | 4.3 | m/s | 19.6003 | 0.0087208 | 22.1306 |  | 1 | 714.5 | 0.7145 | 30.9735 | 8.1453 | 6.6116 | 0.024921 | 58.5421 | 1.2205
2025-05-20 05:53 | 2349 | Remove | 2025-05-20 | 5:53 | ST | GS | - | 127.5 | g | 0 | 115.3 | 10.785 | 1042.6 | 7012 | 19:37 | 27.6 | 2.11 m/s | 31 | 29 | 4.3 m/s | 23 |  | 2.11 | m/s |  | 4.3 | m/s | 19.6086 | 0.0086883 | 22.1393 |  | 0 | 714.5 | 0.7145 | 30.9857 | 8.2518 | 6.6116 | 0.025611 | 58.5677 | 1.22
2025-05-20 05:54 | 2350 | Remove | 2025-05-20 | 5:54 | ST | GS | - | 128 | g | 0 | 115.3 | 10.778 | 1042.1 | 7020 | 19:37 | 27.6 | 2.11 m/s | 31.1 | 28.9 | 4.3 m/s | 22.9 |  | 2.11 | m/s |  | 4.3 | m/s | 19.6169 | 0.0086842 | 22.1479 |  | 0.5 | 715 | 0.715 | 30.9761 | 8.2784 | 6.547 | 0.025694 | 58.5934 | 1.2203
2025-05-20 05:54 | 2351 | Remove | 2025-05-20 | 5:54 | ST | GS | - | 130.5 | g | 0 | 115.4 | 10.829 | 1049.1 | 7029 | 19:38 | 27.6 | 2.09 m/s | 30.3 | 28.9 | 4.36 m/s | 22.1 |  | 2.09 | m/s |  | 4.36 | m/s | 19.6253 | 0.0087425 | 22.1567 |  | 2.5 | 717.5 | 0.7175 | 30.8804 | 8.0654 | 6.3183 | 0.024796 | 58.6182 | 1.224
2025-05-20 05:55 | 2352 | Remove | 2025-05-20 | 5:55 | ST | GS | - | 129.5 | g | 0 | 115.3 | 10.828 | 1048.9 | 7038 | 19:38 | 27.7 | 2.15 m/s | 29.9 | 28.9 | 4.24 m/s | 22 |  | 2.15 | m/s |  | 4.24 | m/s | 19.6336 | 0.0087408 | 22.1654 |  | -1 | 717.5 | 0.7175 | 30.8926 | 8.003 | 6.2897 | 0.02531 | 58.6435 | 1.2235
2025-05-20 05:55 | 2353 | Remove | 2025-05-20 | 5:55 | ST | GS | - | 128.5 | g | 0 | 115.2 | 10.815 | 1046.6 | 7047 | 19:39 | 27.7 | 2.08 m/s | 30 | 28.9 | 4.21 m/s | 21.9 |  | 2.08 | m/s |  | 4.21 | m/s | 19.6419 | 0.0087217 | 22.1741 |  | -1 | 717.5 | 0.7175 | 30.9047 | 8.0298 | 6.2611 | 0.024568 | 58.6681 | 1.223
2025-05-20 05:56 | 2354 | Remove | 2025-05-20 | 5:56 | ST | GS | - | 128 | g | 0 | 115.2 | 10.844 | 1050.4 | 7055 | 19:39 | 27.7 | 2.06 m/s | 29.3 | 28.9 | 4.26 m/s | 21.7 |  | 2.06 | m/s |  | 4.26 | m/s | 19.6503 | 0.0087533 | 22.1829 |  | -0.5 | 717.5 | 0.7175 | 30.9169 | 7.8424 | 6.2039 | 0.023764 | 58.6919 | 1.2225
2025-05-20 05:56 | 2355 | Remove | 2025-05-20 | 5:56 | ST | GS | - | 131 | g | 0 | 115.3 | 10.828 | 1049.2 | 7064 | 19:40 | 27.7 | 2.11 m/s | 29.5 | 29 | 4.4 m/s | 22 |  | 2.11 | m/s |  | 4.4 | m/s | 19.6586 | 0.0087433 | 22.1916 |  | 3 | 720.5 | 0.7205 | 30.8003 | 7.896 | 6.3242 | 0.024507 | 58.7164 | 1.2271
2025-05-20 05:57 | 2356 | Remove | 2025-05-20 | 5:57 | US | GS | - | 129.5 | g | 0 | 115.2 | 10.85 | 1051.8 | 7073 | 19:40 | 27.7 | 2.08 m/s | 28.6 | 29 | 4.35 m/s | 21.3 |  | 2.08 | m/s |  | 4.35 | m/s | 19.6669 | 0.008765 | 22.2004 |  | -1.5 | 720.5 | 0.7205 | 30.8125 | 7.6551 | 6.1229 | 0.023421 | 58.7398 | 1.2266
2025-05-20 05:57 | 2357 | Remove | 2025-05-20 | 5:57 | ST | GS | - | 127.5 | g | 0 | 115.2 | 10.875 | 1055 | 7082 | 19:41 | 27.7 | 1.94 m/s | 28.4 | 29 | 4.4 m/s | 21.1 |  | 1.94 | m/s |  | 4.4 | m/s | 19.6753 | 0.0087917 | 22.2092 |  | -2 | 720.5 | 0.7205 | 30.8247 | 7.6015 | 6.0655 | 0.021692 | 58.7615 | 1.2261
2025-05-20 05:58 | 2358 | Remove | 2025-05-20 | 5:58 | ST | GS | - | 128 | g | 0 | 115.3 | 10.856 | 1052.9 | 7091 | 19:41 | 27.7 | 2.11 m/s | 29 | 29 | 4.29 m/s | 21.5 |  | 2.11 | m/s |  | 4.29 | m/s | 19.6836 | 0.0087742 | 22.218 |  | 0.5 | 721 | 0.721 | 30.8155 | 7.7621 | 6.1804 | 0.024092 | 58.7856 | 1.2265
2025-05-20 05:58 | 2359 | Remove | 2025-05-20 | 5:58 | ST | GS | - | 127.5 | g | 0 | 115.3 | 10.873 | 1054.4 | 7099 | 19:42 | 27.7 | 2.13 m/s | 28.7 | 29 | 4.4 m/s | 21.4 |  | 2.13 | m/s |  | 4.4 | m/s | 19.6919 | 0.0087867 | 22.2268 |  | -0.5 | 721 | 0.721 | 30.8277 | 7.6818 | 6.1517 | 0.024068 | 58.8096 | 1.226
2025-05-20 05:59 | 2360 | Remove | 2025-05-20 | 5:59 | ST | GS | - | 129 | g | 0 | 115.2 | 10.869 | 1053.6 | 7108 | 19:42 | 27.8 | 2.16 m/s | 28.5 | 29.1 | 4.43 m/s | 21.2 |  | 2.16 | m/s |  | 4.43 | m/s | 19.7003 | 0.00878 | 22.2355 |  | 1.5 | 722.5 | 0.7225 | 30.7758 | 7.6705 | 6.1276 | 0.024371 | 58.834 | 1.228
2025-05-20 05:59 | 2361 | Remove | 2025-05-20 | 5:59 | ST | GS | - | 129 | g | 0 | 115.1 | 10.86 | 1052.4 | 7117 | 19:43 | 27.7 | 2.13 m/s | 28.4 | 29.1 | 4.3 m/s | 21.2 |  | 2.13 | m/s |  | 4.3 | m/s | 19.7086 | 0.00877 | 22.2443 |  | 0 | 722.5 | 0.7225 | 30.788 | 7.6015 | 6.1276 | 0.023817 | 58.8578 | 1.2275
2025-05-20 06:00 | 2362 | Remove | 2025-05-20 | 6:00 | ST | GS | - | 130 | g | 0 | 115.2 | 10.861 | 1053.3 | 7126 | 19:43 | 27.8 | 2.15 m/s | 28 | 29.1 | 4.6 m/s | 20.8 |  | 2.15 | m/s |  | 4.6 | m/s | 19.7169 | 0.0087775 | 22.2531 |  | 1 | 723.5 | 0.7235 | 30.7576 | 7.5359 | 6.012 | 0.023833 | 58.8817 | 1.2287
2025-05-20 06:00 | 2363 | Remove | 2025-05-20 | 6:00 | ST | GS | - | 128.5 | g | 0 | 115.1 | 10.873 | 1054.9 | 7135 | 19:44 | 27.8 | 2.16 m/s | 27.9 | 29.1 | 4.64 m/s | 20.7 |  | 2.16 | m/s |  | 4.64 | m/s | 19.7253 | 0.0087908 | 22.2619 |  | -1.5 | 723.5 | 0.7235 | 30.7697 | 7.509 | 5.9831 | 0.023858 | 58.9055 | 1.2282
2025-05-20 06:01 | 2364 | Remove | 2025-05-20 | 6:01 | ST | GS | - | 129 | g | 0 | 115 | 10.876 | 1055.5 | 7143 | 19:44 | 27.7 | 2.15 m/s | 29.3 | 29.1 | 4.23 m/s | 21.6 |  | 2.15 | m/s |  | 4.23 | m/s | 19.7336 | 0.0087958 | 22.2707 |  | 0.5 | 724 | 0.724 | 30.7606 | 7.8424 | 6.2432 | 0.024802 | 58.9303 | 1.2286
2025-05-20 06:01 | 2365 | Remove | 2025-05-20 | 6:01 | ST | GS | - | 127.5 | g | 0 | 114.8 | 10.836 | 1049.8 | 7152 | 19:45 | 27.7 | 2.06 m/s | 29.4 | 29.1 | 4.29 m/s | 20.9 |  | 2.06 | m/s |  | 4.29 | m/s | 19.7422 | 0.0087483 | 22.2794 |  | -1.5 | 724 | 0.724 | 30.7727 | 7.8692 | 6.0409 | 0.023845 | 58.9542 | 1.2281
2025-05-20 06:02 | 2366 | Remove | 2025-05-20 | 6:02 | ST | GS | - | 128 | g | 0 | 114.9 | 10.829 | 1049.2 | 7161 | 19:45 | 27.7 | 2.06 m/s | 29 | 29.1 | 4.6 m/s | 21.9 |  | 2.06 | m/s |  | 4.6 | m/s | 19.7506 | 0.0087433 | 22.2882 |  | 0.5 | 724.5 | 0.7245 | 30.7635 | 7.7621 | 6.3299 | 0.023521 | 58.9777 | 1.2284
2025-05-20 06:02 | 2367 | Remove | 2025-05-20 | 6:02 | ST | GS | - | 128.5 | g | 0 | 114.9 | 10.873 | 1055 | 7170 | 19:46 | 27.7 | 2.01 m/s | 29.1 | 29.1 | 4.44 m/s | 21.1 |  | 2.01 | m/s |  | 4.44 | m/s | 19.7589 | 0.0087917 | 22.297 |  | 0.5 | 725 | 0.725 | 30.7544 | 7.7889 | 6.0987 | 0.023029 | 59.0007 | 1.2288
2025-05-20 06:03 | 2368 | Remove | 2025-05-20 | 6:03 | ST | GS | - | 128 | g | 0 | 114.9 | 10.878 | 1055.1 | 7179 | 19:46 | 27.8 | 2.06 m/s | 28.2 | 29.1 | 4.44 m/s | 21 |  | 2.06 | m/s |  | 4.44 | m/s | 19.7672 | 0.0087925 | 22.3058 |  | -0.5 | 725 | 0.725 | 30.7666 | 7.5897 | 6.0698 | 0.022998 | 59.0237 | 1.2283
2025-05-20 06:03 | 2369 | Remove | 2025-05-20 | 6:03 | ST | GS | - | 127.5 | g | 0 | 115 | 10.822 | 1047.7 | 7187 | 19:47 | 27.7 | 2.11 m/s | 28.3 | 29.1 | 4.33 m/s | 21.5 |  | 2.11 | m/s |  | 4.33 | m/s | 19.7756 | 0.0087308 | 22.3145 |  | -0.5 | 725 | 0.725 | 30.7786 | 7.5748 | 6.2143 | 0.02351 | 59.0472 | 1.2278
2025-05-20 06:04 | 2370 | Remove | 2025-05-20 | 6:04 | ST | GS | - | 128.5 | g | 0 | 114.9 | 10.847 | 1051.3 | 7196 | 19:47 | 27.7 | 2.15 m/s | 29.1 | 29.2 | 4.23 m/s | 21.7 |  | 2.15 | m/s |  | 4.23 | m/s | 19.7839 | 0.0087608 | 22.3232 |  | 1 | 726 | 0.726 | 30.7483 | 7.7889 | 6.3064 | 0.024633 | 59.0719 | 1.229
2025-05-20 06:04 | 2371 | Keep | 2025-05-20 | 6:04 | ST | GS | - | 129.5 | g | 0 | 114.9 | 10.885 | 1056 | 7205 | 19:48 | 27.7 | 2.12 m/s | 29 | 29.1 | 4.3 m/s | 21.4 |  | 2.12 | m/s |  | 4.3 | m/s | 19.7922 | 0.0088 | 22.332 |  | 1 | 727 | 0.727 | 30.7181 | 7.7621 | 6.1854 | 0.024206 | 59.0961 | 1.2302
2025-05-20 06:05 | 2372 | Remove | 2025-05-20 | 6:05 | ST | GS | - | 128 | g | 0 | 114.9 | 10.84 | 1050.7 | 7214 | 19:48 | 27.7 | 2.08 m/s | 28.3 | 29.2 | 4.35 m/s | 21 |  | 2.08 | m/s |  | 4.35 | m/s | 19.8006 | 0.0087558 | 22.3408 |  | -1.5 | 727 | 0.727 | 30.7301 | 7.5748 | 6.103 | 0.023176 | 59.1192 | 1.2297
2025-05-20 06:05 | 2373 | Remove | 2025-05-20 | 6:05 | ST | GS | - | 127.5 | g | 0 | 114.9 | 10.823 | 1048.2 | 7223 | 19:49 | 27.7 | 1.97 m/s | 29.4 | 29.2 | 4.26 m/s | 21.2 |  | 1.97 | m/s |  | 4.26 | m/s | 19.8089 | 0.008735 | 22.3495 |  | -0.5 | 727 | 0.727 | 30.7421 | 7.8692 | 6.1611 | 0.022803 | 59.142 | 1.2292
2025-05-20 06:06 | 2374 | Remove | 2025-05-20 | 6:06 | ST | GS | - | 127 | g | 0 | 114.9 | 10.807 | 1045.6 | 7231 | 19:49 | 27.7 | 2.09 m/s | 29.3 | 29.2 | 4.33 m/s | 21.5 |  | 2.09 | m/s |  | 4.33 | m/s | 19.8172 | 0.0087133 | 22.3582 |  | -0.5 | 727 | 0.727 | 30.7541 | 7.8424 | 6.2483 | 0.02411 | 59.1662 | 1.2287
2025-05-20 06:06 | 2375 | Remove | 2025-05-20 | 6:06 | ST | GS | - | 127.5 | g | 0 | 115 | 10.781 | 1042.5 | 7240 | 19:50 | 27.6 | 2.11 m/s | 30.6 | 29.2 | 4.38 m/s | 22.5 |  | 2.11 | m/s |  | 4.38 | m/s | 19.8256 | 0.0086875 | 22.3669 |  | 0.5 | 727.5 | 0.7275 | 30.7449 | 8.1453 | 6.5389 | 0.025281 | 59.1914 | 1.2291
2025-05-20 06:07 | 2376 | Remove | 2025-05-20 | 6:07 | US | GS | - | 128 | g | 0 | 114.9 | 10.847 | 1051.7 | 7249 | 19:50 | 27.6 | 2.13 m/s | 30 | 29.1 | 4.24 m/s | 22 |  | 2.13 | m/s |  | 4.24 | m/s | 19.8339 | 0.0087642 | 22.3757 |  | 0.5 | 728 | 0.728 | 30.7359 | 7.9856 | 6.3588 | 0.02502 | 59.2165 | 1.2294
2025-05-20 06:07 | 2377 | Remove | 2025-05-20 | 6:07 | ST | GS | - | 127 | g | 0 | 114.9 | 10.841 | 1050.2 | 7257 | 19:51 | 27.7 | 2.12 m/s | 29 | 29.1 | 4.29 m/s | 21.2 |  | 2.12 | m/s |  | 4.29 | m/s | 19.8422 | 0.0087517 | 22.3845 |  | -1 | 728 | 0.728 | 30.7479 | 7.7621 | 6.1276 | 0.024206 | 59.2407 | 1.2289
2025-05-20 06:08 | 2378 | Remove | 2025-05-20 | 6:08 | US | GS | - | 127 | g | 0 | 114.9 | 10.811 | 1046.9 | 7266 | 19:51 | 27.7 | 2.12 m/s | 29.2 | 29.1 | 4.26 m/s | 21.6 |  | 2.12 | m/s |  | 4.26 | m/s | 19.8506 | 0.0087242 | 22.3932 |  | 0 | 728 | 0.728 | 30.7599 | 7.8157 | 6.2432 | 0.024373 | 59.265 | 1.2284
2025-05-20 06:08 | 2379 | Remove | 2025-05-20 | 6:08 | ST | GS | - | 127.5 | g | 0 | 115 | 10.753 | 1038.5 | 7275 | 19:52 | 27.6 | 2.12 m/s | 31.8 | 29.1 | 4.29 m/s | 22.2 |  | 2.12 | m/s |  | 4.29 | m/s | 19.8589 | 0.0086542 | 22.4018 |  | 0.5 | 728.5 | 0.7285 | 30.7506 | 8.4647 | 6.4166 | 0.026397 | 59.2914 | 1.2287
2025-05-20 06:09 | 2380 | Remove | 2025-05-20 | 6:09 | ST | GS | - | 127.5 | g | 0 | 114.9 | 10.784 | 1043.7 | 7284 | 19:52 | 27.6 | 2.09 m/s | 30.6 | 29.1 | 4.27 m/s | 22.8 |  | 2.09 | m/s |  | 4.27 | m/s | 19.8672 | 0.0086975 | 22.4105 |  | 0 | 728.5 | 0.7285 | 30.7626 | 8.1453 | 6.59 | 0.025041 | 59.3165 | 1.2282
2025-05-20 06:09 | 2381 | Remove | 2025-05-20 | 6:09 | ST | GS | - | 127.5 | g | 0 | 114.9 | 10.797 | 1044.3 | 7292 | 19:53 | 27.6 | 2.06 m/s | 30 | 29.1 | 4.32 m/s | 22 |  | 2.06 | m/s |  | 4.32 | m/s | 19.8756 | 0.0087025 | 22.4192 |  | 0 | 728.5 | 0.7285 | 30.7745 | 7.9856 | 6.3588 | 0.024198 | 59.3407 | 1.2277
2025-05-20 06:10 | 2382 | Remove | 2025-05-20 | 6:10 | ST | GS | - | 127.5 | g | 0 | 114.9 | 10.778 | 1042.9 | 7301 | 19:53 | 27.6 | 2.09 m/s | 30.1 | 29.1 | 4.24 m/s | 22.1 |  | 2.09 | m/s |  | 4.24 | m/s | 19.8839 | 0.0086908 | 22.4279 |  | 0 | 728.5 | 0.7285 | 30.7864 | 8.0122 | 6.3877 | 0.024632 | 59.3653 | 1.2271
2025-05-20 06:10 | 2383 | Remove | 2025-05-20 | 6:10 | ST | GS | - | 127 | g | 0 | 114.9 | 10.783 | 1042.6 | 7310 | 19:54 | 27.5 | 2.08 m/s | 30.8 | 29.1 | 4.29 m/s | 22.3 |  | 2.08 | m/s |  | 4.29 | m/s | 19.8925 | 0.0086883 | 22.4366 |  | -0.5 | 728.5 | 0.7285 | 30.7984 | 8.1534 | 6.4455 | 0.024946 | 59.3902 | 1.2266
2025-05-20 06:11 | 2384 | Remove | 2025-05-20 | 6:11 | ST | GS | - | 127.5 | g | 0 | 114.8 | 10.803 | 1045.4 | 7319 | 19:54 | 27.5 | 2.05 m/s | 30.9 | 29.1 | 4.3 m/s | 22.2 |  | 2.05 | m/s |  | 4.3 | m/s | 19.9008 | 0.0087117 | 22.4453 |  | 0.5 | 729 | 0.729 | 30.7892 | 8.1798 | 6.4166 | 0.024666 | 59.4149 | 1.227
2025-05-20 06:11 | 2385 | Remove | 2025-05-20 | 6:11 | ST | GS | - | 128 | g | 0 | 114.9 | 10.812 | 1046.5 | 7327 | 19:55 | 27.6 | 2.12 m/s | 30.4 | 29.1 | 4.36 m/s | 21.8 |  | 2.12 | m/s |  | 4.36 | m/s | 19.9092 | 0.0087208 | 22.454 |  | 0.5 | 729.5 | 0.7295 | 30.78 | 8.0921 | 6.301 | 0.025235 | 59.4401 | 1.2273
2025-05-20 06:12 | 2386 | Remove | 2025-05-20 | 6:12 | US | GS | - | 128 | g | 0 | 114.8 | 10.806 | 1046.4 | 7336 | 19:55 | 27.6 | 2.08 m/s | 30.1 | 29.1 | 4.23 m/s | 21.8 |  | 2.08 | m/s |  | 4.23 | m/s | 19.9175 | 0.00872 | 22.4628 |  | 0 | 729.5 | 0.7295 | 30.792 | 8.0122 | 6.301 | 0.024514 | 59.4647 | 1.2268
2025-05-20 06:12 | 2387 | Remove | 2025-05-20 | 6:12 | ST | GS | - | 128 | g | 0 | 114.8 | 10.79 | 1044.6 | 7345 | 19:56 | 27.6 | 2.12 m/s | 30 | 29.1 | 4.27 m/s | 22 |  | 2.12 | m/s |  | 4.27 | m/s | 19.9258 | 0.008705 | 22.4715 |  | 0 | 729.5 | 0.7295 | 30.8039 | 7.9856 | 6.3588 | 0.024903 | 59.4896 | 1.2263
2025-05-20 06:13 | 2388 | Remove | 2025-05-20 | 6:13 | ST | GS | - | 127.5 | g | 0 | 114.8 | 10.798 | 1045.1 | 7354 | 19:56 | 27.6 | 2.0 m/s | 30.8 | 29.1 | 4.43 m/s | 23 |  | 2 | m/s |  | 4.43 | m/s | 19.9342 | 0.0087092 | 22.4802 |  | -0.5 | 729.5 | 0.7295 | 30.8159 | 8.1985 | 6.6478 | 0.02412 | 59.5137 | 1.2258
2025-05-20 06:13 | 2389 | Remove | 2025-05-20 | 6:13 | ST | GS | - | 127.5 | g | 0 | 114.8 | 10.777 | 1043.1 | 7362 | 19:57 | 27.6 | 2.11 m/s | 31.6 | 29.1 | 4.26 m/s | 22.3 |  | 2.11 | m/s |  | 4.26 | m/s | 19.9425 | 0.0086925 | 22.4889 |  | 0 | 729.5 | 0.7295 | 30.8278 | 8.4115 | 6.4455 | 0.026107 | 59.5398 | 1.2252
2025-05-20 06:14 | 2390 | Remove | 2025-05-20 | 6:14 | ST | GS | - | 127.5 | g | 0 | 114.8 | 10.779 | 1042.2 | 7371 | 19:57 | 27.5 | 2.11 m/s | 30.3 | 29.1 | 4.29 m/s | 21.8 |  | 2.11 | m/s |  | 4.29 | m/s | 19.9508 | 0.008685 | 22.4976 |  | 0 | 729.5 | 0.7295 | 30.8397 | 8.021 | 6.301 | 0.024895 | 59.5647 | 1.2247
2025-05-20 06:14 | 2391 | Remove | 2025-05-20 | 6:14 | ST | GS | - | 129 | g | 0 | 114.6 | 10.866 | 1054.7 | 7380 | 19:58 | 27.6 | 2.16 m/s | 30.1 | 29.1 | 4.33 m/s | 21.9 |  | 2.16 | m/s |  | 4.33 | m/s | 19.9592 | 0.0087892 | 22.5063 |  | 1.5 | 731 | 0.731 | 30.7884 | 8.0122 | 6.3299 | 0.025457 | 59.5901 | 1.2267
2025-05-20 06:15 | 2392 | Remove | 2025-05-20 | 6:15 | ST | GS | - | 127 | g | 0 | 114.7 | 10.813 | 1047.9 | 7388 | 19:58 | 27.6 | 2.15 m/s | 29.6 | 29.1 | 4.26 m/s | 21.3 |  | 2.15 | m/s |  | 4.26 | m/s | 19.9675 | 0.0087325 | 22.5151 |  | -2 | 731 | 0.731 | 30.8004 | 7.8791 | 6.1565 | 0.024918 | 59.6151 | 1.2262
2025-05-20 06:15 | 2393 | Remove | 2025-05-20 | 6:15 | ST | GS | - | 129.5 | g | 0 | 114.7 | 10.831 | 1050.3 | 7397 | 19:59 | 27.6 | 2.09 m/s | 31.7 | 29.1 | 4.26 m/s | 22.1 |  | 2.09 | m/s |  | 4.26 | m/s | 19.9758 | 0.0087525 | 22.5238 |  | 2.5 | 733.5 | 0.7335 | 30.7073 | 8.4381 | 6.3877 | 0.025941 | 59.641 | 1.2299
2025-05-20 06:16 | 2394 | Remove | 2025-05-20 | 6:16 | ST | GS | - | 127 | g | 0 | 114.7 | 10.834 | 1049.2 | 7406 | 19:59 | 27.6 | 2.06 m/s | 29.6 | 29.2 | 4.26 m/s | 21.6 |  | 2.06 | m/s |  | 4.26 | m/s | 19.9842 | 0.0087433 | 22.5326 |  | -2.5 | 733.5 | 0.7335 | 30.7193 | 7.8791 | 6.2773 | 0.023875 | 59.6649 | 1.2294
2025-05-20 06:16 | 2395 | Remove | 2025-05-20 | 6:16 | ST | GS | - | 127.5 | g | 0 | 114.7 | 10.778 | 1043.4 | 7415 | 20:00 | 27.6 | 2.08 m/s | 30 | 29.2 | 4.41 m/s | 22.3 |  | 2.08 | m/s |  | 4.41 | m/s | 19.9925 | 0.008695 | 22.5413 |  | 0.5 | 734 | 0.734 | 30.7102 | 7.9856 | 6.4808 | 0.024433 | 59.6893 | 1.2297
2025-05-20 06:17 | 2396 | Remove | 2025-05-20 | 6:17 | ST | GS | - | 130 | g | 0 | 114.7 | 10.854 | 1053.5 | 7424 | 20:00 | 27.6 | 2.13 m/s | 30 | 29.2 | 4.24 m/s | 22 |  | 2.13 | m/s |  | 4.24 | m/s | 20.0008 | 0.0087792 | 22.55 |  | 2.5 | 736.5 | 0.7365 | 30.6178 | 7.9856 | 6.3936 | 0.02502 | 59.7143 | 1.2334
2025-05-20 06:17 | 2397 | Remove | 2025-05-20 | 6:17 | ST | GS | - | 130 | g | 0 | 114.7 | 10.883 | 1056.9 | 7432 | 20:01 | 27.7 | 2.19 m/s | 29.2 | 29.2 | 4.23 m/s | 20.7 |  | 2.19 | m/s |  | 4.23 | m/s | 20.0092 | 0.0088075 | 22.5589 |  | 0 | 736.5 | 0.7365 | 30.6298 | 7.8157 | 6.0158 | 0.025177 | 59.7395 | 1.2329
2025-05-20 06:18 | 2398 | Remove | 2025-05-20 | 6:18 | ST | GS | - | 127.5 | g | 0 | 114.6 | 10.838 | 1051.1 | 7441 | 20:01 | 27.7 | 2.13 m/s | 29 | 29.2 | 4.29 m/s | 21.2 |  | 2.13 | m/s |  | 4.29 | m/s | 20.0178 | 0.0087592 | 22.5676 |  | -2.5 | 736.5 | 0.7365 | 30.6417 | 7.7621 | 6.1611 | 0.02432 | 59.7638 | 1.2324
2025-05-20 06:18 | 2399 | Remove | 2025-05-20 | 6:18 | ST | GS | - | 127 | g | 0 | 114.7 | 10.817 | 1048.4 | 7450 | 20:02 | 27.6 | 2.11 m/s | 29.6 | 29.2 | 4.36 m/s | 21.7 |  | 2.11 | m/s |  | 4.36 | m/s | 20.0261 | 0.0087367 | 22.5763 |  | -0.5 | 736.5 | 0.7365 | 30.6536 | 7.8791 | 6.3064 | 0.024455 | 59.7883 | 1.2318
2025-05-20 06:19 | 2400 | Remove | 2025-05-20 | 6:19 | ST | GS | - | 127 | g | 0 | 114.7 | 10.856 | 1053.6 | 7459 | 20:02 | 27.7 | 2.09 m/s | 30.1 | 29.2 | 4.26 m/s | 21.6 |  | 2.09 | m/s |  | 4.26 | m/s | 20.0347 | 0.00878 | 22.5851 |  | 0 | 736.5 | 0.7365 | 30.6655 | 8.0566 | 6.2773 | 0.024768 | 59.8131 | 1.2313
2025-05-20 06:19 | 2401 | Keep | 2025-05-20 | 6:19 | ST | GS | - | 127.5 | g | 0 | 114.7 | 10.839 | 1051.1 | 7468 | 20:03 | 27.7 | 2.12 m/s | 29.3 | 29.2 | 4.27 m/s | 21.8 |  | 2.12 | m/s |  | 4.27 | m/s | 20.0431 | 0.0087592 | 22.5939 |  | 0.5 | 737 | 0.737 | 30.6566 | 7.8424 | 6.3355 | 0.024456 | 59.8375 | 1.2317
2025-05-20 06:20 | 2402 | Remove | 2025-05-20 | 6:20 | ST | GS | - | 126.5 | g | 0 | 114.7 | 10.829 | 1050.5 | 7476 | 20:03 | 27.7 | 2.08 m/s | 28.9 | 29.2 | 4.26 m/s | 21.3 |  | 2.08 | m/s |  | 4.26 | m/s | 20.0514 | 0.0087542 | 22.6026 |  | -1 | 737 | 0.737 | 30.6684 | 7.7354 | 6.1902 | 0.023667 | 59.8612 | 1.2312
2025-05-20 06:20 | 2403 | Remove | 2025-05-20 | 6:20 | ST | GS | - | 129.5 | g | 0 | 114.7 | 10.856 | 1054.2 | 7485 | 20:04 | 27.7 | 2.09 m/s | 29.9 | 29.2 | 4.26 m/s | 21.9 |  | 2.09 | m/s |  | 4.26 | m/s | 20.0597 | 0.008785 | 22.6114 |  | 3 | 740 | 0.74 | 30.556 | 8.003 | 6.3645 | 0.024604 | 59.8858 | 1.2357
2025-05-20 06:21 | 2404 | Remove | 2025-05-20 | 6:21 | ST | GS | - | 127 | g | 0 | 114.7 | 10.874 | 1056.8 | 7494 | 20:04 | 27.7 | 2.11 m/s | 28.7 | 29.2 | 4.29 m/s | 20.7 |  | 2.11 | m/s |  | 4.29 | m/s | 20.0681 | 0.0088067 | 22.6202 |  | -2.5 | 740 | 0.74 | 30.5679 | 7.6818 | 6.0158 | 0.023842 | 59.9096 | 1.2352
2025-05-20 06:21 | 2405 | Remove | 2025-05-20 | 6:21 | ST | GS | - | 127.5 | g | 0 | 114.7 | 10.836 | 1051.7 | 7503 | 20:05 | 27.7 | 2.02 m/s | 29.5 | 29.2 | 4.21 m/s | 21.6 |  | 2.02 | m/s |  | 4.21 | m/s | 20.0764 | 0.0087642 | 22.629 |  | 0.5 | 740.5 | 0.7405 | 30.5591 | 7.896 | 6.2773 | 0.023462 | 59.9331 | 1.2355
2025-05-20 06:22 | 2406 | Remove | 2025-05-20 | 6:22 | ST | GS | - | 127.5 | g | 0 | 114.6 | 10.809 | 1048.3 | 7512 | 20:05 | 27.7 | 2.09 m/s | 29.8 | 29.2 | 4.3 m/s | 21.7 |  | 2.09 | m/s |  | 4.3 | m/s | 20.0847 | 0.0087358 | 22.6377 |  | 0 | 740.5 | 0.7405 | 30.5709 | 7.9763 | 6.3064 | 0.024522 | 59.9576 | 1.235
2025-05-20 06:22 | 2407 | Remove | 2025-05-20 | 6:22 | ST | GS | - | 127.5 | g | 0 | 114.7 | 10.833 | 1051.4 | 7520 | 20:06 | 27.7 | 2.11 m/s | 29.7 | 29.2 | 4.35 m/s | 22.3 |  | 2.11 | m/s |  | 4.35 | m/s | 20.0931 | 0.0087617 | 22.6465 |  | 0 | 740.5 | 0.7405 | 30.5827 | 7.9495 | 6.4808 | 0.024673 | 59.9823 | 1.2345
2025-05-20 06:23 | 2408 | Remove | 2025-05-20 | 6:23 | ST | GS | - | 127.5 | g | 0 | 114.7 | 10.788 | 1045.1 | 7529 | 20:06 | 27.6 | 2.06 m/s | 29.8 | 29.2 | 4.32 m/s | 22.2 |  | 2.06 | m/s |  | 4.32 | m/s | 20.1014 | 0.0087092 | 22.6552 |  | 0 | 740.5 | 0.7405 | 30.5945 | 7.9323 | 6.4517 | 0.024037 | 60.0063 | 1.234
2025-05-20 06:23 | 2409 | Remove | 2025-05-20 | 6:23 | ST | GS | - | 128.5 | g | 0 | 114.7 | 10.855 | 1054 | 7538 | 20:07 | 27.6 | 2.08 m/s | 30.8 | 29.2 | 4.29 m/s | 22.1 |  | 2.08 | m/s |  | 4.29 | m/s | 20.1097 | 0.0087833 | 22.664 |  | 1 | 741.5 | 0.7415 | 30.5651 | 8.1985 | 6.4227 | 0.025084 | 60.0314 | 1.2352
2025-05-20 06:24 | 2410 | Remove | 2025-05-20 | 6:24 | US | GS | - | 127 | g | 0 | 114.6 | 10.864 | 1055.9 | 7547 | 20:07 | 27.7 | 2.11 m/s | 29.3 | 29.2 | 4.3 m/s | 20.9 |  | 2.11 | m/s |  | 4.3 | m/s | 20.1181 | 0.0087992 | 22.6728 |  | -1.5 | 741.5 | 0.7415 | 30.5769 | 7.8424 | 6.0739 | 0.024341 | 60.0557 | 1.2347
2025-05-20 06:24 | 2411 | Remove | 2025-05-20 | 6:24 | ST | GS | - | 129 | g | 0 | 114.5 | 10.911 | 1061.8 | 7556 | 20:08 | 27.7 | 2.13 m/s | 29.5 | 29.3 | 4.33 m/s | 21 |  | 2.13 | m/s |  | 4.33 | m/s | 20.1264 | 0.0088483 | 22.6816 |  | 2 | 743.5 | 0.7435 | 30.5066 | 7.896 | 6.1363 | 0.024739 | 60.0805 | 1.2375
2025-05-20 06:25 | 2412 | Remove | 2025-05-20 | 6:25 | ST | GS | - | 128 | g | 0 | 114.6 | 10.902 | 1060.4 | 7564 | 20:08 | 27.8 | 2.22 m/s | 28.9 | 29.3 | 4.32 m/s | 20.8 |  | 2.22 | m/s |  | 4.32 | m/s | 20.1347 | 0.0088367 | 22.6905 |  | -1 | 743.5 | 0.7435 | 30.5185 | 7.7781 | 6.0779 | 0.0254 | 60.1059 | 1.237
2025-05-20 06:25 | 2413 | Remove | 2025-05-20 | 6:25 | ST | GS | - | 129 | g | 0 | 114.6 | 10.885 | 1058.3 | 7573 | 20:09 | 27.8 | 2.18 m/s | 29.2 | 29.3 | 4.27 m/s | 21.3 |  | 2.18 | m/s |  | 4.27 | m/s | 20.1431 | 0.0088192 | 22.6993 |  | 1 | 744.5 | 0.7445 | 30.4893 | 7.8589 | 6.224 | 0.025201 | 60.1311 | 1.2381
2025-05-20 06:26 | 2414 | Remove | 2025-05-20 | 6:26 | ST | GS | - | 128 | g | 0 | 114.7 | 10.875 | 1057 | 7582 | 20:09 | 27.8 | 2.02 m/s | 28.8 | 29.3 | 4.21 m/s | 20.9 |  | 2.02 | m/s |  | 4.21 | m/s | 20.1514 | 0.0088083 | 22.7081 |  | -1 | 744.5 | 0.7445 | 30.5011 | 7.7512 | 6.1071 | 0.023032 | 60.1541 | 1.2377
2025-05-20 06:26 | 2415 | Remove | 2025-05-20 | 6:26 | ST | GS | - | 128.5 | g | 0 | 114.6 | 10.894 | 1059.6 | 7591 | 20:10 | 27.8 | 2.08 m/s | 30 | 29.3 | 4.26 m/s | 21.2 |  | 2.08 | m/s |  | 4.26 | m/s | 20.1597 | 0.00883 | 22.7169 |  | 0.5 | 745 | 0.745 | 30.4925 | 8.0742 | 6.1948 | 0.024704 | 60.1788 | 1.238
2025-05-20 06:27 | 2416 | Remove | 2025-05-20 | 6:27 | ST | GS | - | 126 | g | 0 | 114.6 | 10.9 | 1060.5 | 7600 | 20:10 | 27.8 | 2.02 m/s | 29.2 | 29.3 | 4.29 m/s | 21.1 |  | 2.02 | m/s |  | 4.29 | m/s | 20.1681 | 0.0088375 | 22.7258 |  | -2.5 | 745 | 0.745 | 30.5044 | 7.8589 | 6.1656 | 0.023351 | 60.2022 | 1.2375
2025-05-20 06:27 | 2417 | Remove | 2025-05-20 | 6:27 | US | GS | - | 129.5 | g | 0 | 114.6 | 10.906 | 1061.4 | 7609 | 20:11 | 27.8 | 2.19 m/s | 29.9 | 29.3 | 4.29 m/s | 21.1 |  | 2.19 | m/s |  | 4.29 | m/s | 20.1767 | 0.008845 | 22.7346 |  | 3.5 | 748.5 | 0.7485 | 30.3736 | 8.0473 | 6.1656 | 0.025924 | 60.2281 | 1.2428
2025-05-20 06:28 | 2418 | Remove | 2025-05-20 | 6:28 | ST | GS | - | 127.5 | g | 0 | 114.7 | 10.873 | 1056.6 | 7617 | 20:11 | 27.8 | 2.02 m/s | 30.5 | 29.3 | 4.27 m/s | 21.7 |  | 2.02 | m/s |  | 4.27 | m/s | 20.185 | 0.008805 | 22.7434 |  | -2 | 748.5 | 0.7485 | 30.3853 | 8.2088 | 6.3409 | 0.024391 | 60.2525 | 1.2423
2025-05-20 06:28 | 2419 | Remove | 2025-05-20 | 6:28 | US | GS | - | 129 | g | 0 | 114.7 | 10.887 | 1058.1 | 7626 | 20:12 | 27.8 | 2.12 m/s | 29.5 | 29.3 | 4.23 m/s | 20.8 |  | 2.12 | m/s |  | 4.23 | m/s | 20.1933 | 0.0088175 | 22.7522 |  | 1.5 | 750 | 0.75 | 30.3363 | 7.9396 | 6.0779 | 0.024759 | 60.2772 | 1.2443
2025-05-20 06:29 | 2420 | Remove | 2025-05-20 | 6:29 | ST | GS | - | 129 | g | 0 | 114.6 | 10.956 | 1068 | 7635 | 20:12 | 27.8 | 2.18 m/s | 28.9 | 29.3 | 4.43 m/s | 20.7 |  | 2.18 | m/s |  | 4.43 | m/s | 20.2017 | 0.0089 | 22.7611 |  | 0 | 750 | 0.75 | 30.3482 | 7.7781 | 6.0487 | 0.024942 | 60.3022 | 1.2437
2025-05-20 06:29 | 2421 | Remove | 2025-05-20 | 6:29 | ST | GS | - | 129 | g | 0 | 114.6 | 10.945 | 1066.1 | 7644 | 20:13 | 27.8 | 2.06 m/s | 28.6 | 29.4 | 4.27 m/s | 20.6 |  | 2.06 | m/s |  | 4.27 | m/s | 20.21 | 0.0088842 | 22.77 |  | 0 | 750 | 0.75 | 30.36 | 7.6974 | 6.0524 | 0.023325 | 60.3255 | 1.2433
2025-05-20 06:30 | 2422 | Remove | 2025-05-20 | 6:30 | ST | GS | - | 127 | g | 0 | 114.6 | 10.938 | 1065 | 7653 | 20:13 | 27.9 | 2.06 m/s | 28.4 | 29.4 | 4.23 m/s | 20.3 |  | 2.06 | m/s |  | 4.23 | m/s | 20.2183 | 0.008875 | 22.7789 |  | -2 | 750 | 0.75 | 30.3719 | 7.6858 | 5.9642 | 0.023289 | 60.3488 | 1.2428
2025-05-20 06:30 | 2423 | Remove | 2025-05-20 | 6:30 | ST | GS | - | 127.5 | g | 0 | 114.5 | 10.951 | 1067.4 | 7662 | 20:14 | 27.9 | 2.08 m/s | 28.9 | 29.4 | 4.33 m/s | 20.8 |  | 2.08 | m/s |  | 4.33 | m/s | 20.2267 | 0.008895 | 22.7878 |  | 0.5 | 750.5 | 0.7505 | 30.3635 | 7.8211 | 6.1111 | 0.02393 | 60.3727 | 1.2431
2025-05-20 06:31 | 2424 | Remove | 2025-05-20 | 6:31 | ST | GS | - | 128 | g | 0 | 114.7 | 10.957 | 1067.6 | 7671 | 20:14 | 27.9 | 2.13 m/s | 28.7 | 29.4 | 4.26 m/s | 20.5 |  | 2.13 | m/s |  | 4.26 | m/s | 20.235 | 0.0088967 | 22.7967 |  | 0.5 | 751 | 0.751 | 30.3551 | 7.767 | 6.023 | 0.024335 | 60.3971 | 1.2434
2025-05-20 06:31 | 2425 | Remove | 2025-05-20 | 6:31 | ST | GS | - | 126.5 | g | 0 | 114.6 | 10.944 | 1066.2 | 7680 | 20:15 | 27.9 | 2.15 m/s | 28.2 | 29.4 | 4.3 m/s | 20.4 |  | 2.15 | m/s |  | 4.3 | m/s | 20.2433 | 0.008885 | 22.8056 |  | -1.5 | 751 | 0.751 | 30.3669 | 7.6317 | 5.9936 | 0.024136 | 60.4212 | 1.2429
2025-05-20 06:32 | 2426 | Remove | 2025-05-20 | 6:32 | ST | GS | - | 127 | g | 0 | 114.6 | 10.932 | 1064 | 7689 | 20:15 | 27.9 | 2.11 m/s | 28.4 | 29.4 | 4.26 m/s | 20.6 |  | 2.11 | m/s |  | 4.26 | m/s | 20.2517 | 0.0088667 | 22.8144 |  | 0.5 | 751.5 | 0.7515 | 30.3585 | 7.6858 | 6.0524 | 0.023855 | 60.4451 | 1.2433
2025-05-20 06:32 | 2427 | Remove | 2025-05-20 | 6:32 | ST | GS | - | 127.5 | g | 0 | 114.7 | 10.906 | 1061 | 7698 | 20:16 | 27.8 | 2.13 m/s | 29.4 | 29.4 | 4.44 m/s | 21.4 |  | 2.13 | m/s |  | 4.44 | m/s | 20.26 | 0.0088417 | 22.8233 |  | 0.5 | 752 | 0.752 | 30.3501 | 7.9127 | 6.2874 | 0.024792 | 60.4698 | 1.2436
2025-05-20 06:33 | 2428 | Remove | 2025-05-20 | 6:33 | ST | GS | - | 127.5 | g | 0 | 114.5 | 10.91 | 1062 | 7706 | 20:16 | 27.8 | 2.05 m/s | 29.6 | 29.4 | 4.38 m/s | 21.5 |  | 2.05 | m/s |  | 4.38 | m/s | 20.2683 | 0.00885 | 22.8321 |  | 0 | 752 | 0.752 | 30.3619 | 7.9665 | 6.3168 | 0.024023 | 60.4939 | 1.2431
2025-05-20 06:33 | 2429 | Remove | 2025-05-20 | 6:33 | ST | GS | - | 127.5 | g | 0 | 114.6 | 10.881 | 1057.7 | 7715 | 20:17 | 27.8 | 2.08 m/s | 29.9 | 29.4 | 4.32 m/s | 21.9 |  | 2.08 | m/s |  | 4.32 | m/s | 20.2767 | 0.0088142 | 22.8409 |  | 0 | 752 | 0.752 | 30.3736 | 8.0473 | 6.4343 | 0.024622 | 60.5185 | 1.2426
2025-05-20 06:34 | 2430 | Remove | 2025-05-20 | 6:34 | ST | GS | - | 127.5 | g | 0 | 114.6 | 10.893 | 1059.3 | 7724 | 20:17 | 27.8 | 2.09 m/s | 29.8 | 29.4 | 4.41 m/s | 21.9 |  | 2.09 | m/s |  | 4.41 | m/s | 20.285 | 0.0088275 | 22.8498 |  | 0 | 752 | 0.752 | 30.3853 | 8.0204 | 6.4343 | 0.024657 | 60.5431 | 1.2421
2025-05-20 06:34 | 2431 | Keep | 2025-05-20 | 6:34 | ST | GS | - | 127.5 | g | 0 | 114.6 | 10.876 | 1056.5 | 7733 | 20:18 | 27.7 | 2.09 m/s | 30.6 | 29.4 | 4.33 m/s | 22.7 |  | 2.09 | m/s |  | 4.33 | m/s | 20.2933 | 0.0088042 | 22.8586 |  | 0 | 752 | 0.752 | 30.397 | 8.1904 | 6.6693 | 0.02518 | 60.5683 | 1.2416
2025-05-20 06:35 | 2432 | Remove | 2025-05-20 | 6:35 | ST | GS | - | 127.5 | g | 0 | 114.6 | 10.938 | 1065 | 7742 | 20:18 | 27.7 | 2.06 m/s | 30.3 | 29.4 | 4.32 m/s | 21.5 |  | 2.06 | m/s |  | 4.32 | m/s | 20.3017 | 0.008875 | 22.8674 |  | 0 | 752 | 0.752 | 30.4088 | 8.1101 | 6.3168 | 0.024575 | 60.5929 | 1.2411
2025-05-20 06:35 | 2433 | Remove | 2025-05-20 | 6:35 | ST | GS | - | 129.5 | g | 0 | 114.5 | 10.947 | 1066.5 | 7751 | 20:19 | 27.8 | 2.04 m/s | 29.1 | 29.4 | 4.27 m/s | 20.5 |  | 2.04 | m/s |  | 4.27 | m/s | 20.31 | 0.0088875 | 22.8763 |  | 2 | 754 | 0.754 | 30.34 | 7.832 | 6.023 | 0.023502 | 60.6164 | 1.2439
2025-05-20 06:36 | 2434 | Remove | 2025-05-20 | 6:36 | ST | GS | - | 130.5 | g | 0 | 114.5 | 10.912 | 1062 | 7760 | 20:19 | 27.8 | 2.08 m/s | 29.5 | 29.4 | 4.3 m/s | 21.2 |  | 2.08 | m/s |  | 4.3 | m/s | 20.3186 | 0.00885 | 22.8852 |  | 1 | 755 | 0.755 | 30.3115 | 7.9396 | 6.2286 | 0.024292 | 60.6407 | 1.245
2025-05-20 06:36 | 2435 | Remove | 2025-05-20 | 6:36 | ST | GS | - | 128 | g | 0 | 114.5 | 10.979 | 1070.9 | 7769 | 20:20 | 27.9 | 2.06 m/s | 28.7 | 29.4 | 4.64 m/s | 20.4 |  | 2.06 | m/s |  | 4.64 | m/s | 20.3269 | 0.0089242 | 22.8941 |  | -2.5 | 755 | 0.755 | 30.3233 | 7.767 | 5.9936 | 0.023535 | 60.6642 | 1.2446
2025-05-20 06:37 | 2436 | Remove | 2025-05-20 | 6:37 | ST | GS | - | 127.5 | g | 0 | 114.4 | 10.952 | 1067 | 7778 | 20:20 | 27.8 | 2.11 m/s | 30.6 | 29.5 | 4.33 m/s | 21.4 |  | 2.11 | m/s |  | 4.33 | m/s | 20.3353 | 0.0088917 | 22.903 |  | -0.5 | 755 | 0.755 | 30.3351 | 8.2357 | 6.3217 | 0.025561 | 60.6898 | 1.244
2025-05-20 06:37 | 2437 | Remove | 2025-05-20 | 6:37 | ST | GS | - | 127.5 | g | 0 | 114.5 | 10.926 | 1063.8 | 7786 | 20:21 | 27.8 | 2.02 m/s | 29.9 | 29.5 | 4.38 m/s | 21.8 |  | 2.02 | m/s |  | 4.38 | m/s | 20.3436 | 0.008865 | 22.9119 |  | 0 | 755 | 0.755 | 30.3468 | 8.0473 | 6.4399 | 0.023911 | 60.7137 | 1.2435
2025-05-20 06:38 | 2438 | Remove | 2025-05-20 | 6:38 | ST | GS | - | 127.5 | g | 0 | 114.4 | 10.903 | 1060.9 | 7795 | 20:21 | 27.8 | 2.09 m/s | 29.6 | 29.5 | 4.29 m/s | 21.9 |  | 2.09 | m/s |  | 4.29 | m/s | 20.3519 | 0.0088408 | 22.9207 |  | 0 | 755 | 0.755 | 30.3586 | 7.9665 | 6.4694 | 0.024492 | 60.7382 | 1.243
2025-05-20 06:38 | 2439 | Remove | 2025-05-20 | 6:38 | ST | GS | - | 127.5 | g | 0 | 114.5 | 10.881 | 1058 | 7804 | 20:22 | 27.8 | 2.06 m/s | 30 | 29.5 | 4.35 m/s | 21.9 |  | 2.06 | m/s |  | 4.35 | m/s | 20.3603 | 0.0088167 | 22.9295 |  | 0 | 755 | 0.755 | 30.3702 | 8.0742 | 6.4694 | 0.024466 | 60.7627 | 1.2425
2025-05-20 06:39 | 2440 | Remove | 2025-05-20 | 6:39 | ST | GS | - | 129 | g | 0 | 114.4 | 10.96 | 1068.4 | 7813 | 20:22 | 27.8 | 2.08 m/s | 29.5 | 29.5 | 4.3 m/s | 21 |  | 2.08 | m/s |  | 4.3 | m/s | 20.3686 | 0.0089033 | 22.9384 |  | 1.5 | 756.5 | 0.7565 | 30.3218 | 7.9396 | 6.2036 | 0.024292 | 60.787 | 1.2445
2025-05-20 06:39 | 2441 | Remove | 2025-05-20 | 6:39 | ST | GS | - | 127.5 | g | 0 | 114.4 | 10.925 | 1063.4 | 7822 | 20:23 | 27.8 | 2.04 m/s | 30.6 | 29.5 | 4.32 m/s | 21.3 |  | 2.04 | m/s |  | 4.32 | m/s | 20.3769 | 0.0088617 | 22.9473 |  | -1.5 | 756.5 | 0.7565 | 30.3335 | 8.2357 | 6.2922 | 0.024713 | 60.8117 | 1.244
2025-05-20 06:40 | 2442 | Remove | 2025-05-20 | 6:40 | ST | GS | - | 127.5 | g | 0 | 114.4 | 10.94 | 1065.8 | 7831 | 20:23 | 27.8 | 2.05 m/s | 30.1 | 29.5 | 4.29 m/s | 21.4 |  | 2.05 | m/s |  | 4.29 | m/s | 20.3853 | 0.0088817 | 22.9562 |  | 0 | 756.5 | 0.7565 | 30.3452 | 8.1011 | 6.3217 | 0.024429 | 60.8361 | 1.2435
2025-05-20 06:40 | 2443 | Remove | 2025-05-20 | 6:40 | ST | GS | - | 128.5 | g | 0 | 114.4 | 10.952 | 1067.6 | 7840 | 20:24 | 27.8 | 2.08 m/s | 29.9 | 29.5 | 4.27 m/s | 21.1 |  | 2.08 | m/s |  | 4.27 | m/s | 20.3936 | 0.0088967 | 22.9651 |  | 1 | 757.5 | 0.7575 | 30.3169 | 8.0473 | 6.2331 | 0.024622 | 60.8607 | 1.2446
2025-05-20 06:41 | 2444 | Remove | 2025-05-20 | 6:41 | ST | GS | - | 129 | g | 0 | 114.2 | 10.984 | 1071.4 | 7849 | 20:24 | 27.9 | 1.81 m/s | 29.6 | 29.5 | 4.27 m/s | 21.3 |  | 1.81 | m/s |  | 4.27 | m/s | 20.4019 | 0.0089283 | 22.974 |  | 0.5 | 758 | 0.758 | 30.3087 | 8.0106 | 6.2922 | 0.021328 | 60.882 | 1.245
2025-05-20 06:41 | 2445 | Remove | 2025-05-20 | 6:41 | ST | GS | - | 127.5 | g | 0 | 114.4 | 10.97 | 1070 | 7858 | 20:25 | 27.9 | 1.95 m/s | 29.8 | 29.5 | 4.2 m/s | 21.4 |  | 1.95 | m/s |  | 4.2 | m/s | 20.4103 | 0.0089167 | 22.9829 |  | -1.5 | 758 | 0.758 | 30.3205 | 8.0647 | 6.3217 | 0.023133 | 60.9052 | 1.2446
2025-05-20 06:42 | 2446 | Remove | 2025-05-20 | 6:42 | ST | GS | - | 128.5 | g | 0 | 114.3 | 11.003 | 1074 | 7867 | 20:25 | 27.9 | 2.11 m/s | 29 | 29.5 | 4.29 m/s | 20.5 |  | 2.11 | m/s |  | 4.29 | m/s | 20.4186 | 0.00895 | 22.9919 |  | 1 | 759 | 0.759 | 30.2923 | 7.8482 | 6.0559 | 0.024359 | 60.9295 | 1.2457
2025-05-20 06:42 | 2447 | Remove | 2025-05-20 | 6:42 | ST | GS | - | 128.5 | g | 0 | 114.3 | 10.996 | 1073.7 | 7876 | 20:26 | 27.9 | 2.08 m/s | 29.1 | 29.6 | 4.26 m/s | 20.7 |  | 2.08 | m/s |  | 4.26 | m/s | 20.4269 | 0.0089475 | 23.0008 |  | 0 | 759 | 0.759 | 30.3041 | 7.8753 | 6.1483 | 0.024095 | 60.9536 | 1.2452
2025-05-20 06:43 | 2448 | Remove | 2025-05-20 | 6:43 | ST | GS | - | 128 | g | 0 | 114.3 | 10.99 | 1072.3 | 7885 | 20:26 | 27.9 | 2.05 m/s | 30.7 | 29.6 | 4.41 m/s | 21.3 |  | 2.05 | m/s |  | 4.41 | m/s | 20.4353 | 0.0089358 | 23.0097 |  | -0.5 | 759 | 0.759 | 30.3159 | 8.3083 | 6.3265 | 0.025053 | 60.9787 | 1.2447
2025-05-20 06:43 | 2449 | Remove | 2025-05-20 | 6:43 | ST | GS | - | 127.5 | g | 0 | 114.2 | 11.002 | 1073.9 | 7894 | 20:27 | 27.9 | 2.08 m/s | 29.3 | 29.6 | 4.29 m/s | 21.1 |  | 2.08 | m/s |  | 4.29 | m/s | 20.4436 | 0.0089492 | 23.0187 |  | -0.5 | 759 | 0.759 | 30.3277 | 7.9294 | 6.2671 | 0.024261 | 61.0029 | 1.2442
2025-05-20 06:44 | 2450 | Remove | 2025-05-20 | 6:44 | ST | GS | - | 128.5 | g | 0 | 114.2 | 11.005 | 1074.7 | 7902 | 20:27 | 27.9 | 2.08 m/s | 29.2 | 29.6 | 4.24 m/s | 20.5 |  | 2.08 | m/s |  | 4.24 | m/s | 20.4519 | 0.0089558 | 23.0277 |  | 1 | 760 | 0.76 | 30.2995 | 7.9023 | 6.0889 | 0.024178 | 61.0271 | 1.2453
2025-05-20 06:44 | 2451 | Remove | 2025-05-20 | 6:44 | ST | GS | - | 130.5 | g | 0 | 114.3 | 11.016 | 1076.1 | 7911 | 20:28 | 28 | 2.13 m/s | 28.6 | 29.6 | 4.3 m/s | 20.5 |  | 2.13 | m/s |  | 4.3 | m/s | 20.4606 | 0.0089675 | 23.0366 |  | 2 | 762 | 0.762 | 30.2318 | 7.7827 | 6.0889 | 0.024384 | 61.0515 | 1.2481
2025-05-20 06:45 | 2452 | Remove | 2025-05-20 | 6:45 | ST | GS | - | 130.5 | g | 0 | 114.3 | 11.012 | 1075.6 | 7921 | 20:28 | 28 | 2.06 m/s | 27.9 | 29.6 | 4.36 m/s | 19.7 |  | 2.06 | m/s |  | 4.36 | m/s | 20.4689 | 0.0089633 | 23.0456 |  | 0 | 762 | 0.762 | 30.2435 | 7.5922 | 5.8513 | 0.023006 | 61.0745 | 1.2477
2025-05-20 06:45 | 2453 | Remove | 2025-05-20 | 6:45 | ST | GS | - | 129.5 | g | 0 | 114.4 | 11.022 | 1076.7 | 7929 | 20:29 | 28 | 2.09 m/s | 28.8 | 29.7 | 4.2 m/s | 19.7 |  | 2.09 | m/s |  | 4.2 | m/s | 20.4772 | 0.0089725 | 23.0546 |  | -1 | 762 | 0.762 | 30.2553 | 7.8371 | 5.8832 | 0.024094 | 61.0986 | 1.2472
2025-05-20 06:46 | 2454 | Remove | 2025-05-20 | 6:46 | ST | GS | - | 127.5 | g | 0 | 114.3 | 11.01 | 1075.2 | 7938 | 20:29 | 28 | 2.13 m/s | 27.5 | 29.7 | 4.38 m/s | 19.6 |  | 2.13 | m/s |  | 4.38 | m/s | 20.4856 | 0.00896 | 23.0635 |  | -2 | 762 | 0.762 | 30.2671 | 7.4833 | 5.8533 | 0.023446 | 61.1221 | 1.2467
2025-05-20 06:46 | 2455 | Remove | 2025-05-20 | 6:46 | ST | GS | - | 127.5 | g | 0 | 114.2 | 10.984 | 1071.4 | 7947 | 20:30 | 27.9 | 2.09 m/s | 28.5 | 29.7 | 4.35 m/s | 20.4 |  | 2.09 | m/s |  | 4.35 | m/s | 20.4939 | 0.0089283 | 23.0724 |  | 0 | 762 | 0.762 | 30.2788 | 7.7129 | 6.0922 | 0.023712 | 61.1458 | 1.2462
2025-05-20 06:47 | 2456 | Remove | 2025-05-20 | 6:47 | ST | GS | - | 127.5 | g | 0 | 114.3 | 10.964 | 1068.7 | 7956 | 20:30 | 27.9 | 2.08 m/s | 28.9 | 29.7 | 4.21 m/s | 20.4 |  | 2.08 | m/s |  | 4.21 | m/s | 20.5022 | 0.0089058 | 23.0813 |  | 0 | 762 | 0.762 | 30.2905 | 7.8211 | 6.0922 | 0.02393 | 61.1697 | 1.2457
2025-05-20 06:47 | 2457 | Remove | 2025-05-20 | 6:47 | ST | GS | - | 128 | g | 0 | 114.4 | 10.952 | 1067 | 7965 | 20:31 | 27.9 | 2.08 m/s | 29.7 | 29.6 | 4.3 m/s | 21.5 |  | 2.08 | m/s |  | 4.3 | m/s | 20.5106 | 0.0088917 | 23.0902 |  | 0.5 | 762.5 | 0.7625 | 30.2823 | 8.0376 | 6.3859 | 0.024592 | 61.1943 | 1.246
2025-05-20 06:48 | 2458 | Remove | 2025-05-20 | 6:48 | ST | GS | - | 128 | g | 0 | 114.3 | 10.99 | 1072.7 | 7974 | 20:31 | 27.9 | 2.11 m/s | 28.8 | 29.6 | 4.23 m/s | 20.3 |  | 2.11 | m/s |  | 4.23 | m/s | 20.5189 | 0.0089392 | 23.0992 |  | 0 | 762.5 | 0.7625 | 30.294 | 7.7941 | 6.0295 | 0.024191 | 61.2185 | 1.2455
2025-05-20 06:48 | 2459 | Remove | 2025-05-20 | 6:48 | ST | GS | - | 128 | g | 0 | 114.4 | 10.953 | 1067.3 | 7983 | 20:32 | 27.9 | 2.08 m/s | 30 | 29.6 | 4.29 m/s | 21.1 |  | 2.08 | m/s |  | 4.29 | m/s | 20.5272 | 0.0088942 | 23.1081 |  | 0 | 762.5 | 0.7625 | 30.3057 | 8.1188 | 6.2671 | 0.02484 | 61.2433 | 1.245
2025-05-20 06:49 | 2460 | Remove | 2025-05-20 | 6:49 | ST | GS | - | 128 | g | 0 | 114.4 | 10.93 | 1064.2 | 7992 | 20:32 | 27.8 | 2.09 m/s | 31.7 | 29.6 | 4.26 m/s | 21.3 |  | 2.09 | m/s |  | 4.26 | m/s | 20.5356 | 0.0088683 | 23.1169 |  | 0 | 762.5 | 0.7625 | 30.3173 | 8.5317 | 6.3265 | 0.026229 | 61.2695 | 1.2445
2025-05-20 06:49 | 2461 | Keep | 2025-05-20 | 6:49 | ST | GS | - | 128.5 | g | 0 | 114.3 | 10.978 | 1070.8 | 8001 | 20:33 | 27.8 | 2.01 m/s | 30.7 | 29.6 | 4.27 m/s | 21.5 |  | 2.01 | m/s |  | 4.27 | m/s | 20.5439 | 0.0089233 | 23.1259 |  | 0.5 | 763 | 0.763 | 30.3091 | 8.2626 | 6.3859 | 0.02443 | 61.294 | 1.2448
2025-05-20 06:50 | 2462 | Remove | 2025-05-20 | 6:50 | ST | GS | - | 128 | g | 0 | 114.3 | 11.029 | 1077.3 | 8010 | 20:33 | 27.9 | 2.13 m/s | 29.5 | 29.6 | 4.61 m/s | 20.8 |  | 2.13 | m/s |  | 4.61 | m/s | 20.5522 | 0.0089775 | 23.1348 |  | -0.5 | 763 | 0.763 | 30.3209 | 7.9835 | 6.178 | 0.025014 | 61.319 | 1.2443
2025-05-20 06:50 | 2463 | Remove | 2025-05-20 | 6:50 | ST | GS | - | 128.5 | g | 0 | 114.3 | 11.032 | 1077.9 | 8019 | 20:34 | 27.9 | 2.04 m/s | 30 | 29.6 | 4.63 m/s | 20.9 |  | 2.04 | m/s |  | 4.63 | m/s | 20.5606 | 0.0089825 | 23.1438 |  | 0.5 | 763.5 | 0.7635 | 30.3128 | 8.1188 | 6.2077 | 0.024363 | 61.3434 | 1.2446
2025-05-20 06:51 | 2464 | Remove | 2025-05-20 | 6:51 | ST | GS | - | 129 | g | 0 | 114.3 | 11.003 | 1074.7 | 8028 | 20:34 | 27.9 | 2.18 m/s | 30 | 29.7 | 4.21 m/s | 21.3 |  | 2.18 | m/s |  | 4.21 | m/s | 20.5689 | 0.0089558 | 23.1528 |  | 0.5 | 764 | 0.764 | 30.3047 | 8.1188 | 6.361 | 0.026035 | 61.3694 | 1.2449
2025-05-20 06:51 | 2465 | Remove | 2025-05-20 | 6:51 | ST | GS | - | 129.5 | g | 0 | 114.2 | 11.051 | 1079.9 | 8037 | 20:35 | 28 | 1.98 m/s | 30.2 | 29.7 | 4.23 m/s | 20.7 |  | 1.98 | m/s |  | 4.23 | m/s | 20.5772 | 0.0089992 | 23.1618 |  | 0.5 | 764.5 | 0.7645 | 30.2966 | 8.2181 | 6.1818 | 0.023935 | 61.3933 | 1.2452
2025-05-20 06:52 | 2466 | Remove | 2025-05-20 | 6:52 | ST | GS | - | 128.5 | g | 0 | 114.2 | 11.079 | 1083.7 | 8046 | 20:35 | 28 | 2.11 m/s | 28.6 | 29.7 | 4.27 m/s | 20 |  | 2.11 | m/s |  | 4.27 | m/s | 20.5856 | 0.0090308 | 23.1708 |  | -1 | 764.5 | 0.7645 | 30.3085 | 7.7827 | 5.9728 | 0.024155 | 61.4175 | 1.2448
2025-05-20 06:52 | 2467 | Remove | 2025-05-20 | 6:52 | ST | GS | - | 128.5 | g | 0 | 114.3 | 11.084 | 1084.3 | 8055 | 20:36 | 28 | 2.01 m/s | 28.3 | 29.7 | 4.27 m/s | 20 |  | 2.01 | m/s |  | 4.27 | m/s | 20.5939 | 0.0090358 | 23.1798 |  | 0 | 764.5 | 0.7645 | 30.3203 | 7.701 | 5.9728 | 0.022769 | 61.4402 | 1.2443
2025-05-20 06:53 | 2468 | Remove | 2025-05-20 | 6:53 | ST | GS | - | 127.5 | g | 0 | 114.3 | 11.053 | 1080.7 | 8064 | 20:36 | 28 | 2.09 m/s | 28.8 | 29.7 | 4.32 m/s | 20.4 |  | 2.09 | m/s |  | 4.32 | m/s | 20.6025 | 0.0090058 | 23.1889 |  | -1 | 764.5 | 0.7645 | 30.3321 | 7.8371 | 6.0922 | 0.024094 | 61.4643 | 1.2438
2025-05-20 06:53 | 2469 | Remove | 2025-05-20 | 6:53 | ST | GS | - | 128 | g | 0 | 114.3 | 11.037 | 1078.4 | 8073 | 20:37 | 28 | 2.05 m/s | 28.9 | 29.7 | 4.23 m/s | 20.7 |  | 2.05 | m/s |  | 4.23 | m/s | 20.6108 | 0.0089867 | 23.1978 |  | 0.5 | 765 | 0.765 | 30.324 | 7.8643 | 6.1818 | 0.023715 | 61.4881 | 1.2441
2025-05-20 06:54 | 2470 | Remove | 2025-05-20 | 6:54 | ST | GS | - | 127.5 | g | 0 | 114.3 | 11.012 | 1075.4 | 8082 | 20:37 | 28 | 2.08 m/s | 29.4 | 29.7 | 4.29 m/s | 20.9 |  | 2.08 | m/s |  | 4.29 | m/s | 20.6192 | 0.0089617 | 23.2068 |  | -0.5 | 765 | 0.765 | 30.3357 | 8.0004 | 6.2415 | 0.024478 | 61.5125 | 1.2436
2025-05-20 06:54 | 2471 | Remove | 2025-05-20 | 6:54 | ST | GS | - | 128 | g | 0 | 114.3 | 11.004 | 1074.2 | 8091 | 20:38 | 28 | 2.11 m/s | 29.4 | 29.7 | 4.32 m/s | 20.7 |  | 2.11 | m/s |  | 4.32 | m/s | 20.6275 | 0.0089517 | 23.2158 |  | 0.5 | 765.5 | 0.7655 | 30.3276 | 8.0004 | 6.1818 | 0.024831 | 61.5374 | 1.244
2025-05-20 06:55 | 2472 | Remove | 2025-05-20 | 6:55 | ST | GS | - | 127.5 | g | 0 | 114.2 | 11.054 | 1080.6 | 8100 | 20:38 | 28 | 1.97 m/s | 29 | 29.7 | 4.26 m/s | 20.4 |  | 1.97 | m/s |  | 4.26 | m/s | 20.6358 | 0.009005 | 23.2248 |  | -0.5 | 765.5 | 0.7655 | 30.3393 | 7.8915 | 6.0922 | 0.022868 | 61.5602 | 1.2435
2025-05-20 06:55 | 2473 | Remove | 2025-05-20 | 6:55 | ST | GS | - | 127.5 | g | 0 | 114.3 | 11.001 | 1074.2 | 8109 | 20:39 | 27.9 | 2.08 m/s | 29.3 | 29.7 | 4.3 m/s | 21.6 |  | 2.08 | m/s |  | 4.3 | m/s | 20.6442 | 0.0089517 | 23.2337 |  | 0 | 765.5 | 0.7655 | 30.351 | 7.9294 | 6.4506 | 0.024261 | 61.5845 | 1.243
2025-05-20 06:56 | 2474 | Remove | 2025-05-20 | 6:56 | ST | GS | - | 127.5 | g | 0 | 114.3 | 11.035 | 1078.7 | 8118 | 20:39 | 27.9 | 2.08 m/s | 29.7 | 29.7 | 4.36 m/s | 20.3 |  | 2.08 | m/s |  | 4.36 | m/s | 20.6525 | 0.0089892 | 23.2427 |  | 0 | 765.5 | 0.7655 | 30.3628 | 8.0376 | 6.0624 | 0.024592 | 61.6091 | 1.2425
2025-05-20 06:56 | 2475 | Remove | 2025-05-20 | 6:56 | ST | GS | - | 128 | g | 0 | 114.4 | 11.019 | 1075.5 | 8127 | 20:40 | 28 | 2.07 m/s | 29.3 | 29.6 | 4.24 m/s | 21 |  | 2.07 | m/s |  | 4.24 | m/s | 20.6608 | 0.0089625 | 23.2517 |  | 0.5 | 766 | 0.766 | 30.3546 | 7.9732 | 6.2374 | 0.024277 | 61.6334 | 1.2428
2025-05-20 06:57 | 2476 | Remove | 2025-05-20 | 6:57 | ST | GS | - | 128 | g | 0 | 114.4 | 11.009 | 1074.8 | 8136 | 20:40 | 27.9 | 1.91 m/s | 30 | 29.6 | 4.26 m/s | 22 |  | 1.91 | m/s |  | 4.26 | m/s | 20.6692 | 0.0089567 | 23.2606 |  | 0 | 766 | 0.766 | 30.3663 | 8.1188 | 6.5344 | 0.02281 | 61.6562 | 1.2424
2025-05-20 06:57 | 2477 | Remove | 2025-05-20 | 6:57 | ST | GS | - | 128.5 | g | 0 | 114.4 | 11.043 | 1079.1 | 8145 | 20:41 | 28 | 2.11 m/s | 29 | 29.6 | 4.33 m/s | 20.6 |  | 2.11 | m/s |  | 4.33 | m/s | 20.6775 | 0.0089925 | 23.2696 |  | 0.5 | 766.5 | 0.7665 | 30.3583 | 7.8915 | 6.1186 | 0.024493 | 61.6807 | 1.2427
2025-05-20 06:58 | 2478 | Remove | 2025-05-20 | 6:58 | ST | GS | - | 128 | g | 0 | 114.3 | 11.044 | 1079.6 | 8154 | 20:41 | 28 | 2.11 m/s | 29.8 | 29.6 | 4.33 m/s | 20.6 |  | 2.11 | m/s |  | 4.33 | m/s | 20.6858 | 0.0089967 | 23.2786 |  | -0.5 | 766.5 | 0.7665 | 30.37 | 8.1092 | 6.1186 | 0.025169 | 61.7058 | 1.2422
2025-05-20 06:58 | 2479 | Remove | 2025-05-20 | 6:58 | ST | GS | - | 128 | g | 0 | 114.3 | 11.022 | 1076.4 | 8163 | 20:42 | 28 | 2.12 m/s | 29.3 | 29.6 | 4.32 m/s | 21.3 |  | 2.12 | m/s |  | 4.32 | m/s | 20.6942 | 0.00897 | 23.2876 |  | 0 | 766.5 | 0.7665 | 30.3817 | 7.9732 | 6.3265 | 0.024864 | 61.7307 | 1.2417
2025-05-20 06:59 | 2480 | Remove | 2025-05-20 | 6:59 | ST | GS | - | 128 | g | 0 | 114.2 | 11.033 | 1077.3 | 8172 | 20:42 | 28 | 2.15 m/s | 29.1 | 29.6 | 4.29 m/s | 21 |  | 2.15 | m/s |  | 4.29 | m/s | 20.7025 | 0.0089775 | 23.2966 |  | 0 | 766.5 | 0.7665 | 30.3934 | 7.9187 | 6.2374 | 0.025044 | 61.7557 | 1.2412
2025-05-20 06:59 | 2481 | Remove | 2025-05-20 | 6:59 | US | GS | - | 130.5 | g | 0 | 114.4 | 11.019 | 1075.6 | 8181 | 20:43 | 28 | 2.11 m/s | 30 | 29.6 | 4.26 m/s | 21 |  | 2.11 | m/s |  | 4.26 | m/s | 20.7108 | 0.0089633 | 23.3055 |  | 2.5 | 769 | 0.769 | 30.3063 | 8.1637 | 6.2374 | 0.025338 | 61.7811 | 1.2447
2025-05-20 07:00 | 2482 | Remove | 2025-05-20 | 7:00 | ST | GS | - | 129 | g | 0 | 114.2 | 11.067 | 1081.9 | 8190 | 20:43 | 28 | 2.08 m/s | 28.3 | 29.5 | 4.5 m/s | 20 |  | 2.08 | m/s |  | 4.5 | m/s | 20.7192 | 0.0090158 | 23.3145 |  | -1.5 | 769 | 0.769 | 30.318 | 7.701 | 5.9082 | 0.023562 | 61.8046 | 1.2442
2025-05-20 07:00 | 2483 | Remove | 2025-05-20 | 7:00 | ST | GS | - | 128 | g | 0 | 114.1 | 11.054 | 1080.2 | 8199 | 20:44 | 28 | 2.06 m/s | 29 | 29.6 | 4.24 m/s | 20.4 |  | 2.06 | m/s |  | 4.24 | m/s | 20.7275 | 0.0090017 | 23.3235 |  | -1 | 769 | 0.769 | 30.3297 | 7.8915 | 6.0592 | 0.023913 | 61.8286 | 1.2438
2025-05-20 07:01 | 2484 | Remove | 2025-05-20 | 7:01 | ST | GS | - | 130 | g | 0 | 114.1 | 11.055 | 1080.2 | 8208 | 20:44 | 28 | 2.09 m/s | 28.2 | 29.6 | 4.47 m/s | 20.2 |  | 2.09 | m/s |  | 4.47 | m/s | 20.7358 | 0.0090017 | 23.3325 |  | 2 | 771 | 0.771 | 30.2627 | 7.6738 | 5.9998 | 0.023592 | 61.8521 | 1.2465
2025-05-20 07:01 | 2485 | Remove | 2025-05-20 | 7:01 | ST | GS | - | 129.5 | g | 0 | 114 | 11.072 | 1082.3 | 8217 | 20:45 | 28 | 1.93 m/s | 28.4 | 29.6 | 4.21 m/s | 20.2 |  | 1.93 | m/s |  | 4.21 | m/s | 20.7444 | 0.0090192 | 23.3416 |  | -0.5 | 771 | 0.771 | 30.2744 | 7.7283 | 5.9998 | 0.02194 | 61.8741 | 1.2461
2025-05-20 07:02 | 2486 | Remove | 2025-05-20 | 7:02 | ST | GS | - | 129.5 | g | 0 | 114.1 | 11.065 | 1081.2 | 8226 | 20:45 | 28.1 | 2.13 m/s | 28.3 | 29.5 | 4.24 m/s | 20.4 |  | 2.13 | m/s |  | 4.24 | m/s | 20.7528 | 0.00901 | 23.3506 |  | 0 | 771 | 0.771 | 30.2861 | 7.7435 | 6.0263 | 0.024262 | 61.8983 | 1.2456
2025-05-20 07:02 | 2487 | Remove | 2025-05-20 | 7:02 | ST | GS | - | 128 | g | 0 | 114 | 11.084 | 1083.8 | 8235 | 20:46 | 28.1 | 2.06 m/s | 27.7 | 29.5 | 4.27 m/s | 20.1 |  | 2.06 | m/s |  | 4.27 | m/s | 20.7611 | 0.0090317 | 23.3596 |  | -1.5 | 771 | 0.771 | 30.2978 | 7.5794 | 5.9377 | 0.022967 | 61.9213 | 1.2451
2025-05-20 07:03 | 2488 | Remove | 2025-05-20 | 7:03 | ST | GS | - | 128.5 | g | 0 | 114.1 | 11.028 | 1076.8 | 8244 | 20:46 | 28 | 2.05 m/s | 30 | 29.6 | 4.23 m/s | 21.4 |  | 2.05 | m/s |  | 4.23 | m/s | 20.7694 | 0.0089733 | 23.3686 |  | 0.5 | 771.5 | 0.7715 | 30.2898 | 8.1637 | 6.3562 | 0.024617 | 61.9459 | 1.2454
2025-05-20 07:03 | 2489 | Remove | 2025-05-20 | 7:03 | ST | GS | - | 128 | g | 0 | 114 | 11.085 | 1083.8 | 8254 | 20:47 | 28.1 | 2.06 m/s | 27.8 | 29.6 | 4.27 m/s | 20.4 |  | 2.06 | m/s |  | 4.27 | m/s | 20.7778 | 0.0090317 | 23.3776 |  | -0.5 | 771.5 | 0.7715 | 30.3015 | 7.6067 | 6.0592 | 0.02305 | 61.969 | 1.245
2025-05-20 07:04 | 2490 | Remove | 2025-05-20 | 7:04 | ST | GS | - | 127.5 | g | 0 | 114.1 | 11.075 | 1082.9 | 8263 | 20:47 | 28.1 | 2.11 m/s | 27.9 | 29.6 | 4.29 m/s | 20.5 |  | 2.11 | m/s |  | 4.29 | m/s | 20.7861 | 0.0090242 | 23.3866 |  | -0.5 | 771.5 | 0.7715 | 30.3132 | 7.6341 | 6.0889 | 0.023694 | 61.9927 | 1.2445
2025-05-20 07:04 | 2491 | Keep | 2025-05-20 | 7:04 | US | GS | - | 131 | g | 0 | 114 | 11.078 | 1083.5 | 8272 | 20:48 | 28.1 | 1.9 m/s | 27.5 | 29.6 | 4.63 m/s | 19.8 |  | 1.9 | m/s |  | 4.63 | m/s | 20.7944 | 0.0090292 | 23.3957 |  | 3.5 | 775 | 0.775 | 30.1879 | 7.5246 | 5.881 | 0.02103 | 62.0137 | 1.2497
2025-05-20 07:05 | 2492 | Remove | 2025-05-20 | 7:05 | ST | GS | - | 128 | g | 0 | 114 | 11.094 | 1085.5 | 8281 | 20:48 | 28.1 | 2.12 m/s | 27.6 | 29.6 | 4.52 m/s | 20 |  | 2.12 | m/s |  | 4.52 | m/s | 20.8028 | 0.0090458 | 23.4047 |  | -3 | 775 | 0.775 | 30.1996 | 7.552 | 5.9404 | 0.023551 | 62.0373 | 1.2492
2025-05-20 07:05 | 2493 | Remove | 2025-05-20 | 7:05 | US | GS | - | 128.5 | g | 0 | 113.9 | 11.055 | 1080.2 | 8290 | 20:49 | 28.1 | 2.04 m/s | 27.8 | 29.6 | 4.33 m/s | 20.3 |  | 2.04 | m/s |  | 4.33 | m/s | 20.8111 | 0.0090017 | 23.4137 |  | 0.5 | 775.5 | 0.7755 | 30.1918 | 7.6067 | 6.0295 | 0.022826 | 62.0601 | 1.2496
2025-05-20 07:06 | 2494 | Remove | 2025-05-20 | 7:06 | ST | GS | - | 128.5 | g | 0 | 114 | 11.031 | 1077.6 | 8299 | 20:49 | 28.1 | 2.05 m/s | 29.2 | 29.6 | 4.35 m/s | 21.2 |  | 2.05 | m/s |  | 4.35 | m/s | 20.8194 | 0.00898 | 23.4227 |  | 0 | 775.5 | 0.7755 | 30.2033 | 7.9898 | 6.2968 | 0.024093 | 62.0842 | 1.2491
2025-05-20 07:06 | 2495 | Remove | 2025-05-20 | 7:06 | ST | GS | - | 128 | g | 0 | 114 | 11.021 | 1076.1 | 8308 | 20:50 | 28 | 2.05 m/s | 29.1 | 29.6 | 4.23 m/s | 21 |  | 2.05 | m/s |  | 4.23 | m/s | 20.8278 | 0.0089675 | 23.4317 |  | -0.5 | 775.5 | 0.7755 | 30.2149 | 7.9187 | 6.2374 | 0.023879 | 62.1081 | 1.2486
2025-05-20 07:07 | 2496 | Remove | 2025-05-20 | 7:07 | ST | GS | - | 128.5 | g | 0 | 114.1 | 11.051 | 1079.9 | 8317 | 20:50 | 28.1 | 2.04 m/s | 28.3 | 29.6 | 4.32 m/s | 20.2 |  | 2.04 | m/s |  | 4.32 | m/s | 20.8361 | 0.0089992 | 23.4407 |  | 0.5 | 776 | 0.776 | 30.207 | 7.7435 | 5.9998 | 0.023237 | 62.1313 | 1.249
2025-05-20 07:07 | 2497 | Remove | 2025-05-20 | 7:07 | ST | GS | - | 129 | g | 0 | 113.9 | 11.023 | 1075.9 | 8326 | 20:51 | 28.1 | 2.08 m/s | 28.8 | 29.6 | 4.26 m/s | 21.3 |  | 2.08 | m/s |  | 4.26 | m/s | 20.8444 | 0.0089658 | 23.4496 |  | 0.5 | 776.5 | 0.7765 | 30.1991 | 7.8804 | 6.3265 | 0.024111 | 62.1554 | 1.2493
2025-05-20 07:08 | 2498 | Remove | 2025-05-20 | 7:08 | ST | GS | - | 130 | g | 0 | 114 | 11.055 | 1080.5 | 8335 | 20:51 | 28.1 | 2.08 m/s | 28.4 | 29.6 | 4.26 m/s | 20.3 |  | 2.08 | m/s |  | 4.26 | m/s | 20.8528 | 0.0090042 | 23.4586 |  | 1 | 777.5 | 0.7775 | 30.1719 | 7.7709 | 6.0295 | 0.023776 | 62.1792 | 1.2504
2025-05-20 07:08 | 2499 | Remove | 2025-05-20 | 7:08 | ST | GS | - | 131 | g | 0 | 114.1 | 11.069 | 1081.9 | 8344 | 20:52 | 28.1 | 2.13 m/s | 27.5 | 29.6 | 4.41 m/s | 20 |  | 2.13 | m/s |  | 4.41 | m/s | 20.8611 | 0.0090158 | 23.4676 |  | 1 | 778.5 | 0.7785 | 30.1447 | 7.5246 | 5.9404 | 0.023576 | 62.2028 | 1.2516
2025-05-20 07:09 | 2500 | Remove | 2025-05-20 | 7:09 | ST | GS | - | 129 | g | 0 | 114.2 | 11.044 | 1079.1 | 8353 | 20:52 | 28.1 | 2.01 m/s | 28 | 29.6 | 4.24 m/s | 20 |  | 2.01 | m/s |  | 4.24 | m/s | 20.8694 | 0.0089925 | 23.4766 |  | -2 | 778.5 | 0.7785 | 30.1562 | 7.6615 | 5.9404 | 0.022652 | 62.2254 | 1.2511
2025-05-20 07:09 | 2501 | Remove | 2025-05-20 | 7:09 | ST | GS | - | 128.5 | g | 0 | 114.2 | 11.045 | 1079.1 | 8362 | 20:53 | 28.1 | 2.09 m/s | 29.1 | 29.6 | 4.24 m/s | 20.5 |  | 2.09 | m/s |  | 4.24 | m/s | 20.8778 | 0.0089925 | 23.4856 |  | -0.5 | 778.5 | 0.7785 | 30.1678 | 7.9624 | 6.0889 | 0.024479 | 62.2499 | 1.2506
2025-05-20 07:10 | 2502 | Remove | 2025-05-20 | 7:10 | US | GS | - | 131 | g | 0 | 114.2 | 11.039 | 1077.9 | 8371 | 20:53 | 28.1 | 2.05 m/s | 28.8 | 29.6 | 4.43 m/s | 20.7 |  | 2.05 | m/s |  | 4.43 | m/s | 20.8864 | 0.0089825 | 23.4946 |  | 2.5 | 781 | 0.781 | 30.0827 | 7.8804 | 6.1483 | 0.023763 | 62.2736 | 1.2541
2025-05-20 07:10 | 2503 | Remove | 2025-05-20 | 7:10 | ST | GS | - | 130.5 | g | 0 | 114.3 | 11.058 | 1080.3 | 8380 | 20:54 | 28.1 | 2.13 m/s | 27.9 | 29.6 | 4.56 m/s | 20.1 |  | 2.13 | m/s |  | 4.56 | m/s | 20.8947 | 0.0090025 | 23.5036 |  | -0.5 | 781 | 0.781 | 30.0942 | 7.6341 | 5.9701 | 0.023919 | 62.2976 | 1.2537
2025-05-20 07:11 | 2504 | Remove | 2025-05-20 | 7:11 | ST | GS | - | 130 | g | 0 | 114.1 | 11.083 | 1083.4 | 8389 | 20:54 | 28.1 | 2.05 m/s | 27.5 | 29.6 | 4.55 m/s | 20.1 |  | 2.05 | m/s |  | 4.55 | m/s | 20.9031 | 0.0090283 | 23.5126 |  | -0.5 | 781 | 0.781 | 30.1058 | 7.5246 | 5.9701 | 0.02269 | 62.3203 | 1.2532
2025-05-20 07:11 | 2505 | Remove | 2025-05-20 | 7:11 | ST | GS | - | 130.5 | g | 0 | 114.2 | 11.084 | 1084 | 8398 | 20:55 | 28.1 | 2.11 m/s | 27.4 | 29.6 | 4.41 m/s | 20 |  | 2.11 | m/s |  | 4.41 | m/s | 20.9114 | 0.0090333 | 23.5217 |  | 0.5 | 781.5 | 0.7815 | 30.0981 | 7.4973 | 5.9404 | 0.02327 | 62.3435 | 1.2535
2025-05-20 07:12 | 2506 | Remove | 2025-05-20 | 7:12 | ST | GS | - | 129.5 | g | 0 | 114.2 | 11.087 | 1084.4 | 8407 | 20:55 | 28.2 | 1.98 m/s | 27.5 | 29.6 | 5.0 m/s | 20.2 |  | 1.98 | m/s |  | 5 | m/s | 20.9197 | 0.0090367 | 23.5307 |  | -1 | 781.5 | 0.7815 | 30.1097 | 7.5661 | 5.9998 | 0.022036 | 62.3656 | 1.2531
2025-05-20 07:12 | 2507 | Remove | 2025-05-20 | 7:12 | ST | GS | - | 135 | g | 0 | 114.2 | 11.079 | 1082.8 | 8416 | 20:56 | 28.2 | 2.09 m/s | 26.9 | 29.6 | 4.32 m/s | 19.7 |  | 2.09 | m/s |  | 4.32 | m/s | 20.9281 | 0.0090233 | 23.5397 |  | 5.5 | 787 | 0.787 | 29.9107 | 7.4011 | 5.8513 | 0.022753 | 62.3883 | 1.2615
2025-05-20 07:13 | 2508 | Remove | 2025-05-20 | 7:13 | ST | GS | - | 132 | g | 0 | 114.1 | 11.104 | 1086.4 | 8425 | 20:56 | 28.2 | 2.19 m/s | 26.7 | 29.6 | 4.85 m/s | 19.6 |  | 2.19 | m/s |  | 4.85 | m/s | 20.9364 | 0.0090533 | 23.5488 |  | -3 | 787 | 0.787 | 29.9222 | 7.346 | 5.8216 | 0.023665 | 62.412 | 1.261
2025-05-20 07:13 | 2509 | Remove | 2025-05-20 | 7:13 | ST | GS | - | 133.5 | g | 0 | 114.2 | 11.114 | 1087.7 | 8434 | 20:57 | 28.2 | 2.05 m/s | 26.7 | 29.6 | 4.38 m/s | 19.6 |  | 2.05 | m/s |  | 4.38 | m/s | 20.9447 | 0.0090642 | 23.5578 |  | 1.5 | 788.5 | 0.7885 | 29.8768 | 7.346 | 5.8216 | 0.022152 | 62.4341 | 1.2629
2025-05-20 07:14 | 2510 | Remove | 2025-05-20 | 7:14 | ST | GS | - | 135 | g | 0 | 114.3 | 11.111 | 1087.5 | 8443 | 20:57 | 28.2 | 2.01 m/s | 26.8 | 29.6 | 4.3 m/s | 19.7 |  | 2.01 | m/s |  | 4.3 | m/s | 20.9531 | 0.0090625 | 23.5669 |  | 1.5 | 790 | 0.79 | 29.8315 | 7.3735 | 5.8513 | 0.021801 | 62.4559 | 1.2649
2025-05-20 07:14 | 2511 | Remove | 2025-05-20 | 7:14 | US | GS | - | 133.5 | g | 0 | 114.2 | 11.1 | 1086.1 | 8452 | 20:58 | 28.2 | 2.08 m/s | 26.6 | 29.7 | 4.24 m/s | 19.5 |  | 2.08 | m/s |  | 4.24 | m/s | 20.9614 | 0.0090508 | 23.576 |  | -1.5 | 790 | 0.79 | 29.843 | 7.3185 | 5.8234 | 0.022392 | 62.4783 | 1.2644
2025-05-20 07:15 | 2512 | Remove | 2025-05-20 | 7:15 | US | GS | - | 135.5 | g | 0 | 114.3 | 11.075 | 1083.1 | 8462 | 20:58 | 28.2 | 2.04 m/s | 26.7 | 29.7 | 4.41 m/s | 19.7 |  | 2.04 | m/s |  | 4.41 | m/s | 20.9697 | 0.0090258 | 23.585 |  | 2 | 792 | 0.792 | 29.779 | 7.346 | 5.8832 | 0.022044 | 62.5004 | 1.2672
2025-05-20 07:15 | 2513 | Remove | 2025-05-20 | 7:15 | US | GS | - | 131 | g | 0 | 114.2 | 11.093 | 1085.4 | 8470 | 20:59 | 28.2 | 2.08 m/s | 27 | 29.7 | 4.5 m/s | 19.7 |  | 2.08 | m/s |  | 4.5 | m/s | 20.9781 | 0.009045 | 23.594 |  | -4.5 | 792 | 0.792 | 29.7904 | 7.4286 | 5.8832 | 0.022728 | 62.5231 | 1.2667
2025-05-20 07:16 | 2514 | Remove | 2025-05-20 | 7:16 | US | GS | - | 130.5 | g | 0 | 114.3 | 11.088 | 1084.8 | 8480 | 20:59 | 28.2 | 2.09 m/s | 26.9 | 29.7 | 5.0 m/s | 19.8 |  | 2.09 | m/s |  | 5 | m/s | 20.9864 | 0.00904 | 23.6031 |  | -0.5 | 792 | 0.792 | 29.8019 | 7.4011 | 5.913 | 0.022753 | 62.5459 | 1.2663
2025-05-20 07:16 | 2515 | Remove | 2025-05-20 | 7:16 | ST | GS | - | 134 | g | 0 | 114.1 | 11.086 | 1084.8 | 8489 | 21:00 | 28.2 | 2.15 m/s | 27 | 29.7 | 4.5 m/s | 19.8 |  | 2.15 | m/s |  | 4.5 | m/s | 20.9947 | 0.00904 | 23.6121 |  | 3.5 | 795.5 | 0.7955 | 29.6821 | 7.4286 | 5.913 | 0.023493 | 62.5693 | 1.2714
2025-05-20 07:17 | 2516 | Remove | 2025-05-20 | 7:17 | ST | GS | - | 132 | g | 0 | 114.2 | 11.104 | 1087 | 8498 | 21:00 | 28.2 | 1.94 m/s | 27.1 | 29.7 | 4.6 m/s | 20 |  | 1.94 | m/s |  | 4.6 | m/s | 21.0031 | 0.0090583 | 23.6212 |  | -2 | 795.5 | 0.7955 | 29.6935 | 7.4561 | 5.9728 | 0.021277 | 62.5906 | 1.271
2025-05-20 07:17 | 2517 | Remove | 2025-05-20 | 7:17 | ST | GS | - | 135 | g | 0 | 114.2 | 11.105 | 1087.2 | 8507 | 21:01 | 28.3 | 2.15 m/s | 26.6 | 29.7 | 4.69 m/s | 19.6 |  | 2.15 | m/s |  | 4.69 | m/s | 21.0114 | 0.00906 | 23.6302 |  | 3 | 798.5 | 0.7985 | 29.5933 | 7.3588 | 5.8533 | 0.023273 | 62.6139 | 1.2753
2025-05-20 07:18 | 2518 | Remove | 2025-05-20 | 7:18 | ST | GS | - | 134.5 | g | 0 | 114.2 | 11.111 | 1088.1 | 8516 | 21:01 | 28.3 | 2.13 m/s | 27.1 | 29.7 | 4.72 m/s | 19.8 |  | 2.13 | m/s |  | 4.72 | m/s | 21.0197 | 0.0090675 | 23.6393 |  | -0.5 | 798.5 | 0.7985 | 29.6046 | 7.4972 | 5.913 | 0.02349 | 62.6374 | 1.2748
2025-05-20 07:18 | 2519 | Remove | 2025-05-20 | 7:18 | ST | GS | - | 135.5 | g | 0 | 114.2 | 11.103 | 1087.4 | 8525 | 21:02 | 28.3 | 1.9 m/s | 26.7 | 29.7 | 4.32 m/s | 19.7 |  | 1.9 | m/s |  | 4.32 | m/s | 21.0283 | 0.0090617 | 23.6484 |  | 1 | 799.5 | 0.7995 | 29.5789 | 7.3865 | 5.8832 | 0.020644 | 62.658 | 1.276
2025-05-20 07:19 | 2520 | Remove | 2025-05-20 | 7:19 | US | GS | - | 139 | g | 0 | 114.2 | 11.109 | 1088 | 8534 | 21:02 | 28.3 | 2.13 m/s | 26.4 | 29.7 | 4.35 m/s | 19.6 |  | 2.13 | m/s |  | 4.35 | m/s | 21.0367 | 0.0090667 | 23.6574 |  | 3.5 | 803 | 0.803 | 29.4613 | 7.3035 | 5.8533 | 0.022883 | 62.6809 | 1.2811
2025-05-20 07:19 | 2521 | Keep | 2025-05-20 | 7:19 | US | GS | - | 131.5 | g | 0 | 114.1 | 11.107 | 1088.1 | 8543 | 21:03 | 28.3 | 2.09 m/s | 26.5 | 29.6 | 4.41 m/s | 19.6 |  | 2.09 | m/s |  | 4.41 | m/s | 21.045 | 0.0090675 | 23.6665 |  | -7.5 | 803 | 0.803 | 29.4726 | 7.3312 | 5.8216 | 0.022538 | 62.7035 | 1.2806
2025-05-20 07:20 | 2522 | Remove | 2025-05-20 | 7:20 | US | GS | - | 133.5 | g | 0 | 114 | 11.146 | 1092.9 | 8552 | 21:03 | 28.3 | 2.11 m/s | 26.4 | 29.7 | 4.94 m/s | 19.6 |  | 2.11 | m/s |  | 4.94 | m/s | 21.0533 | 0.0091075 | 23.6756 |  | 2 | 805 | 0.805 | 29.4107 | 7.3035 | 5.8533 | 0.022668 | 62.7261 | 1.2834
2025-05-20 07:20 | 2523 | Remove | 2025-05-20 | 7:20 | ST | GS | - | 130.5 | g | 0 | 114 | 11.119 | 1089.3 | 8561 | 21:04 | 28.3 | 2.11 m/s | 27.1 | 29.7 | 4.88 m/s | 20 |  | 2.11 | m/s |  | 4.88 | m/s | 21.0617 | 0.0090775 | 23.6847 |  | -3 | 805 | 0.805 | 29.422 | 7.4972 | 5.9728 | 0.023269 | 62.7494 | 1.2829
2025-05-20 07:21 | 2524 | Remove | 2025-05-20 | 7:21 | ST | GS | - | 137.5 | g | 0 | 114.1 | 11.099 | 1086.9 | 8570 | 21:04 | 28.3 | 2.01 m/s | 27.3 | 29.7 | 4.7 m/s | 20 |  | 2.01 | m/s |  | 4.7 | m/s | 21.07 | 0.0090575 | 23.6937 |  | 7 | 812 | 0.812 | 29.1795 | 7.5525 | 5.9728 | 0.02233 | 62.7717 | 1.2936
2025-05-20 07:21 | 2525 | Remove | 2025-05-20 | 7:21 | ST | GS | - | 135 | g | 0 | 114 | 11.105 | 1088.2 | 8580 | 21:05 | 28.3 | 1.98 m/s | 27 | 29.7 | 4.33 m/s | 20 |  | 1.98 | m/s |  | 4.33 | m/s | 21.0783 | 0.0090683 | 23.7028 |  | -2.5 | 812 | 0.812 | 29.1906 | 7.4695 | 5.9728 | 0.021755 | 62.7935 | 1.2931
2025-05-20 07:22 | 2526 | Remove | 2025-05-20 | 7:22 | US | GS | - | 136 | g | 0 | 114 | 11.116 | 1089.2 | 8589 | 21:05 | 28.3 | 2.11 m/s | 26.7 | 29.7 | 4.32 m/s | 19.7 |  | 2.11 | m/s |  | 4.32 | m/s | 21.0867 | 0.0090767 | 23.7119 |  | 1 | 813 | 0.813 | 29.1659 | 7.3865 | 5.8832 | 0.022926 | 62.8164 | 1.2942
2025-05-20 07:22 | 2527 | Remove | 2025-05-20 | 7:22 | ST | GS | - | 134.5 | g | 0 | 114 | 11.124 | 1090.3 | 8598 | 21:06 | 28.3 | 2.19 m/s | 26.6 | 29.7 | 4.88 m/s | 19.6 |  | 2.19 | m/s |  | 4.88 | m/s | 21.095 | 0.0090858 | 23.721 |  | -1.5 | 813 | 0.813 | 29.1771 | 7.3588 | 5.8533 | 0.023706 | 62.8401 | 1.2938
2025-05-20 07:23 | 2528 | Remove | 2025-05-20 | 7:23 | ST | GS | - | 135 | g | 0 | 114 | 11.101 | 1087.5 | 8607 | 21:06 | 28.3 | 1.95 m/s | 26.9 | 29.7 | 4.53 m/s | 19.8 |  | 1.95 | m/s |  | 4.53 | m/s | 21.1033 | 0.0090625 | 23.73 |  | 0.5 | 813.5 | 0.8135 | 29.1703 | 7.4418 | 5.913 | 0.021346 | 62.8615 | 1.2941
2025-05-20 07:23 | 2529 | Remove | 2025-05-20 | 7:23 | ST | GS | - | 134.5 | g | 0 | 114 | 11.117 | 1089.5 | 8616 | 21:07 | 28.3 | 2.02 m/s | 26.8 | 29.7 | 4.9 m/s | 19.7 |  | 2.02 | m/s |  | 4.9 | m/s | 21.1117 | 0.0090792 | 23.7391 |  | -0.5 | 813.5 | 0.8135 | 29.1814 | 7.4142 | 5.8832 | 0.02203 | 62.8835 | 1.2937
2025-05-20 07:24 | 2530 | Remove | 2025-05-20 | 7:24 | ST | GS | - | 134.5 | g | 0 | 114 | 11.117 | 1089.5 | 8625 | 21:07 | 28.3 | 2.08 m/s | 26.9 | 29.7 | 4.66 m/s | 19.8 |  | 2.08 | m/s |  | 4.66 | m/s | 21.12 | 0.0090792 | 23.7482 |  | 0 | 813.5 | 0.8135 | 29.1926 | 7.4418 | 5.913 | 0.022769 | 62.9063 | 1.2932
2025-05-20 07:24 | 2531 | Remove | 2025-05-20 | 7:24 | ST | GS | - | 132 | g | 0 | 114 | 11.107 | 1088.6 | 8634 | 21:08 | 28.3 | 2.08 m/s | 26.9 | 29.7 | 4.43 m/s | 20 |  | 2.08 | m/s |  | 4.43 | m/s | 21.1283 | 0.0090717 | 23.7573 |  | -2.5 | 813.5 | 0.8135 | 29.2038 | 7.4418 | 5.9728 | 0.022769 | 62.929 | 1.2927
2025-05-20 07:25 | 2532 | Remove | 2025-05-20 | 7:25 | US | GS | - | 132.5 | g | 0 | 113.9 | 11.096 | 1086.8 | 8643 | 21:08 | 28.3 | 2.01 m/s | 27.3 | 29.7 | 4.73 m/s | 19.7 |  | 2.01 | m/s |  | 4.73 | m/s | 21.1367 | 0.0090567 | 23.7663 |  | 0.5 | 814 | 0.814 | 29.1969 | 7.5525 | 5.8832 | 0.02233 | 62.9513 | 1.2931
2025-05-20 07:25 | 2533 | Remove | 2025-05-20 | 7:25 | ST | GS | - | 134.5 | g | 0 | 113.9 | 11.115 | 1089.2 | 8652 | 21:09 | 28.3 | 2.11 m/s | 26.9 | 29.7 | 4.32 m/s | 19.5 |  | 2.11 | m/s |  | 4.32 | m/s | 21.145 | 0.0090767 | 23.7754 |  | 2 | 816 | 0.816 | 29.1365 | 7.4418 | 5.8234 | 0.023097 | 62.9744 | 1.2958
2025-05-20 07:26 | 2534 | Remove | 2025-05-20 | 7:26 | ST | GS | - | 132.5 | g | 0 | 113.9 | 11.108 | 1088 | 8662 | 21:09 | 28.3 | 2.09 m/s | 26.5 | 29.7 | 4.69 m/s | 19.5 |  | 2.09 | m/s |  | 4.69 | m/s | 21.1533 | 0.0090667 | 23.7845 |  | -2 | 816 | 0.816 | 29.1476 | 7.3312 | 5.8234 | 0.022538 | 62.997 | 1.2953
2025-05-20 07:26 | 2535 | Remove | 2025-05-20 | 7:26 | ST | GS | - | 132.5 | g | 0 | 114 | 11.086 | 1085.2 | 8670 | 21:10 | 28.3 | 2.06 m/s | 26.6 | 29.7 | 4.75 m/s | 21.1 |  | 2.06 | m/s |  | 4.75 | m/s | 21.1617 | 0.0090433 | 23.7935 |  | 0 | 816 | 0.816 | 29.1587 | 7.3588 | 6.3013 | 0.022299 | 63.0193 | 1.2948
2025-05-20 07:27 | 2536 | Remove | 2025-05-20 | 7:27 | ST | GS | - | 134.5 | g | 0 | 113.9 | 11.143 | 1093.2 | 8680 | 21:10 | 28.3 | 2.05 m/s | 29.1 | 29.7 | 4.38 m/s | 20 |  | 2.05 | m/s |  | 4.38 | m/s | 21.17 | 0.00911 | 23.8026 |  | 2 | 818 | 0.818 | 29.0985 | 8.0505 | 5.9728 | 0.024276 | 63.0436 | 1.2975
2025-05-20 07:27 | 2537 | Remove | 2025-05-20 | 7:27 | US | GS | - | 140 | g | 0 | 114 | 11.122 | 1090.5 | 8689 | 21:11 | 28.3 | 2.02 m/s | 27.3 | 29.7 | 4.26 m/s | 19.5 |  | 2.02 | m/s |  | 4.26 | m/s | 21.1783 | 0.0090875 | 23.8117 |  | 5.5 | 823.5 | 0.8235 | 28.9152 | 7.5525 | 5.8234 | 0.022441 | 63.066 | 1.3058
2025-05-20 07:28 | 2538 | Remove | 2025-05-20 | 7:28 | US | GS | - | 134 | g | 0 | 114.1 | 11.165 | 1095.4 | 8698 | 21:11 | 28.3 | 1.97 m/s | 25.9 | 29.7 | 4.3 m/s | 19.2 |  | 1.97 | m/s |  | 4.3 | m/s | 21.1869 | 0.0091283 | 23.8208 |  | -6 | 823.5 | 0.8235 | 28.9263 | 7.1652 | 5.7339 | 0.020763 | 63.0868 | 1.3053
2025-05-20 07:28 | 2539 | Remove | 2025-05-20 | 7:28 | ST | GS | - | 133.5 | g | 0 | 114.1 | 11.161 | 1094.7 | 8707 | 21:12 | 28.4 | 2.11 m/s | 26.3 | 29.7 | 4.63 m/s | 19.4 |  | 2.11 | m/s |  | 4.63 | m/s | 21.1953 | 0.0091225 | 23.8299 |  | -0.5 | 823.5 | 0.8235 | 28.9374 | 7.3159 | 5.7936 | 0.022707 | 63.1095 | 1.3049
2025-05-20 07:29 | 2540 | Remove | 2025-05-20 | 7:29 | ST | GS | - | 130.5 | g | 0 | 114 | 11.137 | 1091.8 | 8716 | 21:12 | 28.4 | 2.11 m/s | 26.3 | 29.7 | 4.96 m/s | 20 |  | 2.11 | m/s |  | 4.96 | m/s | 21.2036 | 0.0090983 | 23.839 |  | -3 | 823.5 | 0.8235 | 28.9484 | 7.3159 | 5.9728 | 0.022707 | 63.1322 | 1.3044
2025-05-20 07:29 | 2541 | Remove | 2025-05-20 | 7:29 | US | GS | - | 134.5 | g | 0 | 114 | 11.137 | 1092.2 | 8725 | 21:13 | 28.4 | 2.13 m/s | 27 | 29.7 | 4.3 m/s | 20 |  | 2.13 | m/s |  | 4.3 | m/s | 21.2119 | 0.0091017 | 23.8481 |  | 4 | 827.5 | 0.8275 | 28.8195 | 7.5106 | 5.9728 | 0.023532 | 63.1557 | 1.3103
2025-05-20 07:30 | 2542 | Remove | 2025-05-20 | 7:30 | US | GS | - | 130 | g | 0 | 114 | 11.145 | 1093.5 | 8734 | 21:13 | 28.4 | 1.83 m/s | 27.1 | 29.7 | 4.33 m/s | 19.5 |  | 1.83 | m/s |  | 4.33 | m/s | 21.2203 | 0.0091125 | 23.8573 |  | -4.5 | 827.5 | 0.8275 | 28.8305 | 7.5384 | 5.8234 | 0.020292 | 63.176 | 1.3098
2025-05-20 07:30 | 2543 | Remove | 2025-05-20 | 7:30 | ST | GS | - | 136 | g | 0 | 113.8 | 11.17 | 1096.3 | 8744 | 21:14 | 28.4 | 2.08 m/s | 26.3 | 29.7 | 4.38 m/s | 19.3 |  | 2.08 | m/s |  | 4.38 | m/s | 21.2286 | 0.0091358 | 23.8664 |  | 6 | 833.5 | 0.8335 | 28.634 | 7.3159 | 5.7637 | 0.022384 | 63.1984 | 1.3189
2025-05-20 07:31 | 2544 | Remove | 2025-05-20 | 7:31 | US | GS | - | 135.5 | g | 0 | 113.7 | 11.163 | 1095.3 | 8753 | 21:14 | 28.4 | 1.95 m/s | 26.2 | 29.7 | 4.56 m/s | 19.3 |  | 1.95 | m/s |  | 4.56 | m/s | 21.2369 | 0.0091275 | 23.8755 |  | -0.5 | 833.5 | 0.8335 | 28.6449 | 7.2881 | 5.7637 | 0.020905 | 63.2193 | 1.3184
2025-05-20 07:31 | 2545 | Remove | 2025-05-20 | 7:31 | US | GS | - | 140 | g | 0 | 113.9 | 11.112 | 1089.4 | 8762 | 21:15 | 28.4 | 1.98 m/s | 26.3 | 29.7 | 4.38 m/s | 19.2 |  | 1.98 | m/s |  | 4.38 | m/s | 21.2453 | 0.0090783 | 23.8846 |  | 4.5 | 838 | 0.838 | 28.5019 | 7.3159 | 5.7339 | 0.021308 | 63.2406 | 1.3251
2025-05-20 07:32 | 2546 | Remove | 2025-05-20 | 7:32 | ST | GS | - | 133 | g | 0 | 113.8 | 11.185 | 1098.7 | 8771 | 21:15 | 28.4 | 1.9 m/s | 26.1 | 29.8 | 4.94 m/s | 18.8 |  | 1.9 | m/s |  | 4.94 | m/s | 21.2536 | 0.0091558 | 23.8938 |  | -7 | 838 | 0.838 | 28.5128 | 7.2603 | 5.645 | 0.020291 | 63.2609 | 1.3247
2025-05-20 07:32 | 2547 | Remove | 2025-05-20 | 7:32 | ST | GS | - | 131.5 | g | 0 | 113.9 | 11.167 | 1096.4 | 8780 | 21:16 | 28.4 | 2.13 m/s | 25.7 | 29.8 | 4.69 m/s | 19.4 |  | 2.13 | m/s |  | 4.69 | m/s | 21.2619 | 0.0091367 | 23.9029 |  | -1.5 | 838 | 0.838 | 28.5237 | 7.149 | 5.8251 | 0.022399 | 63.2833 | 1.3242
2025-05-20 07:33 | 2548 | Remove | 2025-05-20 | 7:33 | US | GS | - | 128.5 | g | 0 | 113.7 | 11.155 | 1095.1 | 8789 | 21:16 | 28.4 | 2.2 m/s | 26.6 | 29.8 | 4.26 m/s | 18.7 |  | 2.2 | m/s |  | 4.26 | m/s | 21.2703 | 0.0091258 | 23.912 |  | -3 | 838 | 0.838 | 28.5346 | 7.3993 | 5.615 | 0.023945 | 63.3072 | 1.3237
2025-05-20 07:33 | 2549 | Remove | 2025-05-20 | 7:33 | ST | GS | - | 134 | g | 0 | 113.9 | 11.183 | 1097.9 | 8799 | 21:17 | 28.4 | 2.02 m/s | 25.7 | 29.8 | 4.76 m/s | 19.3 |  | 2.02 | m/s |  | 4.76 | m/s | 21.2786 | 0.0091492 | 23.9212 |  | 5.5 | 843.5 | 0.8435 | 28.3594 | 7.149 | 5.7951 | 0.021242 | 63.3285 | 1.3319
2025-05-20 07:34 | 2550 | Remove | 2025-05-20 | 7:34 | ST | GS | - | 130 | g | 0 | 113.8 | 11.189 | 1098.6 | 8808 | 21:17 | 28.4 | 2.16 m/s | 26.2 | 29.8 | 4.56 m/s | 19.1 |  | 2.16 | m/s |  | 4.56 | m/s | 21.2869 | 0.009155 | 23.9303 |  | -4 | 843.5 | 0.8435 | 28.3703 | 7.2881 | 5.7351 | 0.023156 | 63.3516 | 1.3315
2025-05-20 07:34 | 2551 | Keep | 2025-05-20 | 7:34 | US | GS | - | 133.5 | g | 0 | 113.8 | 11.186 | 1098.2 | 8817 | 21:18 | 28.4 | 1.87 m/s | 26 | 29.8 | 4.56 m/s | 19.1 |  | 1.87 | m/s |  | 4.56 | m/s | 21.2953 | 0.0091517 | 23.9395 |  | 3.5 | 847 | 0.847 | 28.2638 | 7.2324 | 5.7351 | 0.019894 | 63.3715 | 1.3366
2025-05-20 07:35 | 2552 | Remove | 2025-05-20 | 7:35 | ST | GS | - | 139.5 | g | 0 | 113.8 | 11.208 | 1101.3 | 8826 | 21:18 | 28.4 | 2.01 m/s | 25.8 | 29.8 | 4.63 m/s | 18.9 |  | 2.01 | m/s |  | 4.63 | m/s | 21.3036 | 0.0091775 | 23.9487 |  | 6 | 853 | 0.853 | 28.0758 | 7.1768 | 5.675 | 0.021219 | 63.3927 | 1.3456
2025-05-20 07:35 | 2553 | Remove | 2025-05-20 | 7:35 | ST | GS | - | 135 | g | 0 | 113.8 | 11.175 | 1097.2 | 8835 | 21:19 | 28.4 | 2.12 m/s | 25.2 | 29.8 | 4.46 m/s | 18.5 |  | 2.12 | m/s |  | 4.46 | m/s | 21.3119 | 0.0091433 | 23.9578 |  | -4.5 | 853 | 0.853 | 28.0865 | 7.0099 | 5.5549 | 0.02186 | 63.4146 | 1.3451
2025-05-20 07:36 | 2554 | Remove | 2025-05-20 | 7:36 | US | GS | - | 135 | g | 0 | 113.7 | 11.212 | 1102 | 8845 | 21:19 | 28.4 | 1.81 m/s | 25.4 | 29.8 | 4.35 m/s | 18.7 |  | 1.81 | m/s |  | 4.35 | m/s | 21.3206 | 0.0091833 | 23.967 |  | 0 | 853 | 0.853 | 28.0973 | 7.0655 | 5.615 | 0.018812 | 63.4334 | 1.3447
2025-05-20 07:36 | 2555 | Remove | 2025-05-20 | 7:36 | ST | GS | - | 134.5 | g | 0 | 113.9 | 11.168 | 1096 | 8854 | 21:20 | 28.5 | 1.98 m/s | 24.5 | 29.8 | 4.55 m/s | 18.2 |  | 1.98 | m/s |  | 4.55 | m/s | 21.3289 | 0.0091333 | 23.9761 |  | -0.5 | 853 | 0.853 | 28.108 | 6.8527 | 5.4648 | 0.019959 | 63.4534 | 1.3443
2025-05-20 07:37 | 2556 | Remove | 2025-05-20 | 7:37 | US | GS | - | 133 | g | 0 | 113.9 | 11.175 | 1097.7 | 8863 | 21:20 | 28.4 | 1.93 m/s | 25.4 | 29.8 | 4.44 m/s | 18.7 |  | 1.93 | m/s |  | 4.44 | m/s | 21.3372 | 0.0091475 | 23.9853 |  | -1.5 | 853 | 0.853 | 28.1187 | 7.0655 | 5.615 | 0.020059 | 63.4734 | 1.3439
2025-05-20 07:37 | 2557 | Remove | 2025-05-20 | 7:37 | ST | GS | - | 134 | g | 0 | 113.8 | 11.219 | 1103.3 | 8872 | 21:21 | 28.4 | 2.05 m/s | 25.4 | 29.9 | 4.41 m/s | 18.4 |  | 2.05 | m/s |  | 4.41 | m/s | 21.3458 | 0.0091942 | 23.9945 |  | 1 | 854 | 0.854 | 28.0966 | 7.0655 | 5.555 | 0.021306 | 63.4947 | 1.345
2025-05-20 07:38 | 2558 | Remove | 2025-05-20 | 7:38 | ST | GS | - | 134 | g | 0 | 113.8 | 11.214 | 1102 | 8881 | 21:21 | 28.5 | 2.01 m/s | 24.8 | 29.9 | 4.41 m/s | 18.4 |  | 2.01 | m/s |  | 4.41 | m/s | 21.3542 | 0.0091833 | 24.0036 |  | 0 | 854 | 0.854 | 28.1073 | 6.9366 | 5.555 | 0.020509 | 63.5152 | 1.3446
2025-05-20 07:38 | 2559 | Remove | 2025-05-20 | 7:38 | ST | GS | - | 134 | g | 0 | 113.8 | 11.19 | 1099.2 | 8890 | 21:22 | 28.5 | 2.12 m/s | 24.8 | 29.9 | 4.38 m/s | 18.3 |  | 2.12 | m/s |  | 4.38 | m/s | 21.3625 | 0.00916 | 24.0128 |  | 0 | 854 | 0.854 | 28.118 | 6.9366 | 5.5248 | 0.021631 | 63.5369 | 1.3441
2025-05-20 07:39 | 2560 | Remove | 2025-05-20 | 7:39 | US | GS | - | 131 | g | 0 | 113.8 | 11.195 | 1100.1 | 8900 | 21:22 | 28.5 | 2.13 m/s | 25.5 | 29.9 | 4.44 m/s | 18.8 |  | 2.13 | m/s |  | 4.44 | m/s | 21.3708 | 0.0091675 | 24.022 |  | -3 | 854 | 0.854 | 28.1288 | 7.1324 | 5.6757 | 0.022347 | 63.5592 | 1.3436
2025-05-20 07:39 | 2561 | Remove | 2025-05-20 | 7:39 | ST | GS | - | 133.5 | g | 0 | 113.6 | 11.227 | 1103.9 | 8909 | 21:23 | 28.5 | 2.13 m/s | 25.3 | 29.9 | 4.87 m/s | 18.5 |  | 2.13 | m/s |  | 4.87 | m/s | 21.3792 | 0.0091992 | 24.0312 |  | 2.5 | 856.5 | 0.8565 | 28.0574 | 7.0764 | 5.5851 | 0.022172 | 63.5814 | 1.3471
2025-05-20 07:40 | 2562 | Remove | 2025-05-20 | 7:40 | US | GS | - | 132.5 | g | 0 | 113.7 | 11.203 | 1101 | 8918 | 21:23 | 28.5 | 1.91 m/s | 24.8 | 29.9 | 4.29 m/s | 18.3 |  | 1.91 | m/s |  | 4.29 | m/s | 21.3875 | 0.009175 | 24.0403 |  | -1 | 856.5 | 0.8565 | 28.0681 | 6.9366 | 5.5248 | 0.019489 | 63.6009 | 1.3467
2025-05-20 07:40 | 2563 | Remove | 2025-05-20 | 7:40 | US | GS | - | 136 | g | 0 | 113.7 | 11.185 | 1098.4 | 8927 | 21:24 | 28.5 | 2.15 m/s | 24.8 | 29.9 | 4.33 m/s | 18.3 |  | 2.15 | m/s |  | 4.33 | m/s | 21.3958 | 0.0091533 | 24.0495 |  | 3.5 | 860 | 0.86 | 27.9645 | 6.9366 | 5.5248 | 0.021937 | 63.6228 | 1.3517
2025-05-20 07:41 | 2564 | Remove | 2025-05-20 | 7:41 | ST | GS | - | 137 | g | 0 | 113.7 | 11.183 | 1098.9 | 8936 | 21:24 | 28.5 | 2.08 m/s | 25.6 | 29.9 | 4.9 m/s | 18.7 |  | 2.08 | m/s |  | 4.9 | m/s | 21.4042 | 0.0091575 | 24.0587 |  | 1 | 861 | 0.861 | 27.9427 | 7.1604 | 5.6455 | 0.021908 | 63.6447 | 1.3528
2025-05-20 07:41 | 2565 | Remove | 2025-05-20 | 7:41 | ST | GS | - | 135 | g | 0 | 113.5 | 11.193 | 1099.1 | 8946 | 21:25 | 28.5 | 2.01 m/s | 25.5 | 29.9 | 4.87 m/s | 18.6 |  | 2.01 | m/s |  | 4.87 | m/s | 21.4125 | 0.0091592 | 24.0678 |  | -2 | 861 | 0.861 | 27.9533 | 7.1324 | 5.6153 | 0.021088 | 63.6658 | 1.3524
2025-05-20 07:42 | 2566 | Remove | 2025-05-20 | 7:42 | ST | GS | - | 132.5 | g | 0 | 113.7 | 11.198 | 1100.3 | 8955 | 21:25 | 28.5 | 1.97 m/s | 24.6 | 29.9 | 4.38 m/s | 18.1 |  | 1.97 | m/s |  | 4.38 | m/s | 21.4208 | 0.0091692 | 24.077 |  | -2.5 | 861 | 0.861 | 27.964 | 6.8807 | 5.4644 | 0.019939 | 63.6858 | 1.352
2025-05-20 07:42 | 2567 | Remove | 2025-05-20 | 7:42 | ST | GS | - | 135.5 | g | 0 | 113.6 | 11.233 | 1104.6 | 8964 | 21:26 | 28.5 | 2.18 m/s | 24.6 | 29.9 | 4.63 m/s | 18.3 |  | 2.18 | m/s |  | 4.63 | m/s | 21.4292 | 0.009205 | 24.0862 |  | 3 | 864 | 0.864 | 27.8775 | 6.8807 | 5.5248 | 0.022064 | 63.7078 | 1.3562
2025-05-20 07:43 | 2568 | Remove | 2025-05-20 | 7:43 | ST | GS | - | 134.5 | g | 0 | 113.7 | 11.223 | 1103.3 | 8973 | 21:26 | 28.5 | 2.0 m/s | 25 | 29.9 | 4.38 m/s | 18.4 |  | 2 | m/s |  | 4.38 | m/s | 21.4375 | 0.0091942 | 24.0954 |  | -1 | 864 | 0.864 | 27.8882 | 6.9925 | 5.555 | 0.020572 | 63.7284 | 1.3558
2025-05-20 07:43 | 2569 | Remove | 2025-05-20 | 7:43 | ST | GS | - | 135.5 | g | 0 | 113.7 | 11.204 | 1100.7 | 8983 | 21:27 | 28.5 | 1.95 m/s | 24.8 | 29.9 | 4.44 m/s | 18.2 |  | 1.95 | m/s |  | 4.44 | m/s | 21.4458 | 0.0091725 | 24.1046 |  | 1 | 865 | 0.865 | 27.8665 | 6.9366 | 5.4946 | 0.019897 | 63.7483 | 1.3569
2025-05-20 07:44 | 2570 | Remove | 2025-05-20 | 7:44 | US | GS | - | 134.5 | g | 0 | 113.6 | 11.253 | 1106.8 | 8992 | 21:27 | 28.5 | 2.11 m/s | 26 | 29.9 | 4.58 m/s | 18.9 |  | 2.11 | m/s |  | 4.58 | m/s | 21.4542 | 0.0092233 | 24.1138 |  | -1 | 865 | 0.865 | 27.8772 | 7.2722 | 5.7059 | 0.022571 | 63.7709 | 1.3564
2025-05-20 07:44 | 2571 | Remove | 2025-05-20 | 7:44 | ST | GS | - | 135.5 | g | 0 | 113.6 | 11.218 | 1102.1 | 9001 | 21:28 | 28.5 | 2.12 m/s | 25.3 | 29.9 | 4.29 m/s | 18.7 |  | 2.12 | m/s |  | 4.29 | m/s | 21.4625 | 0.0091842 | 24.123 |  | 1 | 866 | 0.866 | 27.8556 | 7.0764 | 5.6455 | 0.022068 | 63.7929 | 1.3575
2025-05-20 07:45 | 2572 | Remove | 2025-05-20 | 7:45 | ST | GS | - | 133 | g | 0 | 113.6 | 11.23 | 1103.6 | 9010 | 21:28 | 28.5 | 2.06 m/s | 24.8 | 29.9 | 4.81 m/s | 18.3 |  | 2.06 | m/s |  | 4.81 | m/s | 21.4708 | 0.0091967 | 24.1322 |  | -2.5 | 866 | 0.866 | 27.8662 | 6.9366 | 5.5248 | 0.021019 | 63.814 | 1.3571
2025-05-20 07:45 | 2573 | Remove | 2025-05-20 | 7:45 | ST | GS | - | 133.5 | g | 0 | 113.7 | 11.178 | 1097.3 | 9019 | 21:29 | 28.5 | 2.22 m/s | 25.1 | 29.9 | 4.5 m/s | 18.3 |  | 2.22 | m/s |  | 4.5 | m/s | 21.4792 | 0.0091442 | 24.1413 |  | 0.5 | 866.5 | 0.8665 | 27.8607 | 7.0205 | 5.5248 | 0.022926 | 63.8369 | 1.3574
2025-05-20 07:46 | 2574 | Remove | 2025-05-20 | 7:46 | US | GS | - | 135.5 | g | 0 | 113.6 | 11.226 | 1103.4 | 9028 | 21:29 | 28.5 | 2.25 m/s | 25.5 | 29.9 | 4.3 m/s | 18.7 |  | 2.25 | m/s |  | 4.3 | m/s | 21.4875 | 0.009195 | 24.1505 |  | 2 | 868.5 | 0.8685 | 27.8071 | 7.1324 | 5.6455 | 0.023606 | 63.8605 | 1.36
2025-05-20 07:46 | 2575 | Remove | 2025-05-20 | 7:46 | ST | GS | - | 133 | g | 0 | 113.6 | 11.257 | 1108.2 | 9038 | 21:30 | 28.5 | 2.0 m/s | 25.1 | 29.9 | 4.4 m/s | 18.4 |  | 2 | m/s |  | 4.4 | m/s | 21.4961 | 0.009235 | 24.1597 |  | -2.5 | 868.5 | 0.8685 | 27.8178 | 7.0205 | 5.555 | 0.020654 | 63.8811 | 1.3596
2025-05-20 07:47 | 2576 | Remove | 2025-05-20 | 7:47 | US | GS | - | 133 | g | 0 | 113.5 | 11.249 | 1106.2 | 9047 | 21:30 | 28.5 | 2.02 m/s | 24.6 | 29.9 | 4.3 m/s | 18.2 |  | 2.02 | m/s |  | 4.3 | m/s | 21.5044 | 0.0092183 | 24.1689 |  | 0 | 868.5 | 0.8685 | 27.8284 | 6.8807 | 5.4946 | 0.020445 | 63.9016 | 1.3591
2025-05-20 07:47 | 2577 | Remove | 2025-05-20 | 7:47 | US | GS | - | 131.5 | g | 0 | 113.6 | 11.214 | 1102.2 | 9056 | 21:31 | 28.5 | 2.13 m/s | 25.1 | 29.9 | 4.4 m/s | 18.4 |  | 2.13 | m/s |  | 4.4 | m/s | 21.5128 | 0.009185 | 24.1781 |  | -1.5 | 868.5 | 0.8685 | 27.839 | 7.0205 | 5.555 | 0.021996 | 63.9236 | 1.3587
2025-05-20 07:48 | 2578 | Remove | 2025-05-20 | 7:48 | ST | GS | - | 134.5 | g | 0 | 113.5 | 11.251 | 1106.5 | 9065 | 21:31 | 28.5 | 2.12 m/s | 25.2 | 29.9 | 5.11 m/s | 18.5 |  | 2.12 | m/s |  | 5.11 | m/s | 21.5211 | 0.0092208 | 24.1874 |  | 3 | 871.5 | 0.8715 | 27.7537 | 7.0485 | 5.5851 | 0.02198 | 63.9456 | 1.3629
2025-05-20 07:48 | 2579 | Remove | 2025-05-20 | 7:48 | US | GS | - | 135 | g | 0 | 113.5 | 11.255 | 1107.4 | 9075 | 21:32 | 28.5 | 2.12 m/s | 25.6 | 30 | 5.03 m/s | 18.6 |  | 2.12 | m/s |  | 5.03 | m/s | 21.5294 | 0.0092283 | 24.1966 |  | 0.5 | 872 | 0.872 | 27.7484 | 7.1604 | 5.6459 | 0.022329 | 63.9679 | 1.3632
2025-05-20 07:49 | 2580 | Remove | 2025-05-20 | 7:49 | US | GS | - | 134 | g | 0 | 113.5 | 11.268 | 1108.2 | 9084 | 21:32 | 28.5 | 2.18 m/s | 25 | 30 | 4.58 m/s | 18.3 |  | 2.18 | m/s |  | 4.58 | m/s | 21.5378 | 0.009235 | 24.2058 |  | -1 | 872 | 0.872 | 27.759 | 6.9925 | 5.5548 | 0.022423 | 63.9903 | 1.3627
2025-05-20 07:49 | 2581 | Keep | 2025-05-20 | 7:49 | ST | GS | - | 136 | g | 0 | 113.5 | 11.223 | 1103.3 | 9093 | 21:33 | 28.5 | 1.86 m/s | 24.8 | 30 | 4.29 m/s | 18.3 |  | 1.86 | m/s |  | 4.29 | m/s | 21.5461 | 0.0091942 | 24.215 |  | 2 | 874 | 0.874 | 27.706 | 6.9366 | 5.5548 | 0.018978 | 64.0093 | 1.3654
2025-05-20 07:50 | 2582 | Remove | 2025-05-20 | 7:50 | US | GS | - | 138 | g | 0 | 113.5 | 11.265 | 1108.4 | 9102 | 21:33 | 28.5 | 2.0 m/s | 25 | 30 | 4.3 m/s | 18.3 |  | 2 | m/s |  | 4.3 | m/s | 21.5544 | 0.0092367 | 24.2242 |  | 2 | 876 | 0.876 | 27.6533 | 6.9925 | 5.5548 | 0.020572 | 64.0299 | 1.3681
2025-05-20 07:50 | 2583 | Remove | 2025-05-20 | 7:50 | ST | GS | - | 142 | g | 0 | 113.6 | 11.236 | 1104.8 | 9112 | 21:34 | 28.6 | 1.9 m/s | 24.3 | 30 | 4.53 m/s | 18 |  | 1.9 | m/s |  | 4.53 | m/s | 21.5628 | 0.0092067 | 24.2335 |  | 4 | 880 | 0.88 | 27.538 | 6.8341 | 5.4637 | 0.0191 | 64.049 | 1.3739
2025-05-20 07:51 | 2584 | Remove | 2025-05-20 | 7:51 | US | GS | - | 133.5 | g | 0 | 113.4 | 11.25 | 1106.9 | 9121 | 21:34 | 28.6 | 2.06 m/s | 24 | 30 | 4.44 m/s | 17.9 |  | 2.06 | m/s |  | 4.44 | m/s | 21.5711 | 0.0092242 | 24.2427 |  | -8.5 | 880 | 0.88 | 27.5485 | 6.7497 | 5.4334 | 0.020453 | 64.0694 | 1.3735
2025-05-20 07:51 | 2585 | Remove | 2025-05-20 | 7:51 | ST | GS | - | 135 | g | 0 | 113.5 | 11.253 | 1106.5 | 9130 | 21:35 | 28.6 | 2.05 m/s | 25.1 | 30 | 4.46 m/s | 18.3 |  | 2.05 | m/s |  | 4.46 | m/s | 21.5794 | 0.0092208 | 24.2519 |  | 1.5 | 881.5 | 0.8815 | 27.5121 | 7.0591 | 5.5548 | 0.021287 | 64.0907 | 1.3754
2025-05-20 07:52 | 2586 | Remove | 2025-05-20 | 7:52 | US | GS | - | 135 | g | 0 | 113.5 | 11.278 | 1110.1 | 9139 | 21:35 | 28.6 | 2.12 m/s | 24.7 | 30 | 4.72 m/s | 18.1 |  | 2.12 | m/s |  | 4.72 | m/s | 21.5878 | 0.0092508 | 24.2612 |  | 0 | 881.5 | 0.8815 | 27.5226 | 6.9466 | 5.4941 | 0.021663 | 64.1124 | 1.3749
2025-05-20 07:52 | 2587 | Remove | 2025-05-20 | 7:52 | US | GS | - | 135.5 | g | 0 | 113.6 | 11.254 | 1108 | 9149 | 21:36 | 28.6 | 2.0 m/s | 24.4 | 30 | 4.5 m/s | 18 |  | 2 | m/s |  | 4.5 | m/s | 21.5961 | 0.0092333 | 24.2704 |  | 0.5 | 882 | 0.882 | 27.5174 | 6.8622 | 5.4637 | 0.020188 | 64.1326 | 1.3753
2025-05-20 07:53 | 2588 | Remove | 2025-05-20 | 7:53 | ST | GS | - | 134 | g | 0 | 113.5 | 11.271 | 1108.8 | 9158 | 21:36 | 28.6 | 2.13 m/s | 24.7 | 30 | 4.84 m/s | 18.1 |  | 2.13 | m/s |  | 4.84 | m/s | 21.6044 | 0.00924 | 24.2796 |  | -1.5 | 882 | 0.882 | 27.5279 | 6.9466 | 5.4941 | 0.021765 | 64.1543 | 1.3748
2025-05-20 07:53 | 2589 | Remove | 2025-05-20 | 7:53 | US | GS | - | 141 | g | 0 | 113.5 | 11.251 | 1107.5 | 9167 | 21:37 | 28.6 | 2.15 m/s | 25 | 30 | 4.35 m/s | 18.3 |  | 2.15 | m/s |  | 4.35 | m/s | 21.6128 | 0.0092292 | 24.2889 |  | 7 | 889 | 0.889 | 27.3215 | 7.031 | 5.5548 | 0.022236 | 64.1766 | 1.3852
2025-05-20 07:54 | 2590 | Remove | 2025-05-20 | 7:54 | ST | GS | - | 137.5 | g | 0 | 113.6 | 11.269 | 1108.8 | 9176 | 21:37 | 28.6 | 2.02 m/s | 24.6 | 30 | 4.38 m/s | 17.9 |  | 2.02 | m/s |  | 4.38 | m/s | 21.6211 | 0.00924 | 24.2981 |  | -3.5 | 889 | 0.889 | 27.3319 | 6.9185 | 5.4334 | 0.020557 | 64.1971 | 1.3848
2025-05-20 07:54 | 2591 | Remove | 2025-05-20 | 7:54 | ST | GS | - | 136.5 | g | 0 | 113.5 | 11.279 | 1110 | 9186 | 21:38 | 28.6 | 1.86 m/s | 24.2 | 30 | 4.41 m/s | 17.8 |  | 1.86 | m/s |  | 4.41 | m/s | 21.6294 | 0.00925 | 24.3073 |  | -1 | 889 | 0.889 | 27.3423 | 6.806 | 5.403 | 0.018621 | 64.2157 | 1.3844
2025-05-20 07:55 | 2592 | Remove | 2025-05-20 | 7:55 | ST | GS | - | 135 | g | 0 | 113.5 | 11.285 | 1110.6 | 9195 | 21:38 | 28.6 | 1.97 m/s | 24.1 | 30 | 4.41 m/s | 17.8 |  | 1.97 | m/s |  | 4.41 | m/s | 21.6381 | 0.009255 | 24.3166 |  | -1.5 | 889 | 0.889 | 27.3528 | 6.7779 | 5.403 | 0.019641 | 64.2354 | 1.384
2025-05-20 07:55 | 2593 | Remove | 2025-05-20 | 7:55 | ST | GS | - | 136.5 | g | 0 | 113.4 | 11.296 | 1112.7 | 9204 | 21:39 | 28.6 | 2.0 m/s | 24 | 30 | 4.4 m/s | 17.7 |  | 2 | m/s |  | 4.4 | m/s | 21.6464 | 0.0092725 | 24.3259 |  | 1.5 | 890.5 | 0.8905 | 27.3171 | 6.7497 | 5.3727 | 0.019857 | 64.2552 | 1.3859
2025-05-20 07:56 | 2594 | Remove | 2025-05-20 | 7:56 | US | GS | - | 135.5 | g | 0 | 113.4 | 11.29 | 1111.7 | 9214 | 21:39 | 28.6 | 2.11 m/s | 24.5 | 30 | 4.85 m/s | 18 |  | 2.11 | m/s |  | 4.85 | m/s | 21.6547 | 0.0092642 | 24.3351 |  | -1 | 890.5 | 0.8905 | 27.3275 | 6.8904 | 5.4637 | 0.021386 | 64.2766 | 1.3854
2025-05-20 07:56 | 2595 | Remove | 2025-05-20 | 7:56 | ST | GS | - | 139.5 | g | 0 | 113.5 | 11.279 | 1110.4 | 9223 | 21:40 | 28.6 | 2.18 m/s | 23.9 | 30 | 4.96 m/s | 17.6 |  | 2.18 | m/s |  | 4.96 | m/s | 21.6631 | 0.0092533 | 24.3444 |  | 4 | 894.5 | 0.8945 | 27.2156 | 6.7216 | 5.3423 | 0.021554 | 64.2982 | 1.3912
2025-05-20 07:57 | 2596 | Remove | 2025-05-20 | 7:57 | ST | GS | - | 140.5 | g | 0 | 113.5 | 11.301 | 1113 | 9232 | 21:40 | 28.6 | 1.9 m/s | 23.4 | 30 | 4.38 m/s | 17.4 |  | 1.9 | m/s |  | 4.38 | m/s | 21.6714 | 0.009275 | 24.3537 |  | 1 | 895.5 | 0.8955 | 27.1956 | 6.581 | 5.2816 | 0.018393 | 64.3166 | 1.3923
2025-05-20 07:57 | 2597 | Remove | 2025-05-20 | 7:57 | US | GS | - | 137.5 | g | 0 | 113.4 | 11.3 | 1112.8 | 9241 | 21:41 | 28.6 | 1.9 m/s | 23.3 | 30 | 4.43 m/s | 17.4 |  | 1.9 | m/s |  | 4.43 | m/s | 21.6797 | 0.0092733 | 24.3629 |  | -3 | 895.5 | 0.8955 | 27.206 | 6.5529 | 5.2816 | 0.018314 | 64.3349 | 1.3919
2025-05-20 07:58 | 2598 | Remove | 2025-05-20 | 7:58 | ST | GS | - | 133 | g | 0 | 113.4 | 11.331 | 1116.6 | 9251 | 21:41 | 28.6 | 1.89 m/s | 23.8 | 30 | 4.38 m/s | 17.7 |  | 1.89 | m/s |  | 4.38 | m/s | 21.6881 | 0.009305 | 24.3722 |  | -4.5 | 895.5 | 0.8955 | 27.2164 | 6.6935 | 5.3727 | 0.018609 | 64.3535 | 1.3915
2025-05-20 07:58 | 2599 | Remove | 2025-05-20 | 7:58 | ST | GS | - | 140 | g | 0 | 113.3 | 11.292 | 1112.5 | 9260 | 21:42 | 28.7 | 2.05 m/s | 24 | 30 | 4.47 m/s | 17.8 |  | 2.05 | m/s |  | 4.47 | m/s | 21.6964 | 0.0092708 | 24.3815 |  | 7 | 902.5 | 0.9025 | 27.0155 | 6.7868 | 5.403 | 0.020465 | 64.3739 | 1.402
2025-05-20 07:59 | 2600 | Remove | 2025-05-20 | 7:59 | ST | GS | - | 138.5 | g | 0 | 113.3 | 11.323 | 1116.5 | 9269 | 21:42 | 28.7 | 2.08 m/s | 23.5 | 30 | 4.56 m/s | 17.4 |  | 2.08 | m/s |  | 4.56 | m/s | 21.7047 | 0.0093042 | 24.3908 |  | -1.5 | 902.5 | 0.9025 | 27.0258 | 6.6454 | 5.2816 | 0.020332 | 64.3943 | 1.4015
2025-05-20 07:59 | 2601 | Remove | 2025-05-20 | 7:59 | ST | GS | - | 139.5 | g | 0 | 113.2 | 11.317 | 1115.1 | 9279 | 21:43 | 28.7 | 2.05 m/s | 24 | 30.1 | 4.27 m/s | 17.7 |  | 2.05 | m/s |  | 4.27 | m/s | 21.7131 | 0.0092925 | 24.4001 |  | 1 | 903.5 | 0.9035 | 27.0062 | 6.7868 | 5.4019 | 0.020465 | 64.4147 | 1.4026
2025-05-20 08:00 | 2602 | Remove | 2025-05-20 | 8:00 | ST | GS | - | 137.5 | g | 0 | 113.3 | 11.328 | 1116.8 | 9288 | 21:43 | 28.7 | 1.94 m/s | 23.8 | 30.1 | 4.35 m/s | 17.7 |  | 1.94 | m/s |  | 4.35 | m/s | 21.7214 | 0.0093067 | 24.4094 |  | -2 | 903.5 | 0.9035 | 27.0165 | 6.7303 | 5.4019 | 0.019206 | 64.434 | 1.4022
2025-05-20 08:00 | 2603 | Remove | 2025-05-20 | 8:00 | ST | GS | - | 138 | g | 0 | 113.4 | 11.314 | 1115.2 | 9297 | 21:44 | 28.7 | 1.95 m/s | 23.4 | 30.1 | 4.33 m/s | 17.4 |  | 1.95 | m/s |  | 4.33 | m/s | 21.7297 | 0.0092933 | 24.4187 |  | 0.5 | 904 | 0.904 | 27.0118 | 6.6171 | 5.3103 | 0.01898 | 64.4529 | 1.4026
2025-05-20 08:01 | 2604 | Remove | 2025-05-20 | 8:01 | US | GS | - | 147 | g | 0 | 113.3 | 11.32 | 1115.5 | 9307 | 21:44 | 28.7 | 1.79 m/s | 23.5 | 30.1 | 4.32 m/s | 17.4 |  | 1.79 | m/s |  | 4.32 | m/s | 21.7381 | 0.0092958 | 24.428 |  | 9 | 913 | 0.913 | 26.7558 | 6.6454 | 5.3103 | 0.017498 | 64.4704 | 1.4162
2025-05-20 08:01 | 2605 | Remove | 2025-05-20 | 8:01 | US | GS | - | 138 | g | 0 | 113.3 | 11.291 | 1112 | 9316 | 21:45 | 28.7 | 2.0 m/s | 23 | 30.1 | 4.27 m/s | 17.1 |  | 2 | m/s |  | 4.27 | m/s | 21.7464 | 0.0092667 | 24.4373 |  | -9 | 913 | 0.913 | 26.7659 | 6.504 | 5.2188 | 0.019134 | 64.4896 | 1.4157
2025-05-20 08:02 | 2606 | Remove | 2025-05-20 | 8:02 | US | GS | - | 133 | g | 0 | 113.1 | 11.314 | 1112.3 | 9325 | 21:45 | 28.7 | 2.02 m/s | 23.3 | 30.1 | 4.46 m/s | 17.3 |  | 2.02 | m/s |  | 4.46 | m/s | 21.7547 | 0.0092692 | 24.4465 |  | -5 | 913 | 0.913 | 26.7761 | 6.5889 | 5.2798 | 0.019578 | 64.5091 | 1.4153
2025-05-20 08:02 | 2607 | Remove | 2025-05-20 | 8:02 | ST | GS | - | 132.5 | g | 0 | 113.3 | 11.28 | 1111.1 | 9335 | 21:46 | 28.7 | 2.08 m/s | 23.2 | 30.1 | 4.21 m/s | 17.3 |  | 2.08 | m/s |  | 4.21 | m/s | 21.7631 | 0.0092592 | 24.4558 |  | -0.5 | 913 | 0.913 | 26.7862 | 6.5606 | 5.2798 | 0.020073 | 64.5292 | 1.4149
2025-05-20 08:03 | 2608 | Remove | 2025-05-20 | 8:03 | ST | GS | - | 139 | g | 0 | 113.2 | 11.331 | 1116 | 9344 | 21:46 | 28.7 | 1.86 m/s | 23.8 | 30.1 | 4.38 m/s | 17.6 |  | 1.86 | m/s |  | 4.38 | m/s | 21.7714 | 0.0093 | 24.4651 |  | 6.5 | 919.5 | 0.9195 | 26.607 | 6.7303 | 5.3714 | 0.018414 | 64.5476 | 1.4245
2025-05-20 08:04 | 2609 | Remove | 2025-05-20 | 8:03 | ST | GS | - | 135.5 | g | 0 | 113.1 | 11.365 | 1119.5 | 9353 | 21:47 | 28.7 | 1.79 m/s | 23.6 | 30.1 | 4.26 m/s | 17.5 |  | 1.79 | m/s |  | 4.26 | m/s | 21.78 | 0.0093292 | 24.4744 |  | -3.5 | 919.5 | 0.9195 | 26.6171 | 6.6737 | 5.3408 | 0.017572 | 64.5652 | 1.4241
2025-05-20 08:04 | 2610 | Remove | 2025-05-20 | 8:04 | ST | GS | - | 140.5 | g | 0 | 113.3 | 11.315 | 1114.5 | 9363 | 21:47 | 28.7 | 1.9 m/s | 23.2 | 30.1 | 4.39 m/s | 17.3 |  | 1.9 | m/s |  | 4.39 | m/s | 21.7883 | 0.0092875 | 24.4837 |  | 5 | 924.5 | 0.9245 | 26.4832 | 6.5606 | 5.2798 | 0.018336 | 64.5835 | 1.4315
2025-05-20 08:04 | 2611 | Keep | 2025-05-20 | 8:05 | US | GS | - | 138.5 | g | 0 | 113 | 11.309 | 1113.1 | 9372 | 21:48 | 28.7 | 1.86 m/s | 23.2 | 30.1 | 4.21 m/s | 17.3 |  | 1.86 | m/s |  | 4.21 | m/s | 21.7967 | 0.0092758 | 24.493 |  | -2 | 924.5 | 0.9245 | 26.4932 | 6.5606 | 5.2798 | 0.01795 | 64.6015 | 1.4311
2025-05-20 08:05 | 2612 | Remove | 2025-05-20 | 8:05 | ST | GS | - | 136 | g | 0 | 113.2 | 11.35 | 1119.2 | 9381 | 21:48 | 28.7 | 1.95 m/s | 23.3 | 30.1 | 4.26 m/s | 17.3 |  | 1.95 | m/s |  | 4.26 | m/s | 21.805 | 0.0093267 | 24.5023 |  | -2.5 | 924.5 | 0.9245 | 26.5033 | 6.5889 | 5.2798 | 0.018899 | 64.6204 | 1.4307
2025-05-20 08:06 | 2613 | Remove | 2025-05-20 | 8:06 | US | GS | - | 146 | g | 0 | 113.1 | 11.291 | 1111.2 | 9391 | 21:49 | 28.7 | 1.68 m/s | 23.4 | 30.1 | 4.3 m/s | 17.4 |  | 1.68 | m/s |  | 4.3 | m/s | 21.8133 | 0.00926 | 24.5116 |  | 10 | 934.5 | 0.9345 | 26.2296 | 6.6171 | 5.3103 | 0.016352 | 64.6367 | 1.4458
2025-05-20 08:06 | 2614 | Remove | 2025-05-20 | 8:06 | ST | GS | - | 145 | g | 0 | 113.1 | 11.31 | 1114.2 | 9400 | 21:49 | 28.7 | 1.66 m/s | 23.3 | 30.1 | 4.27 m/s | 17.4 |  | 1.66 | m/s |  | 4.27 | m/s | 21.8217 | 0.009285 | 24.5209 |  | -1 | 934.5 | 0.9345 | 26.2396 | 6.5889 | 5.3103 | 0.016089 | 64.6528 | 1.4454
2025-05-20 08:06 | 2615 | Remove | 2025-05-20 | 8:07 | ST | GS | - | 143 | g | 0 | 113.3 | 11.27 | 1108.6 | 9409 | 21:50 | 28.7 | 1.74 m/s | 23.5 | 30.1 | 4.29 m/s | 17.6 |  | 1.74 | m/s |  | 4.29 | m/s | 21.83 | 0.0092383 | 24.5301 |  | -2 | 934.5 | 0.9345 | 26.2494 | 6.6454 | 5.3714 | 0.017009 | 64.6698 | 1.445
2025-05-20 08:07 | 2616 | Remove | 2025-05-20 | 8:07 | ST | GS | - | 144 | g | 0 | 113.2 | 11.285 | 1110.9 | 9418 | 21:50 | 28.7 | 1.45 m/s | 22.9 | 30 | 4.26 m/s | 17.2 |  | 1.45 | m/s |  | 4.26 | m/s | 21.8383 | 0.0092575 | 24.5394 |  | 1 | 935.5 | 0.9355 | 26.2313 | 6.4757 | 5.2209 | 0.013812 | 64.6836 | 1.4463
2025-05-20 08:08 | 2617 | Remove | 2025-05-20 | 8:08 | US | GS | - | 146 | g | 0 | 113.2 | 11.295 | 1111.4 | 9428 | 21:51 | 28.7 | 1.87 m/s | 23.3 | 30 | 4.3 m/s | 17.5 |  | 1.87 | m/s |  | 4.3 | m/s | 21.8467 | 0.0092617 | 24.5486 |  | 2 | 937.5 | 0.9375 | 26.1852 | 6.5889 | 5.312 | 0.018124 | 64.7018 | 1.449
2025-05-20 08:08 | 2618 | Remove | 2025-05-20 | 8:08 | US | GS | - | 142 | g | 0 | 113.1 | 11.302 | 1112.6 | 9437 | 21:51 | 28.7 | 1.51 m/s | 22.9 | 30 | 4.26 m/s | 17.2 |  | 1.51 | m/s |  | 4.26 | m/s | 21.855 | 0.0092717 | 24.5579 |  | -4 | 937.5 | 0.9375 | 26.1951 | 6.4757 | 5.2209 | 0.014384 | 64.7162 | 1.4486
2025-05-20 08:08 | 2619 | Remove | 2025-05-20 | 8:08 | US | GS | - | 138 | g | 0 | 113.1 | 11.366 | 1120.1 | 9446 | 21:52 | 28.7 | 1.91 m/s | 22.8 | 30 | 4.29 m/s | 17.2 |  | 1.91 | m/s |  | 4.29 | m/s | 21.8633 | 0.0093342 | 24.5672 |  | -4 | 937.5 | 0.9375 | 26.205 | 6.4475 | 5.2209 | 0.018114 | 64.7343 | 1.4482
2025-05-20 08:09 | 2620 | Remove | 2025-05-20 | 8:09 | ST | GS | - | 141 | g | 0 | 113.2 | 11.351 | 1118.3 | 9456 | 21:52 | 28.7 | 1.87 m/s | 22.9 | 30 | 4.23 m/s | 17.3 |  | 1.87 | m/s |  | 4.23 | m/s | 21.8717 | 0.0093192 | 24.5765 |  | 3 | 940.5 | 0.9405 | 26.1314 | 6.4757 | 5.2513 | 0.017813 | 64.7521 | 1.4525
2025-05-20 08:10 | 2621 | Remove | 2025-05-20 | 8:10 | ST | GS | - | 141 | g | 0 | 113.2 | 11.334 | 1117.1 | 9465 | 21:53 | 28.7 | 1.86 m/s | 22.8 | 30.1 | 4.27 m/s | 17 |  | 1.86 | m/s |  | 4.27 | m/s | 21.88 | 0.0093092 | 24.5859 |  | 0 | 940.5 | 0.9405 | 26.1413 | 6.4475 | 5.1883 | 0.01764 | 64.7697 | 1.4521
2025-05-20 08:10 | 2622 | Remove | 2025-05-20 | 8:10 | ST | GS | - | 140 | g | 0 | 113 | 11.32 | 1114.9 | 9474 | 21:53 | 28.8 | 1.83 m/s | 22.8 | 30.1 | 4.32 m/s | 17.1 |  | 1.83 | m/s |  | 4.32 | m/s | 21.8883 | 0.0092908 | 24.5951 |  | -1 | 940.5 | 0.9405 | 26.1511 | 6.4829 | 5.2188 | 0.017451 | 64.7872 | 1.4517
2025-05-20 08:10 | 2623 | Remove | 2025-05-20 | 8:10 | US | GS | - | 138 | g | 0 | 113.2 | 11.343 | 1117.5 | 9484 | 21:54 | 28.8 | 1.98 m/s | 22.9 | 30.1 | 4.3 m/s | 17.2 |  | 1.98 | m/s |  | 4.3 | m/s | 21.8967 | 0.0093125 | 24.6045 |  | -2 | 940.5 | 0.9405 | 26.161 | 6.5113 | 5.2493 | 0.018964 | 64.8061 | 1.4513
2025-05-20 08:11 | 2624 | Remove | 2025-05-20 | 8:11 | ST | GS | - | 138.5 | g | 0 | 112.3 | 11.385 | 1122.1 | 9493 | 21:54 | 28.8 | 1.94 m/s | 22.9 | 30.1 | 4.38 m/s | 17.2 |  | 1.94 | m/s |  | 4.38 | m/s | 21.905 | 0.0093508 | 24.6138 |  | 0.5 | 941 | 0.941 | 26.1571 | 6.5113 | 5.2493 | 0.018581 | 64.8247 | 1.4516
2025-05-20 08:12 | 2625 | Remove | 2025-05-20 | 8:12 | ST | GS | - | 137 | g | 0 | 112.3 | 11.336 | 1115.9 | 9502 | 21:55 | 28.8 | 1.89 m/s | 23.1 | 30.1 | 4.29 m/s | 17.3 |  | 1.89 | m/s |  | 4.29 | m/s | 21.9133 | 0.0092992 | 24.6231 |  | -1.5 | 941 | 0.941 | 26.167 | 6.5682 | 5.2798 | 0.01826 | 64.843 | 1.4512
2025-05-20 08:12 | 2626 | Remove | 2025-05-20 | 8:12 | ST | GS | - | 135.5 | g | 0 | 112.3 | 11.37 | 1120.1 | 9512 | 21:55 | 28.8 | 1.87 m/s | 22.8 | 30.1 | 4.49 m/s | 17.1 |  | 1.87 | m/s |  | 4.49 | m/s | 21.9219 | 0.0093342 | 24.6324 |  | -1.5 | 941 | 0.941 | 26.1769 | 6.4829 | 5.2188 | 0.017832 | 64.8608 | 1.4508
2025-05-20 08:13 | 2627 | Remove | 2025-05-20 | 8:13 | ST | GS | - | 138 | g | 0 | 112.2 | 11.352 | 1117.5 | 9521 | 21:56 | 28.8 | 1.83 m/s | 23 | 30.2 | 4.24 m/s | 17.1 |  | 1.83 | m/s |  | 4.24 | m/s | 21.9303 | 0.0093125 | 24.6418 |  | 2.5 | 943.5 | 0.9435 | 26.1174 | 6.5397 | 5.2471 | 0.017604 | 64.8784 | 1.4543
2025-05-20 08:13 | 2628 | Remove | 2025-05-20 | 8:13 | ST | GS | - | 139.5 | g | 0 | 112.4 | 11.367 | 1119.4 | 9531 | 21:56 | 28.8 | 1.89 m/s | 23 | 30.2 | 4.47 m/s | 17.1 |  | 1.89 | m/s |  | 4.47 | m/s | 21.9386 | 0.0093283 | 24.6511 |  | 1.5 | 945 | 0.945 | 26.0858 | 6.5397 | 5.2471 | 0.018181 | 64.8966 | 1.4562
2025-05-20 08:14 | 2629 | Remove | 2025-05-20 | 8:14 | ST | GS | - | 142.5 | g | 0 | 112.3 | 11.336 | 1116.3 | 9540 | 21:57 | 28.8 | 1.79 m/s | 23 | 30.2 | 4.23 m/s | 16.9 |  | 1.79 | m/s |  | 4.23 | m/s | 21.9469 | 0.0093025 | 24.6604 |  | 3 | 948 | 0.948 | 26.0131 | 6.5397 | 5.1857 | 0.017219 | 64.9138 | 1.4604
2025-05-20 08:14 | 2630 | Remove | 2025-05-20 | 8:14 | US | GS | - | 136 | g | 0 | 112.5 | 11.359 | 1119.3 | 9549 | 21:57 | 28.8 | 1.97 m/s | 23.1 | 30.3 | 4.66 m/s | 16.9 |  | 1.97 | m/s |  | 4.66 | m/s | 21.9553 | 0.0093275 | 24.6697 |  | -6.5 | 948 | 0.948 | 26.0229 | 6.5682 | 5.2139 | 0.019033 | 64.9328 | 1.46
2025-05-20 08:15 | 2631 | Remove | 2025-05-20 | 8:15 | ST | GS | - | 141.5 | g | 0 | 112.3 | 11.371 | 1120.3 | 9559 | 21:58 | 28.8 | 1.94 m/s | 23.2 | 30.3 | 4.52 m/s | 17.1 |  | 1.94 | m/s |  | 4.52 | m/s | 21.9636 | 0.0093358 | 24.6791 |  | 5.5 | 953.5 | 0.9535 | 25.8826 | 6.5966 | 5.2756 | 0.018825 | 64.9517 | 1.468
2025-05-20 08:15 | 2632 | Remove | 2025-05-20 | 8:15 | US | GS | - | 143 | g | 0 | 112.4 | 11.337 | 1115.3 | 9568 | 21:58 | 28.8 | 1.83 m/s | 22.8 | 30.4 | 4.16 m/s | 16.6 |  | 1.83 | m/s |  | 4.16 | m/s | 21.9719 | 0.0092942 | 24.6883 |  | 1.5 | 955 | 0.955 | 25.8517 | 6.4829 | 5.1491 | 0.017451 | 64.9691 | 1.4699
2025-05-20 08:16 | 2633 | Remove | 2025-05-20 | 8:16 | ST | GS | - | 139 | g | 0 | 112.4 | 11.33 | 1115 | 9577 | 21:59 | 28.8 | 2.01 m/s | 22.7 | 30.4 | 4.18 m/s | 16.5 |  | 2.01 | m/s |  | 4.18 | m/s | 21.9803 | 0.0092917 | 24.6976 |  | -4 | 955 | 0.955 | 25.8614 | 6.4544 | 5.1181 | 0.019083 | 64.9882 | 1.4695
2025-05-20 08:16 | 2634 | Remove | 2025-05-20 | 8:16 | US | GS | - | 138 | g | 0 | 112.3 | 11.359 | 1118.1 | 9586 | 21:59 | 28.8 | 1.81 m/s | 22.7 | 30.4 | 4.26 m/s | 16.6 |  | 1.81 | m/s |  | 4.26 | m/s | 21.9886 | 0.0093175 | 24.707 |  | -1 | 955 | 0.955 | 25.8712 | 6.4544 | 5.1491 | 0.017185 | 65.0054 | 1.4691
2025-05-20 08:17 | 2635 | Remove | 2025-05-20 | 8:17 | ST | GS | - | 140.5 | g | 0 | 112.4 | 11.361 | 1118.6 | 9596 | 22:00 | 28.8 | 2.02 m/s | 23 | 30.5 | 4.46 m/s | 16.7 |  | 2.02 | m/s |  | 4.46 | m/s | 21.9969 | 0.0093217 | 24.7163 |  | 2.5 | 957.5 | 0.9575 | 25.8133 | 6.5397 | 5.2082 | 0.019432 | 65.0248 | 1.4725
2025-05-20 08:17 | 2636 | Remove | 2025-05-20 | 8:17 | ST | GS | - | 138 | g | 0 | 112.3 | 11.421 | 1127 | 9605 | 22:00 | 28.8 | 2.06 m/s | 23.5 | 30.5 | 4.87 m/s | 16.9 |  | 2.06 | m/s |  | 4.87 | m/s | 22.0053 | 0.0093917 | 24.7257 |  | -2.5 | 957.5 | 0.9575 | 25.8232 | 6.6819 | 5.2706 | 0.020247 | 65.0451 | 1.4721
2025-05-20 08:18 | 2637 | Remove | 2025-05-20 | 8:18 | ST | GS | - | 137.5 | g | 0 | 112.3 | 11.352 | 1118.1 | 9615 | 22:01 | 28.8 | 1.77 m/s | 23.5 | 30.5 | 4.4 m/s | 16.8 |  | 1.77 | m/s |  | 4.4 | m/s | 22.0136 | 0.0093175 | 24.735 |  | -0.5 | 957.5 | 0.9575 | 25.8329 | 6.6819 | 5.2394 | 0.017397 | 65.0625 | 1.4717
2025-05-20 08:18 | 2638 | Remove | 2025-05-20 | 8:18 | US | GS | - | 140 | g | 0 | 112.4 | 11.353 | 1118.3 | 9624 | 22:01 | 28.8 | 1.91 m/s | 23.1 | 30.6 | 4.24 m/s | 16.5 |  | 1.91 | m/s |  | 4.24 | m/s | 22.0219 | 0.0093192 | 24.7443 |  | 2.5 | 960 | 0.96 | 25.7753 | 6.5682 | 5.1737 | 0.018454 | 65.0809 | 1.4751
2025-05-20 08:19 | 2639 | Remove | 2025-05-20 | 8:19 | ST | GS | - | 138.5 | g | 0 | 112.2 | 11.421 | 1125.8 | 9633 | 22:02 | 28.8 | 1.95 m/s | 22.6 | 30.6 | 4.24 m/s | 16.1 |  | 1.95 | m/s |  | 4.24 | m/s | 22.0303 | 0.0093817 | 24.7537 |  | -1.5 | 960 | 0.96 | 25.7851 | 6.426 | 5.0482 | 0.018432 | 65.0994 | 1.4747
2025-05-20 08:19 | 2640 | Remove | 2025-05-20 | 8:19 | ST | GS | - | 136.5 | g | 0 | 112.2 | 11.411 | 1125.1 | 9643 | 22:02 | 28.8 | 1.98 m/s | 22.6 | 30.6 | 4.61 m/s | 16.1 |  | 1.98 | m/s |  | 4.61 | m/s | 22.0386 | 0.0093758 | 24.7631 |  | -2 | 960 | 0.96 | 25.7949 | 6.426 | 5.0482 | 0.018716 | 65.1181 | 1.4742
2025-05-20 08:20 | 2641 | Keep | 2025-05-20 | 8:20 | ST | GS | - | 136.5 | g | 0 | 112.3 | 11.333 | 1115.6 | 9652 | 22:03 | 28.8 | 1.86 m/s | 23.1 | 30.6 | 4.52 m/s | 16.6 |  | 1.86 | m/s |  | 4.52 | m/s | 22.0469 | 0.0092967 | 24.7724 |  | 0 | 960 | 0.96 | 25.8045 | 6.5682 | 5.205 | 0.01797 | 65.136 | 1.4738
2025-05-20 08:20 | 2642 | Remove | 2025-05-20 | 8:20 | ST | GS | - | 142 | g | 0 | 112.3 | 11.404 | 1123.3 | 9662 | 22:03 | 28.8 | 1.9 m/s | 22.8 | 30.7 | 4.4 m/s | 16.2 |  | 1.9 | m/s |  | 4.4 | m/s | 22.0553 | 0.0093608 | 24.7817 |  | 5.5 | 965.5 | 0.9655 | 25.6672 | 6.4829 | 5.1071 | 0.018119 | 65.1542 | 1.4819
2025-05-20 08:21 | 2643 | Remove | 2025-05-20 | 8:21 | ST | GS | - | 138 | g | 0 | 112.3 | 11.421 | 1126.8 | 9671 | 22:04 | 28.8 | 1.86 m/s | 22.6 | 30.7 | 4.24 m/s | 16.1 |  | 1.86 | m/s |  | 4.24 | m/s | 22.0639 | 0.00939 | 24.7911 |  | -4 | 965.5 | 0.9655 | 25.677 | 6.426 | 5.0756 | 0.017581 | 65.1717 | 1.4815
2025-05-20 08:21 | 2644 | Remove | 2025-05-20 | 8:21 | ST | GS | - | 139.5 | g | 0 | 112.3 | 11.396 | 1123.3 | 9680 | 22:04 | 28.8 | 1.73 m/s | 22.9 | 30.7 | 4.2 m/s | 16.3 |  | 1.73 | m/s |  | 4.2 | m/s | 22.0722 | 0.0093608 | 24.8005 |  | 1.5 | 967 | 0.967 | 25.6468 | 6.5113 | 5.1386 | 0.01657 | 65.1883 | 1.4834
2025-05-20 08:22 | 2645 | Remove | 2025-05-20 | 8:22 | US | GS | - | 141.5 | g | 0 | 112.2 | 11.452 | 1129.8 | 9690 | 22:05 | 28.8 | 1.77 m/s | 22.5 | 30.7 | 4.3 m/s | 15.9 |  | 1.77 | m/s |  | 4.3 | m/s | 22.0806 | 0.009415 | 24.8099 |  | 2 | 969 | 0.969 | 25.6036 | 6.3976 | 5.0125 | 0.016657 | 65.205 | 1.4861
2025-05-20 08:22 | 2646 | Remove | 2025-05-20 | 8:22 | ST | GS | - | 144.5 | g | 0 | 112.3 | 11.412 | 1125.8 | 9699 | 22:05 | 28.9 | 1.85 m/s | 22.6 | 30.7 | 4.61 m/s | 16 |  | 1.85 | m/s |  | 4.61 | m/s | 22.0889 | 0.0093817 | 24.8193 |  | 3 | 972 | 0.972 | 25.5342 | 6.4612 | 5.044 | 0.017583 | 65.2226 | 1.4903
2025-05-20 08:23 | 2647 | Remove | 2025-05-20 | 8:23 | US | GS | - | 142.5 | g | 0 | 112.4 | 11.375 | 1120.2 | 9709 | 22:06 | 28.9 | 1.74 m/s | 22.5 | 30.7 | 4.24 m/s | 15.9 |  | 1.74 | m/s |  | 4.24 | m/s | 22.0972 | 0.009335 | 24.8286 |  | -2 | 972 | 0.972 | 25.5438 | 6.4326 | 5.0125 | 0.016464 | 65.239 | 1.4899
2025-05-20 08:23 | 2648 | Remove | 2025-05-20 | 8:23 | ST | GS | - | 144.5 | g | 0 | 112.2 | 11.428 | 1126.6 | 9718 | 22:06 | 28.9 | 1.67 m/s | 22.3 | 30.7 | 4.21 m/s | 15.8 |  | 1.67 | m/s |  | 4.21 | m/s | 22.1056 | 0.0093883 | 24.838 |  | 2 | 974 | 0.974 | 25.501 | 6.3755 | 4.981 | 0.015661 | 65.2547 | 1.4926
2025-05-20 08:24 | 2649 | Remove | 2025-05-20 | 8:24 | US | GS | - | 136.5 | g | 0 | 112.4 | 11.402 | 1124.3 | 9727 | 22:07 | 28.9 | 1.9 m/s | 22.6 | 30.7 | 4.24 m/s | 16 |  | 1.9 | m/s |  | 4.24 | m/s | 22.1139 | 0.0093692 | 24.8474 |  | -8 | 974 | 0.974 | 25.5106 | 6.4612 | 5.044 | 0.018058 | 65.2727 | 1.4922
2025-05-20 08:24 | 2650 | Remove | 2025-05-20 | 8:24 | US | GS | - | 145.5 | g | 0 | 112.2 | 11.426 | 1126.1 | 9737 | 22:07 | 28.9 | 1.82 m/s | 22.3 | 30.7 | 4.21 m/s | 15.9 |  | 1.82 | m/s |  | 4.21 | m/s | 22.1222 | 0.0093842 | 24.8567 |  | 9 | 983 | 0.983 | 25.2866 | 6.3755 | 5.0125 | 0.017068 | 65.2898 | 1.5056
2025-05-20 08:25 | 2651 | Remove | 2025-05-20 | 8:25 | US | GS | - | 148 | g | 0 | 112.3 | 11.352 | 1118.1 | 9746 | 22:08 | 28.9 | 1.79 m/s | 22.2 | 30.7 | 4.41 m/s | 15.7 |  | 1.79 | m/s |  | 4.41 | m/s | 22.1306 | 0.0093175 | 24.8661 |  | 2.5 | 985.5 | 0.9855 | 25.2319 | 6.3469 | 4.9495 | 0.016711 | 65.3065 | 1.509
2025-05-20 08:25 | 2652 | Remove | 2025-05-20 | 8:25 | US | GS | - | 134 | g | 0 | 112.2 | 11.369 | 1119.1 | 9756 | 22:08 | 28.9 | 1.74 m/s | 22.1 | 30.7 | 4.27 m/s | 15.6 |  | 1.74 | m/s |  | 4.27 | m/s | 22.1389 | 0.0093258 | 24.8754 |  | -14 | 985.5 | 0.9855 | 25.2414 | 6.3183 | 4.9179 | 0.016172 | 65.3227 | 1.5087
2025-05-20 08:26 | 2653 | Remove | 2025-05-20 | 8:26 | ST | GS | - | 139 | g | 0 | 112.1 | 11.464 | 1131.3 | 9765 | 22:09 | 28.8 | 1.85 m/s | 22.1 | 30.7 | 4.26 m/s | 15.8 |  | 1.85 | m/s |  | 4.26 | m/s | 22.1472 | 0.0094275 | 24.8848 |  | 5 | 990.5 | 0.9905 | 25.1235 | 6.2838 | 4.981 | 0.0171 | 65.3398 | 1.5159
2025-05-20 08:26 | 2654 | Remove | 2025-05-20 | 8:26 | ST | GS | - | 138 | g | 0 | 112.1 | 11.487 | 1133.1 | 9774 | 22:09 | 28.9 | 2.0 m/s | 22.5 | 30.7 | 4.88 m/s | 15.9 |  | 2 | m/s |  | 4.88 | m/s | 22.1556 | 0.0094425 | 24.8943 |  | -1 | 990.5 | 0.9905 | 25.133 | 6.4326 | 5.0125 | 0.018924 | 65.3587 | 1.5155
2025-05-20 08:27 | 2655 | Remove | 2025-05-20 | 8:27 | ST | GS | - | 138.5 | g | 0 | 112.2 | 11.48 | 1132.3 | 9784 | 22:10 | 28.9 | 1.89 m/s | 22.7 | 30.8 | 4.23 m/s | 15.9 |  | 1.89 | m/s |  | 4.23 | m/s | 22.1639 | 0.0094358 | 24.9037 |  | 0.5 | 991 | 0.991 | 25.1299 | 6.4898 | 5.0396 | 0.018043 | 65.3768 | 1.5158
2025-05-20 08:27 | 2656 | Remove | 2025-05-20 | 8:27 | ST | GS | - | 137.5 | g | 0 | 112.1 | 11.494 | 1134.2 | 9793 | 22:10 | 28.9 | 1.91 m/s | 22.5 | 30.8 | 4.44 m/s | 15.8 |  | 1.91 | m/s |  | 4.44 | m/s | 22.1722 | 0.0094517 | 24.9131 |  | -1 | 991 | 0.991 | 25.1394 | 6.4326 | 5.0079 | 0.018073 | 65.3948 | 1.5154
2025-05-20 08:28 | 2657 | Remove | 2025-05-20 | 8:28 | US | GS | - | 140.5 | g | 0 | 112.3 | 11.438 | 1128.3 | 9803 | 22:11 | 28.9 | 1.91 m/s | 22.3 | 30.8 | 4.61 m/s | 15.6 |  | 1.91 | m/s |  | 4.61 | m/s | 22.1806 | 0.0094025 | 24.9225 |  | 3 | 994 | 0.994 | 25.073 | 6.3755 | 4.9445 | 0.017912 | 65.4127 | 1.5196
2025-05-20 08:28 | 2658 | Remove | 2025-05-20 | 8:28 | ST | GS | - | 145 | g | 0 | 112.2 | 11.464 | 1130.8 | 9812 | 22:11 | 28.9 | 1.89 m/s | 22 | 30.8 | 4.23 m/s | 15.6 |  | 1.89 | m/s |  | 4.23 | m/s | 22.1889 | 0.0094233 | 24.932 |  | 4.5 | 998.5 | 0.9985 | 24.9694 | 6.2897 | 4.9445 | 0.017486 | 65.4302 | 1.5261
2025-05-20 08:29 | 2659 | Remove | 2025-05-20 | 8:29 | US | GS | - | 135 | g | 0 | 112.2 | 11.52 | 1137.6 | 9822 | 22:12 | 28.9 | 1.91 m/s | 22.5 | 30.9 | 4.35 m/s | 15.8 |  | 1.91 | m/s |  | 4.35 | m/s | 22.1972 | 0.00948 | 24.9415 |  | -10 | 998.5 | 0.9985 | 24.9789 | 6.4326 | 5.035 | 0.018073 | 65.4483 | 1.5256
2025-05-20 08:29 | 2660 | Remove | 2025-05-20 | 8:29 | ST | GS | - | 138 | g | 0 | 112.1 | 11.487 | 1133.9 | 9831 | 22:12 | 28.9 | 1.97 m/s | 22.5 | 30.9 | 4.29 m/s | 15.6 |  | 1.97 | m/s |  | 4.29 | m/s | 22.2058 | 0.0094492 | 24.9509 |  | 3 | 1001.5 | 1.0015 | 24.9135 | 6.4326 | 4.9712 | 0.018641 | 65.4669 | 1.5298
2025-05-20 08:30 | 2661 | Remove | 2025-05-20 | 8:30 | ST | GS | - | 144.5 | g | 0 | 112 | 11.483 | 1133.5 | 9841 | 22:13 | 28.9 | 1.74 m/s | 22.2 | 30.9 | 4.24 m/s | 15.5 |  | 1.74 | m/s |  | 4.24 | m/s | 22.2142 | 0.0094458 | 24.9603 |  | 6.5 | 1008 | 1.008 | 24.7622 | 6.3469 | 4.9394 | 0.016245 | 65.4832 | 1.5393
2025-05-20 08:30 | 2662 | Remove | 2025-05-20 | 8:30 | US | GS | - | 139.5 | g | 0 | 111.9 | 11.439 | 1127.2 | 9850 | 22:13 | 28.9 | 1.6 m/s | 22.1 | 30.9 | 4.18 m/s | 15.6 |  | 1.6 | m/s |  | 4.18 | m/s | 22.2225 | 0.0093933 | 24.9697 |  | -5 | 1008 | 1.008 | 24.7716 | 6.3183 | 4.9712 | 0.01487 | 65.4981 | 1.539
2025-05-20 08:31 | 2663 | Remove | 2025-05-20 | 8:31 | US | GS | - | 143 | g | 0 | 112.1 | 11.471 | 1132.1 | 9860 | 22:14 | 28.9 | 1.79 m/s | 22.5 | 30.9 | 4.26 m/s | 15.8 |  | 1.79 | m/s |  | 4.26 | m/s | 22.2308 | 0.0094342 | 24.9792 |  | 3.5 | 1011.5 | 1.0115 | 24.6952 | 6.4326 | 5.035 | 0.016937 | 65.515 | 1.5439
2025-05-20 08:31 | 2664 | Remove | 2025-05-20 | 8:31 | US | GS | - | 145.5 | g | 0 | 112.1 | 11.449 | 1129.7 | 9869 | 22:14 | 28.9 | 1.73 m/s | 22.8 | 30.9 | 4.24 m/s | 15.9 |  | 1.73 | m/s |  | 4.24 | m/s | 22.2392 | 0.0094142 | 24.9886 |  | 2.5 | 1014 | 1.014 | 24.6436 | 6.5184 | 5.0668 | 0.016588 | 65.5316 | 1.5473
2025-05-20 08:32 | 2665 | Remove | 2025-05-20 | 8:32 | US | GS | - | 136.5 | g | 0 | 112.1 | 11.511 | 1137 | 9878 | 22:15 | 28.9 | 2.12 m/s | 22.7 | 30.9 | 4.49 m/s | 16 |  | 2.12 | m/s |  | 4.49 | m/s | 22.2475 | 0.009475 | 24.9981 |  | -9 | 1014 | 1.014 | 24.6529 | 6.4898 | 5.0987 | 0.020238 | 65.5518 | 1.5469
2025-05-20 08:32 | 2666 | Remove | 2025-05-20 | 8:32 | ST | GS | - | 143 | g | 0 | 111.9 | 11.523 | 1137.8 | 9888 | 22:15 | 28.9 | 1.79 m/s | 22.6 | 30.9 | 4.15 m/s | 15.8 |  | 1.79 | m/s |  | 4.15 | m/s | 22.2558 | 0.0094817 | 25.0075 |  | 6.5 | 1020.5 | 1.0205 | 24.5052 | 6.4612 | 5.035 | 0.017013 | 65.5688 | 1.5564
2025-05-20 08:33 | 2667 | Remove | 2025-05-20 | 8:33 | US | GS | - | 141.5 | g | 0 | 112.2 | 11.52 | 1138.8 | 9897 | 22:16 | 29 | 1.9 m/s | 22.3 | 30.9 | 4.26 m/s | 15.5 |  | 1.9 | m/s |  | 4.26 | m/s | 22.2642 | 0.00949 | 25.017 |  | -1.5 | 1020.5 | 1.0205 | 24.5145 | 6.4104 | 4.9394 | 0.017916 | 65.5867 | 1.556
2025-05-20 08:33 | 2668 | Remove | 2025-05-20 | 8:33 | ST | GS | - | 144 | g | 0 | 112 | 11.552 | 1141.6 | 9907 | 22:16 | 29 | 1.82 m/s | 22.2 | 30.9 | 4.53 m/s | 15.6 |  | 1.82 | m/s |  | 4.53 | m/s | 22.2725 | 0.0095133 | 25.0265 |  | 2.5 | 1023 | 1.023 | 24.4639 | 6.3817 | 4.9712 | 0.017085 | 65.6038 | 1.5594
2025-05-20 08:34 | 2669 | Remove | 2025-05-20 | 8:34 | US | GS | - | 137 | g | 0 | 112.3 | 11.487 | 1134.5 | 9917 | 22:17 | 29 | 1.89 m/s | 22.3 | 30.9 | 4.21 m/s | 15.6 |  | 1.89 | m/s |  | 4.21 | m/s | 22.2808 | 0.0094542 | 25.036 |  | -7 | 1023 | 1.023 | 24.4731 | 6.4104 | 4.9712 | 0.017822 | 65.6217 | 1.5589
2025-05-20 08:34 | 2670 | Remove | 2025-05-20 | 8:34 | US | GS | - | 157 | g | 0 | 112.4 | 11.406 | 1124.9 | 9926 | 22:17 | 29 | 1.49 m/s | 22.5 | 30.9 | 4.3 m/s | 15.9 |  | 1.49 | m/s |  | 4.3 | m/s | 22.2892 | 0.0093742 | 25.0454 |  | 20 | 1043 | 1.043 | 24.0128 | 6.4679 | 5.0668 | 0.014176 | 65.6358 | 1.5891
2025-05-20 08:35 | 2671 | Keep | 2025-05-20 | 8:35 | ST | GS | - | 147.5 | g | 0 | 112.4 | 11.418 | 1125.8 | 9935 | 22:18 | 29 | 1.68 m/s | 22.1 | 30.9 | 4.26 m/s | 15.6 |  | 1.68 | m/s |  | 4.26 | m/s | 22.2975 | 0.0093817 | 25.0548 |  | -9.5 | 1043 | 1.043 | 24.0218 | 6.3529 | 4.9712 | 0.015699 | 65.6515 | 1.5887
2025-05-20 08:35 | 2672 | Remove | 2025-05-20 | 8:35 | ST | GS | - | 143 | g | 0 | 112.4 | 11.464 | 1131.8 | 9945 | 22:18 | 29 | 1.74 m/s | 22.6 | 30.9 | 4.35 m/s | 16.5 |  | 1.74 | m/s |  | 4.35 | m/s | 22.3058 | 0.0094317 | 25.0642 |  | -4.5 | 1043 | 1.043 | 24.0309 | 6.4966 | 5.258 | 0.016628 | 65.6682 | 1.5883
2025-05-20 08:36 | 2673 | Remove | 2025-05-20 | 8:36 | US | GS | - | 143.5 | g | 0 | 112.5 | 11.461 | 1132.2 | 9954 | 22:19 | 29 | 1.59 m/s | 23 | 30.9 | 4.23 m/s | 16.4 |  | 1.59 | m/s |  | 4.23 | m/s | 22.3142 | 0.009435 | 25.0736 |  | 0.5 | 1043.5 | 1.0435 | 24.0284 | 6.6116 | 5.2262 | 0.015464 | 65.6836 | 1.5887
2025-05-20 08:36 | 2674 | Remove | 2025-05-20 | 8:36 | ST | GS | - | 143.5 | g | 0 | 112.4 | 11.503 | 1136.4 | 9964 | 22:19 | 28.9 | 1.55 m/s | 24.3 | 30.9 | 4.29 m/s | 16.6 |  | 1.55 | m/s |  | 4.29 | m/s | 22.3225 | 0.00947 | 25.0831 |  | 0 | 1043.5 | 1.0435 | 24.0375 | 6.9473 | 5.2899 | 0.01584 | 65.6995 | 1.5883
2025-05-20 08:37 | 2675 | Remove | 2025-05-20 | 8:37 | US | GS | - | 161 | g | 0 | 112.4 | 11.415 | 1126.2 | 9973 | 22:20 | 28.9 | 1.53 m/s | 22.9 | 30.9 | 4.32 m/s | 15.8 |  | 1.53 | m/s |  | 4.32 | m/s | 22.3308 | 0.009385 | 25.0925 |  | 17.5 | 1061 | 1.061 | 23.6498 | 6.547 | 5.035 | 0.014735 | 65.7142 | 1.6146
2025-05-20 08:37 | 2676 | Remove | 2025-05-20 | 8:37 | US | GS | - | 157.5 | g | 0 | 112.4 | 11.461 | 1131.6 | 9983 | 22:20 | 28.9 | 1.68 m/s | 22.5 | 30.9 | 4.24 m/s | 15.7 |  | 1.68 | m/s |  | 4.24 | m/s | 22.3392 | 0.00943 | 25.1019 |  | -3.5 | 1061 | 1.061 | 23.6587 | 6.4326 | 5.0031 | 0.015896 | 65.7301 | 1.6142
2025-05-20 08:38 | 2677 | Remove | 2025-05-20 | 8:38 | ST | GS | - | 148.5 | g | 0 | 112.5 | 11.467 | 1131.7 | 9992 | 22:21 | 28.9 | 1.64 m/s | 22.7 | 30.8 | 4.38 m/s | 15.8 |  | 1.64 | m/s |  | 4.38 | m/s | 22.3475 | 0.0094308 | 25.1113 |  | -9 | 1061 | 1.061 | 23.6676 | 6.4898 | 5.0079 | 0.015656 | 65.7457 | 1.6138
2025-05-20 08:38 | 2678 | Remove | 2025-05-20 | 8:38 | ST | GS | - | 151 | g | 0 | 112.4 | 11.492 | 1135.5 | 10002 | 22:21 | 28.9 | 1.71 m/s | 22.5 | 30.9 | 4.33 m/s | 15.7 |  | 1.71 | m/s |  | 4.33 | m/s | 22.3561 | 0.0094625 | 25.1208 |  | 2.5 | 1063.5 | 1.0635 | 23.6209 | 6.4326 | 5.0031 | 0.01618 | 65.7619 | 1.6172
2025-05-20 08:39 | 2679 | Remove | 2025-05-20 | 8:39 | US | GS | - | 144 | g | 0 | 112.2 | 11.5 | 1136 | 10011 | 22:22 | 29 | 1.68 m/s | 22.6 | 30.8 | 4.21 m/s | 15.8 |  | 1.68 | m/s |  | 4.21 | m/s | 22.3644 | 0.0094667 | 25.1303 |  | -7 | 1063.5 | 1.0635 | 23.6298 | 6.4966 | 5.0079 | 0.016055 | 65.778 | 1.6168
2025-05-20 08:39 | 2680 | Remove | 2025-05-20 | 8:39 | US | GS | - | 142 | g | 0 | 112.3 | 11.481 | 1133 | 10021 | 22:22 | 29 | 1.68 m/s | 23.3 | 30.9 | 4.43 m/s | 16 |  | 1.68 | m/s |  | 4.43 | m/s | 22.3728 | 0.0094417 | 25.1397 |  | -2 | 1063.5 | 1.0635 | 23.6387 | 6.6979 | 5.0987 | 0.016552 | 65.7945 | 1.6164
2025-05-20 08:40 | 2681 | Remove | 2025-05-20 | 8:40 | US | GS | - | 146.5 | g | 0 | 112.3 | 11.497 | 1135.9 | 10030 | 22:23 | 29 | 1.71 m/s | 23.1 | 30.9 | 4.29 m/s | 16.1 |  | 1.71 | m/s |  | 4.29 | m/s | 22.3811 | 0.0094658 | 25.1492 |  | 4.5 | 1068 | 1.068 | 23.5479 | 6.6404 | 5.1306 | 0.016703 | 65.8112 | 1.6228
2025-05-20 08:40 | 2682 | Remove | 2025-05-20 | 8:40 | US | GS | - | 147.5 | g | 0 | 112.4 | 11.502 | 1136.6 | 10040 | 22:23 | 29 | 1.91 m/s | 22.8 | 30.9 | 4.29 m/s | 16.6 |  | 1.91 | m/s |  | 4.29 | m/s | 22.3894 | 0.0094717 | 25.1586 |  | 1 | 1069 | 1.069 | 23.5347 | 6.5541 | 5.2899 | 0.018414 | 65.8296 | 1.6239
2025-05-20 08:41 | 2683 | Remove | 2025-05-20 | 8:41 | ST | GS | - | 149.5 | g | 0 | 112.4 | 11.483 | 1134.4 | 10049 | 22:24 | 29 | 1.94 m/s | 23 | 30.9 | 4.82 m/s | 16.1 |  | 1.94 | m/s |  | 4.82 | m/s | 22.3978 | 0.0094533 | 25.1681 |  | 2 | 1071 | 1.071 | 23.4996 | 6.6116 | 5.1306 | 0.018867 | 65.8485 | 1.6265
2025-05-20 08:41 | 2684 | Remove | 2025-05-20 | 8:41 | ST | GS | - | 147 | g | 0 | 112.4 | 11.459 | 1131.6 | 10059 | 22:24 | 29 | 1.62 m/s | 22.5 | 30.9 | 4.24 m/s | 15.8 |  | 1.62 | m/s |  | 4.24 | m/s | 22.4061 | 0.00943 | 25.1775 |  | -2.5 | 1071 | 1.071 | 23.5084 | 6.4679 | 5.035 | 0.015413 | 65.8639 | 1.6261
2025-05-20 08:42 | 2685 | Remove | 2025-05-20 | 8:42 | US | GS | - | 147 | g | 0 | 112.4 | 11.493 | 1135 | 10068 | 22:25 | 29 | 1.68 m/s | 22.6 | 30.9 | 4.32 m/s | 15.8 |  | 1.68 | m/s |  | 4.32 | m/s | 22.4144 | 0.0094583 | 25.187 |  | 0 | 1071 | 1.071 | 23.5173 | 6.4966 | 5.035 | 0.016055 | 65.88 | 1.6257
2025-05-20 08:42 | 2686 | Remove | 2025-05-20 | 8:42 | ST | GS | - | 146.5 | g | 0 | 112.5 | 11.508 | 1137.3 | 10078 | 22:25 | 29 | 1.87 m/s | 22.7 | 30.9 | 4.29 m/s | 15.9 |  | 1.87 | m/s |  | 4.29 | m/s | 22.4228 | 0.0094775 | 25.1965 |  | -0.5 | 1071 | 1.071 | 23.5261 | 6.5254 | 5.0668 | 0.017949 | 65.8979 | 1.6252
2025-05-20 08:43 | 2687 | Remove | 2025-05-20 | 8:43 | US | GS | - | 148.5 | g | 0 | 112.4 | 11.508 | 1137.1 | 10087 | 22:26 | 29 | 1.53 m/s | 22.5 | 30.9 | 4.23 m/s | 15.8 |  | 1.53 | m/s |  | 4.23 | m/s | 22.4311 | 0.0094758 | 25.2059 |  | 2 | 1073 | 1.073 | 23.4911 | 6.4679 | 5.035 | 0.014556 | 65.9125 | 1.6279
2025-05-20 08:43 | 2688 | Remove | 2025-05-20 | 8:43 | US | GS | - | 143 | g | 0 | 112.5 | 11.462 | 1131.6 | 10097 | 22:26 | 29 | 1.81 m/s | 22.5 | 30.9 | 4.3 m/s | 15.7 |  | 1.81 | m/s |  | 4.3 | m/s | 22.4394 | 0.00943 | 25.2154 |  | -5.5 | 1073 | 1.073 | 23.4999 | 6.4679 | 5.0031 | 0.01722 | 65.9297 | 1.6275
2025-05-20 08:44 | 2689 | Remove | 2025-05-20 | 8:44 | US | GS | - | 155.5 | g | 0 | 112.5 | 11.494 | 1135.3 | 10106 | 22:27 | 29 | 1.83 m/s | 22.6 | 30.9 | 4.32 m/s | 16.2 |  | 1.83 | m/s |  | 4.32 | m/s | 22.4478 | 0.0094608 | 25.2248 |  | 12.5 | 1085.5 | 1.0855 | 23.238 | 6.4966 | 5.1624 | 0.017488 | 65.9472 | 1.646
2025-05-20 08:44 | 2690 | Remove | 2025-05-20 | 8:44 | ST | GS | - | 149.5 | g | 0 | 112.5 | 11.485 | 1134.4 | 10115 | 22:27 | 29 | 1.6 m/s | 22.6 | 30.9 | 4.23 m/s | 15.9 |  | 1.6 | m/s |  | 4.23 | m/s | 22.4561 | 0.0094533 | 25.2343 |  | -6 | 1085.5 | 1.0855 | 23.2467 | 6.4966 | 5.0668 | 0.01529 | 65.9625 | 1.6456
2025-05-20 08:45 | 2691 | Remove | 2025-05-20 | 8:45 | US | GS | - | 145.5 | g | 0 | 112.3 | 11.492 | 1135 | 10125 | 22:28 | 29 | 1.62 m/s | 22.6 | 30.9 | 4.32 m/s | 15.8 |  | 1.62 | m/s |  | 4.32 | m/s | 22.4644 | 0.0094583 | 25.2437 |  | -4 | 1085.5 | 1.0855 | 23.2554 | 6.4966 | 5.035 | 0.015481 | 65.978 | 1.6452
2025-05-20 08:45 | 2692 | Remove | 2025-05-20 | 8:45 | ST | GS | - | 145.5 | g | 0 | 112.4 | 11.538 | 1140.2 | 10135 | 22:28 | 29 | 2.08 m/s | 22.5 | 30.9 | 4.46 m/s | 15.7 |  | 2.08 | m/s |  | 4.46 | m/s | 22.4728 | 0.0095017 | 25.2532 |  | 0 | 1085.5 | 1.0855 | 23.2642 | 6.4679 | 5.0031 | 0.019789 | 65.9978 | 1.6448
2025-05-20 08:46 | 2693 | Remove | 2025-05-20 | 8:46 | ST | GS | - | 144 | g | 0 | 112.4 | 11.533 | 1140 | 10144 | 22:29 | 29 | 1.81 m/s | 22.5 | 30.9 | 4.3 m/s | 15.7 |  | 1.81 | m/s |  | 4.3 | m/s | 22.4811 | 0.0095 | 25.2627 |  | -1.5 | 1085.5 | 1.0855 | 23.2729 | 6.4679 | 5.0031 | 0.01722 | 66.015 | 1.6443
2025-05-20 08:46 | 2694 | Remove | 2025-05-20 | 8:46 | ST | GS | - | 144 | g | 0 | 112.4 | 11.49 | 1135.3 | 10154 | 22:29 | 29 | 1.73 m/s | 22.3 | 30.9 | 4.33 m/s | 15.5 |  | 1.73 | m/s |  | 4.33 | m/s | 22.4894 | 0.0094608 | 25.2722 |  | 0 | 1085.5 | 1.0855 | 23.2816 | 6.4104 | 4.9394 | 0.016313 | 66.0313 | 1.6439
2025-05-20 08:47 | 2695 | Remove | 2025-05-20 | 8:47 | US | GS | - | 155 | g | 0 | 112.4 | 11.505 | 1136.2 | 10163 | 22:30 | 29 | 1.56 m/s | 22.3 | 30.9 | 4.33 m/s | 15.6 |  | 1.56 | m/s |  | 4.33 | m/s | 22.4981 | 0.0094683 | 25.2817 |  | 11 | 1096.5 | 1.0965 | 23.0567 | 6.4104 | 4.9712 | 0.01471 | 66.046 | 1.6602
2025-05-20 08:47 | 2696 | Remove | 2025-05-20 | 8:47 | US | GS | - | 142.5 | g | 0 | 112.4 | 11.513 | 1137.6 | 10173 | 22:30 | 29 | 1.64 m/s | 22.3 | 30.9 | 4.36 m/s | 15.7 |  | 1.64 | m/s |  | 4.36 | m/s | 22.5064 | 0.00948 | 25.2912 |  | -12.5 | 1096.5 | 1.0965 | 23.0653 | 6.4104 | 5.0031 | 0.015464 | 66.0615 | 1.6598
2025-05-20 08:48 | 2697 | Remove | 2025-05-20 | 8:48 | US | GS | - | 149.5 | g | 0 | 112.4 | 11.446 | 1128.5 | 10182 | 22:31 | 29 | 1.64 m/s | 22.5 | 30.9 | 4.35 m/s | 15.7 |  | 1.64 | m/s |  | 4.35 | m/s | 22.5147 | 0.0094042 | 25.3006 |  | 7 | 1103.5 | 1.1035 | 22.9276 | 6.4679 | 5.0031 | 0.015603 | 66.0771 | 1.67
2025-05-20 08:48 | 2698 | Remove | 2025-05-20 | 8:48 | US | GS | - | 149 | g | 0 | 112.4 | 11.499 | 1135.6 | 10192 | 22:31 | 29 | 1.81 m/s | 22.1 | 30.9 | 4.2 m/s | 15.5 |  | 1.81 | m/s |  | 4.2 | m/s | 22.5231 | 0.0094633 | 25.31 |  | -0.5 | 1103.5 | 1.1035 | 22.9361 | 6.3529 | 4.9394 | 0.016914 | 66.094 | 1.6696
2025-05-20 08:49 | 2699 | Remove | 2025-05-20 | 8:49 | ST | GS | - | 145.5 | g | 0 | 112.3 | 11.509 | 1136.2 | 10201 | 22:32 | 29 | 1.78 m/s | 22.5 | 30.9 | 4.26 m/s | 15.8 |  | 1.78 | m/s |  | 4.26 | m/s | 22.5314 | 0.0094683 | 25.3195 |  | -3.5 | 1103.5 | 1.1035 | 22.9447 | 6.4679 | 5.035 | 0.016935 | 66.1109 | 1.6692
2025-05-20 08:49 | 2700 | Remove | 2025-05-20 | 8:49 | US | GS | - | 149.5 | g | 0 | 112.3 | 11.502 | 1136.1 | 10210 | 22:32 | 29 | 1.46 m/s | 22.2 | 30.9 | 4.27 m/s | 15.5 |  | 1.46 | m/s |  | 4.27 | m/s | 22.5397 | 0.0094675 | 25.329 |  | 4 | 1107.5 | 1.1075 | 22.8704 | 6.3817 | 4.9394 | 0.013705 | 66.1246 | 1.6749
2025-05-20 08:50 | 2701 | Keep | 2025-05-20 | 8:50 | US | GS | - | 142.5 | g | 0 | 112.3 | 11.593 | 1147.2 | 10220 | 22:33 | 29 | 1.75 m/s | 22.5 | 30.9 | 4.67 m/s | 15.7 |  | 1.75 | m/s |  | 4.67 | m/s | 22.5481 | 0.00956 | 25.3385 |  | -7 | 1107.5 | 1.1075 | 22.879 | 6.4679 | 5.0031 | 0.01665 | 66.1413 | 1.6744
2025-05-20 08:50 | 2702 | Remove | 2025-05-20 | 8:50 | ST | GS | - | 148.5 | g | 0 | 112.3 | 11.529 | 1138.9 | 10230 | 22:33 | 29 | 1.9 m/s | 22.5 | 31 | 4.29 m/s | 15.7 |  | 1.9 | m/s |  | 4.29 | m/s | 22.5564 | 0.0094908 | 25.348 |  | 6 | 1113.5 | 1.1135 | 22.7643 | 6.4679 | 5.0301 | 0.018077 | 66.1593 | 1.6831
2025-05-20 08:51 | 2703 | Remove | 2025-05-20 | 8:51 | ST | GS | - | 144 | g | 0 | 112.2 | 11.592 | 1146.2 | 10239 | 22:34 | 29 | 2.16 m/s | 22 | 31 | 4.5 m/s | 15.4 |  | 2.16 | m/s |  | 4.5 | m/s | 22.5647 | 0.0095517 | 25.3576 |  | -4.5 | 1113.5 | 1.1135 | 22.7728 | 6.3242 | 4.934 | 0.020094 | 66.1794 | 1.6825
2025-05-20 08:51 | 2704 | Remove | 2025-05-20 | 8:51 | US | GS | - | 142 | g | 0 | 112.4 | 11.632 | 1152.4 | 10249 | 22:34 | 29.1 | 2.0 m/s | 22.2 | 31 | 4.36 m/s | 15.5 |  | 2 | m/s |  | 4.36 | m/s | 22.5731 | 0.0096033 | 25.3672 |  | -2 | 1113.5 | 1.1135 | 22.7815 | 6.4166 | 4.966 | 0.018877 | 66.1983 | 1.6821
2025-05-20 08:52 | 2705 | Remove | 2025-05-20 | 8:52 | ST | GS | - | 146.5 | g | 0 | 112.5 | 11.553 | 1142.8 | 10258 | 22:35 | 29.1 | 1.83 m/s | 22.1 | 31 | 4.55 m/s | 15.4 |  | 1.83 | m/s |  | 4.55 | m/s | 22.5814 | 0.0095233 | 25.3767 |  | 4.5 | 1118 | 1.118 | 22.6983 | 6.3877 | 4.934 | 0.017195 | 66.2155 | 1.6884
2025-05-20 08:52 | 2706 | Remove | 2025-05-20 | 8:52 | US | GS | - | 149 | g | 0 | 112.5 | 11.584 | 1146.1 | 10268 | 22:35 | 29.1 | 1.94 m/s | 22.2 | 31.1 | 4.61 m/s | 15.6 |  | 1.94 | m/s |  | 4.61 | m/s | 22.5897 | 0.0095508 | 25.3862 |  | 2.5 | 1120.5 | 1.1205 | 22.6562 | 6.4166 | 5.025 | 0.018311 | 66.2338 | 1.6917
2025-05-20 08:53 | 2707 | Remove | 2025-05-20 | 8:53 | ST | GS | - | 142 | g | 0 | 112.6 | 11.546 | 1142.2 | 10277 | 22:36 | 29.1 | 1.94 m/s | 22.6 | 31.1 | 4.63 m/s | 15.8 |  | 1.94 | m/s |  | 4.63 | m/s | 22.5981 | 0.0095183 | 25.3958 |  | -7 | 1120.5 | 1.1205 | 22.6647 | 6.5322 | 5.0895 | 0.018641 | 66.2525 | 1.6913
2025-05-20 08:53 | 2708 | Remove | 2025-05-20 | 8:53 | US | GS | - | 150.5 | g | 0 | 112.6 | 11.55 | 1143 | 10287 | 22:36 | 29.1 | 2.08 m/s | 22.1 | 31.1 | 4.3 m/s | 15.4 |  | 2.08 | m/s |  | 4.3 | m/s | 22.6064 | 0.009525 | 25.4053 |  | 8.5 | 1129 | 1.129 | 22.5025 | 6.3877 | 4.9606 | 0.019544 | 66.272 | 1.7036
2025-05-20 08:54 | 2709 | Remove | 2025-05-20 | 8:54 | ST | GS | - | 141 | g | 0 | 112.5 | 11.6 | 1148.6 | 10297 | 22:37 | 29.1 | 1.78 m/s | 22.2 | 31.1 | 4.2 m/s | 15.4 |  | 1.78 | m/s |  | 4.2 | m/s | 22.6147 | 0.0095717 | 25.4149 |  | -9.5 | 1129 | 1.129 | 22.5109 | 6.4166 | 4.9606 | 0.016801 | 66.2888 | 1.7032
2025-05-20 08:54 | 2710 | Remove | 2025-05-20 | 8:54 | ST | GS | - | 144.5 | g | 0 | 112.5 | 11.594 | 1147.7 | 10306 | 22:37 | 29.1 | 1.82 m/s | 23 | 31.1 | 4.32 m/s | 16 |  | 1.82 | m/s |  | 4.32 | m/s | 22.6231 | 0.0095642 | 25.4244 |  | 3.5 | 1132.5 | 1.1325 | 22.4498 | 6.6478 | 5.1539 | 0.017797 | 66.3066 | 1.708
2025-05-20 08:55 | 2711 | Remove | 2025-05-20 | 8:55 | ST | GS | - | 147 | g | 0 | 112.6 | 11.553 | 1142.7 | 10316 | 22:38 | 29.1 | 1.87 m/s | 22.8 | 31.1 | 4.16 m/s | 15.5 |  | 1.87 | m/s |  | 4.16 | m/s | 22.6314 | 0.0095225 | 25.4339 |  | 2.5 | 1135 | 1.135 | 22.4088 | 6.59 | 4.9928 | 0.018127 | 66.3247 | 1.7113
2025-05-20 08:55 | 2712 | Remove | 2025-05-20 | 8:55 | ST | GS | - | 146 | g | 0 | 112.6 | 11.583 | 1146.1 | 10325 | 22:38 | 29.1 | 1.95 m/s | 23.4 | 31.1 | 4.2 m/s | 16.7 |  | 1.95 | m/s |  | 4.2 | m/s | 22.64 | 0.0095508 | 25.4435 |  | -1 | 1135 | 1.135 | 22.4172 | 6.7635 | 5.3794 | 0.0194 | 66.3441 | 1.7108
2025-05-20 08:56 | 2713 | Remove | 2025-05-20 | 8:56 | ST | GS | - | 147 | g | 0 | 112.6 | 11.582 | 1146.7 | 10335 | 22:39 | 29.1 | 1.87 m/s | 23.3 | 31.1 | 4.26 m/s | 17.4 |  | 1.87 | m/s |  | 4.26 | m/s | 22.6483 | 0.0095558 | 25.453 |  | 1 | 1136 | 1.136 | 22.4059 | 6.7345 | 5.6048 | 0.018525 | 66.3627 | 1.7118
2025-05-20 08:56 | 2714 | Remove | 2025-05-20 | 8:56 | US | GS | - | 150.5 | g | 0 | 112.6 | 11.553 | 1142.3 | 10344 | 22:39 | 29.1 | 1.55 m/s | 22.8 | 31.1 | 4.33 m/s | 15.8 |  | 1.55 | m/s |  | 4.33 | m/s | 22.6567 | 0.0095192 | 25.4626 |  | 3.5 | 1139.5 | 1.1395 | 22.3454 | 6.59 | 5.0895 | 0.015025 | 66.3777 | 1.7167
2025-05-20 08:57 | 2715 | Remove | 2025-05-20 | 8:57 | US | GS | - | 146 | g | 0 | 112.6 | 11.468 | 1132.9 | 10354 | 22:40 | 29.1 | 1.83 m/s | 22.2 | 31.1 | 4.32 m/s | 15.5 |  | 1.83 | m/s |  | 4.32 | m/s | 22.6653 | 0.0094408 | 25.472 |  | -4.5 | 1139.5 | 1.1395 | 22.3537 | 6.4166 | 4.9928 | 0.017273 | 66.395 | 1.7162
2025-05-20 08:57 | 2716 | Remove | 2025-05-20 | 8:57 | US | GS | - | 144 | g | 0 | 112.4 | 11.569 | 1144.2 | 10363 | 22:40 | 29.1 | 2.11 m/s | 21.8 | 31 | 4.24 m/s | 15.2 |  | 2.11 | m/s |  | 4.24 | m/s | 22.6736 | 0.009535 | 25.4815 |  | -2 | 1139.5 | 1.1395 | 22.362 | 6.301 | 4.8699 | 0.019557 | 66.4145 | 1.7157
2025-05-20 08:58 | 2717 | Remove | 2025-05-20 | 8:58 | ST | GS | - | 153.5 | g | 0 | 112.6 | 11.575 | 1145.6 | 10373 | 22:41 | 29.1 | 1.74 m/s | 22.2 | 31 | 4.32 m/s | 15.6 |  | 1.74 | m/s |  | 4.32 | m/s | 22.6819 | 0.0095467 | 25.4911 |  | 9.5 | 1149 | 1.149 | 22.1855 | 6.4166 | 4.9981 | 0.016423 | 66.4309 | 1.7296
2025-05-20 08:58 | 2718 | Remove | 2025-05-20 | 8:58 | US | GS | - | 149 | g | 0 | 112.5 | 11.524 | 1139.9 | 10383 | 22:41 | 29.1 | 1.7 m/s | 22.2 | 31 | 4.33 m/s | 15.5 |  | 1.7 | m/s |  | 4.33 | m/s | 22.6903 | 0.0094992 | 25.5006 |  | -4.5 | 1149 | 1.149 | 22.1937 | 6.4166 | 4.966 | 0.016046 | 66.447 | 1.7292
2025-05-20 08:59 | 2719 | Remove | 2025-05-20 | 8:59 | US | GS | - | 155 | g | 0 | 112.6 | 11.516 | 1138.1 | 10392 | 22:42 | 29.1 | 1.6 m/s | 21.9 | 31 | 4.23 m/s | 15.4 |  | 1.6 | m/s |  | 4.23 | m/s | 22.6986 | 0.0094842 | 25.5101 |  | 6 | 1155 | 1.155 | 22.0866 | 6.3299 | 4.934 | 0.014898 | 66.4619 | 1.7378
2025-05-20 08:59 | 2720 | Remove | 2025-05-20 | 8:59 | ST | GS | - | 153.5 | g | 0 | 112.5 | 11.576 | 1145.1 | 10402 | 22:42 | 29.1 | 1.71 m/s | 22 | 31 | 4.32 m/s | 15.5 |  | 1.71 | m/s |  | 4.32 | m/s | 22.7069 | 0.0095425 | 25.5196 |  | -1.5 | 1155 | 1.155 | 22.0949 | 6.3588 | 4.966 | 0.015995 | 66.4779 | 1.7374
2025-05-20 09:00 | 2721 | Remove | 2025-05-20 | 9:00 | US | GS | - | 151 | g | 0 | 112.5 | 11.555 | 1142.5 | 10411 | 22:43 | 29.1 | 1.6 m/s | 22.3 | 31 | 4.32 m/s | 15.8 |  | 1.6 | m/s |  | 4.32 | m/s | 22.7153 | 0.0095208 | 25.5291 |  | -2.5 | 1155 | 1.155 | 22.1031 | 6.4455 | 5.0621 | 0.01517 | 66.493 | 1.737
2025-05-20 09:00 | 2722 | Remove | 2025-05-20 | 9:00 | US | GS | - | 156.5 | g | 0 | 112.5 | 11.503 | 1135.9 | 10421 | 22:43 | 29.1 | 1.14 m/s | 22.1 | 31 | 4.44 m/s | 15.6 |  | 1.14 | m/s |  | 4.44 | m/s | 22.7236 | 0.0094658 | 25.5386 |  | 5.5 | 1160.5 | 1.1605 | 22.0066 | 6.3877 | 4.9981 | 0.010712 | 66.5038 | 1.745
2025-05-20 09:01 | 2723 | Remove | 2025-05-20 | 9:01 | US | GS | - | 156.5 | g | 0 | 112.4 | 11.564 | 1143.7 | 10430 | 22:44 | 29.1 | 1.41 m/s | 22 | 31 | 4.4 m/s | 15.5 |  | 1.41 | m/s |  | 4.4 | m/s | 22.7319 | 0.0095308 | 25.5481 |  | 0 | 1160.5 | 1.1605 | 22.0148 | 6.3588 | 4.966 | 0.013189 | 66.5169 | 1.7447
2025-05-20 09:01 | 2724 | Remove | 2025-05-20 | 9:01 | ST | GS | - | 150 | g | 0 | 112.4 | 11.529 | 1139.9 | 10440 | 22:44 | 29.1 | 1.6 m/s | 22.5 | 31 | 4.3 m/s | 15.7 |  | 1.6 | m/s |  | 4.3 | m/s | 22.7403 | 0.0094992 | 25.5576 |  | -6.5 | 1160.5 | 1.1605 | 22.0229 | 6.5033 | 5.0301 | 0.015306 | 66.5323 | 1.7443
2025-05-20 09:02 | 2725 | Remove | 2025-05-20 | 9:02 | US | GS | - | 149 | g | 0 | 112.4 | 11.553 | 1142.1 | 10449 | 22:45 | 29.1 | 1.73 m/s | 22.2 | 31 | 4.33 m/s | 15.8 |  | 1.73 | m/s |  | 4.33 | m/s | 22.7486 | 0.0095175 | 25.5671 |  | -1 | 1160.5 | 1.1605 | 22.0311 | 6.4166 | 5.0621 | 0.016329 | 66.5486 | 1.7438
2025-05-20 09:02 | 2726 | Remove | 2025-05-20 | 9:02 | US | GS | - | 148 | g | 0 | 112.2 | 11.554 | 1141.2 | 10459 | 22:45 | 29.1 | 1.66 m/s | 24.2 | 31 | 4.29 m/s | 16.3 |  | 1.66 | m/s |  | 4.29 | m/s | 22.7569 | 0.00951 | 25.5767 |  | -1 | 1160.5 | 1.1605 | 22.0393 | 6.9947 | 5.2223 | 0.01708 | 66.5657 | 1.7434
2025-05-20 09:03 | 2727 | Remove | 2025-05-20 | 9:03 | US | GS | - | 154 | g | 0 | 112.2 | 11.535 | 1140 | 10468 | 22:46 | 29.1 | 1.75 m/s | 23.1 | 31 | 4.53 m/s | 16 |  | 1.75 | m/s |  | 4.53 | m/s | 22.7653 | 0.0095 | 25.5862 |  | 6 | 1166.5 | 1.1665 | 21.9341 | 6.6767 | 5.1262 | 0.017187 | 66.5828 | 1.752
2025-05-20 09:03 | 2728 | Remove | 2025-05-20 | 9:03 | ST | GS | - | 149 | g | 0 | 112.1 | 11.546 | 1141.2 | 10478 | 22:46 | 29.1 | 1.7 m/s | 22.2 | 31 | 4.23 m/s | 15.5 |  | 1.7 | m/s |  | 4.23 | m/s | 22.7736 | 0.00951 | 25.5957 |  | -5 | 1166.5 | 1.1665 | 21.9423 | 6.4166 | 4.966 | 0.016046 | 66.5989 | 1.7515
2025-05-20 09:04 | 2729 | Remove | 2025-05-20 | 9:04 | US | GS | - | 150 | g | 0 | 112.2 | 11.544 | 1140.9 | 10488 | 22:47 | 29.1 | 1.73 m/s | 22.7 | 31 | 4.32 m/s | 16.7 |  | 1.73 | m/s |  | 4.32 | m/s | 22.7822 | 0.0095075 | 25.6052 |  | 1 | 1167.5 | 1.1675 | 21.9316 | 6.5611 | 5.3505 | 0.016697 | 66.6156 | 1.7526
2025-05-20 09:04 | 2730 | Remove | 2025-05-20 | 9:04 | ST | GS | - | 146 | g | 0 | 112.1 | 11.611 | 1148.9 | 10497 | 22:47 | 29.1 | 1.68 m/s | 24.1 | 31 | 4.58 m/s | 16.2 |  | 1.68 | m/s |  | 4.58 | m/s | 22.7906 | 0.0095742 | 25.6148 |  | -4 | 1167.5 | 1.1675 | 21.9398 | 6.9658 | 5.1903 | 0.017214 | 66.6328 | 1.7521
2025-05-20 09:05 | 2731 | Keep | 2025-05-20 | 9:05 | ST | GS | - | 151 | g | 0 | 112 | 11.603 | 1147.9 | 10507 | 22:48 | 29.1 | 1.82 m/s | 22.5 | 31.1 | 4.2 m/s | 15.4 |  | 1.82 | m/s |  | 4.2 | m/s | 22.7989 | 0.0095658 | 25.6243 |  | 5 | 1172.5 | 1.1725 | 21.8544 | 6.5033 | 4.9606 | 0.01741 | 66.6502 | 1.7592
2025-05-20 09:05 | 2732 | Remove | 2025-05-20 | 9:05 | ST | GS | - | 158 | g | 0 | 112 | 11.602 | 1147.9 | 10516 | 22:48 | 29.1 | 1.93 m/s | 22.8 | 31.1 | 4.27 m/s | 16.1 |  | 1.93 | m/s |  | 4.27 | m/s | 22.8072 | 0.0095658 | 25.6339 |  | 7 | 1179.5 | 1.1795 | 21.7328 | 6.59 | 5.1861 | 0.018709 | 66.6689 | 1.7692
2025-05-20 09:06 | 2733 | Remove | 2025-05-20 | 9:06 | US | GS | - | 142.5 | g | 0 | 112.1 | 11.516 | 1137.4 | 10526 | 22:49 | 29.1 | 1.49 m/s | 22.2 | 31.1 | 4.47 m/s | 15.4 |  | 1.49 | m/s |  | 4.47 | m/s | 22.8156 | 0.0094783 | 25.6434 |  | -15.5 | 1179.5 | 1.1795 | 21.7409 | 6.4166 | 4.9606 | 0.014064 | 66.683 | 1.7688
2025-05-20 09:06 | 2734 | Remove | 2025-05-20 | 9:06 | US | GS | - | 165 | g | 0 | 112 | 11.539 | 1140 | 10535 | 22:49 | 29.1 | 1.6 m/s | 21.9 | 31.1 | 4.27 m/s | 15.4 |  | 1.6 | m/s |  | 4.27 | m/s | 22.8239 | 0.0095 | 25.6529 |  | 22.5 | 1202 | 1.202 | 21.3418 | 6.3299 | 4.9606 | 0.014898 | 66.6979 | 1.8022
2025-05-20 09:07 | 2735 | Remove | 2025-05-20 | 9:07 | US | GS | - | 162 | g | 0 | 112.1 | 11.558 | 1142.3 | 10545 | 22:50 | 29.1 | 1.62 m/s | 22.1 | 31 | 4.33 m/s | 15.5 |  | 1.62 | m/s |  | 4.33 | m/s | 22.8322 | 0.0095192 | 25.6624 |  | -3 | 1202 | 1.202 | 21.3497 | 6.3877 | 4.966 | 0.015222 | 66.7131 | 1.8017
2025-05-20 09:07 | 2736 | Remove | 2025-05-20 | 9:07 | ST | GS | - | 146.5 | g | 0 | 112 | 11.571 | 1144.2 | 10554 | 22:50 | 29.1 | 1.78 m/s | 22.3 | 31 | 4.27 m/s | 15.5 |  | 1.78 | m/s |  | 4.27 | m/s | 22.8406 | 0.009535 | 25.6719 |  | -15.5 | 1202 | 1.202 | 21.3577 | 6.4455 | 4.966 | 0.016876 | 66.73 | 1.8013
2025-05-20 09:08 | 2737 | Remove | 2025-05-20 | 9:08 | ST | GS | - | 144.5 | g | 0 | 111.9 | 11.673 | 1156.1 | 10564 | 22:51 | 29.1 | 2.06 m/s | 22.5 | 31.1 | 4.46 m/s | 15.8 |  | 2.06 | m/s |  | 4.46 | m/s | 22.8489 | 0.0096342 | 25.6815 |  | -2 | 1202 | 1.202 | 21.3657 | 6.5033 | 5.0895 | 0.019706 | 66.7497 | 1.8008
2025-05-20 09:08 | 2738 | Remove | 2025-05-20 | 9:08 | US | GS | - | 150.5 | g | 0 | 112 | 11.64 | 1152.2 | 10574 | 22:51 | 29.1 | 2.02 m/s | 22.2 | 31.1 | 4.6 m/s | 15.4 |  | 2.02 | m/s |  | 4.6 | m/s | 22.8572 | 0.0096017 | 25.6912 |  | 6 | 1208 | 1.208 | 21.2675 | 6.4166 | 4.9606 | 0.019066 | 66.7688 | 1.8092
2025-05-20 09:09 | 2739 | Remove | 2025-05-20 | 9:09 | US | GS | - | 150 | g | 0 | 112 | 11.564 | 1143.5 | 10583 | 22:52 | 29.1 | 1.64 m/s | 21.9 | 31.1 | 4.24 m/s | 15.2 |  | 1.64 | m/s |  | 4.24 | m/s | 22.8656 | 0.0095292 | 25.7007 |  | -0.5 | 1208 | 1.208 | 21.2754 | 6.3299 | 4.8962 | 0.01527 | 66.784 | 1.8088
2025-05-20 09:09 | 2740 | Remove | 2025-05-20 | 9:09 | US | GS | - | 153.5 | g | 0 | 111.9 | 11.546 | 1140.9 | 10593 | 22:52 | 29.1 | 1.86 m/s | 22 | 31.1 | 4.21 m/s | 15.3 |  | 1.86 | m/s |  | 4.21 | m/s | 22.8739 | 0.0095075 | 25.7102 |  | 3.5 | 1211.5 | 1.2115 | 21.2218 | 6.3588 | 4.9284 | 0.017398 | 66.8014 | 1.8136
2025-05-20 09:10 | 2741 | Remove | 2025-05-20 | 9:10 | ST | GS | - | 149.5 | g | 0 | 112.1 | 11.509 | 1137.1 | 10602 | 22:53 | 29.1 | 1.74 m/s | 21.8 | 31.1 | 4.47 m/s | 15.3 |  | 1.74 | m/s |  | 4.47 | m/s | 22.8822 | 0.0094758 | 25.7197 |  | -4 | 1211.5 | 1.2115 | 21.2296 | 6.301 | 4.9284 | 0.016127 | 66.8175 | 1.8131
2025-05-20 09:10 | 2742 | Remove | 2025-05-20 | 9:10 | ST | GS | - | 152 | g | 0 | 111.9 | 11.553 | 1142.4 | 10612 | 22:53 | 29.1 | 1.41 m/s | 21.9 | 31.1 | 4.26 m/s | 15.3 |  | 1.41 | m/s |  | 4.26 | m/s | 22.8906 | 0.00952 | 25.7292 |  | 2.5 | 1214 | 1.214 | 21.1937 | 6.3299 | 4.9284 | 0.013129 | 66.8307 | 1.8165
2025-05-20 09:11 | 2743 | Remove | 2025-05-20 | 9:11 | US | GS | - | 152 | g | 0 | 111.9 | 11.63 | 1151.5 | 10621 | 22:54 | 29.1 | 1.62 m/s | 22 | 31 | 4.38 m/s | 15.5 |  | 1.62 | m/s |  | 4.38 | m/s | 22.8989 | 0.0095958 | 25.7388 |  | 0 | 1214 | 1.214 | 21.2016 | 6.3588 | 4.966 | 0.015153 | 66.8458 | 1.8161
2025-05-20 09:11 | 2744 | Remove | 2025-05-20 | 9:11 | ST | GS | - | 150.5 | g | 0 | 112.1 | 11.57 | 1144.2 | 10631 | 22:54 | 29.1 | 1.53 m/s | 22.1 | 31 | 4.24 m/s | 15.5 |  | 1.53 | m/s |  | 4.24 | m/s | 22.9072 | 0.009535 | 25.7483 |  | -1.5 | 1214 | 1.214 | 21.2095 | 6.3877 | 4.966 | 0.014376 | 66.8602 | 1.8157
2025-05-20 09:12 | 2745 | Remove | 2025-05-20 | 9:12 | ST | GS | - | 156.5 | g | 0 | 111.9 | 11.552 | 1141.4 | 10641 | 22:55 | 29.1 | 1.44 m/s | 21.9 | 31 | 4.38 m/s | 15.4 |  | 1.44 | m/s |  | 4.38 | m/s | 22.9156 | 0.0095117 | 25.7578 |  | 6 | 1220 | 1.22 | 21.113 | 6.3299 | 4.934 | 0.013408 | 66.8736 | 1.8243
2025-05-20 09:12 | 2746 | Remove | 2025-05-20 | 9:12 | US | GS | - | 150.5 | g | 0 | 112 | 11.649 | 1153.6 | 10650 | 22:55 | 29.1 | 1.66 m/s | 21.9 | 31 | 4.53 m/s | 15.4 |  | 1.66 | m/s |  | 4.53 | m/s | 22.9239 | 0.0096133 | 25.7674 |  | -6 | 1220 | 1.22 | 21.1209 | 6.3299 | 4.934 | 0.015456 | 66.8891 | 1.8239
2025-05-20 09:13 | 2747 | Remove | 2025-05-20 | 9:13 | US | GS | - | 163 | g | 0 | 112 | 11.58 | 1145.5 | 10660 | 22:56 | 29.1 | 1.77 m/s | 22.1 | 31.1 | 4.29 m/s | 15.4 |  | 1.77 | m/s |  | 4.29 | m/s | 22.9325 | 0.0095458 | 25.777 |  | 12.5 | 1232.5 | 1.2325 | 20.9144 | 6.3877 | 4.9606 | 0.016631 | 66.9057 | 1.8421
2025-05-20 09:13 | 2748 | Remove | 2025-05-20 | 9:13 | US | GS | - | 156 | g | 0 | 112 | 11.587 | 1146.4 | 10669 | 22:56 | 29.1 | 1.52 m/s | 21.8 | 31.1 | 4.27 m/s | 15.3 |  | 1.52 | m/s |  | 4.27 | m/s | 22.9408 | 0.0095533 | 25.7865 |  | -7 | 1232.5 | 1.2325 | 20.9221 | 6.301 | 4.9284 | 0.014088 | 66.9198 | 1.8418
2025-05-20 09:14 | 2749 | Remove | 2025-05-20 | 9:14 | ST | GS | - | 153.5 | g | 0 | 112 | 11.579 | 1144.8 | 10679 | 22:57 | 29.1 | 1.62 m/s | 22 | 31.1 | 4.63 m/s | 15.3 |  | 1.62 | m/s |  | 4.63 | m/s | 22.9492 | 0.00954 | 25.7961 |  | -2.5 | 1232.5 | 1.2325 | 20.9299 | 6.3588 | 4.9284 | 0.015153 | 66.9349 | 1.8413
2025-05-20 09:14 | 2750 | Remove | 2025-05-20 | 9:14 | ST | GS | - | 150.5 | g | 0 | 112 | 11.586 | 1146.1 | 10688 | 22:57 | 29.1 | 1.57 m/s | 22 | 31.1 | 4.33 m/s | 15.4 |  | 1.57 | m/s |  | 4.33 | m/s | 22.9575 | 0.0095508 | 25.8056 |  | -3 | 1232.5 | 1.2325 | 20.9376 | 6.3588 | 4.9606 | 0.014685 | 66.9496 | 1.8409
2025-05-20 09:15 | 2751 | Remove | 2025-05-20 | 9:15 | US | GS | - | 148 | g | 0 | 112.1 | 11.515 | 1137.5 | 10698 | 22:58 | 29.1 | 1.51 m/s | 21.9 | 31.1 | 4.26 m/s | 15.3 |  | 1.51 | m/s |  | 4.26 | m/s | 22.9658 | 0.0094792 | 25.8151 |  | -2.5 | 1232.5 | 1.2325 | 20.9453 | 6.3299 | 4.9284 | 0.01406 | 66.9637 | 1.8405
2025-05-20 09:15 | 2752 | Remove | 2025-05-20 | 9:15 | US | GS | - | 150 | g | 0 | 112.1 | 11.522 | 1138.2 | 10707 | 22:58 | 29.1 | 1.49 m/s | 21.8 | 31.1 | 4.36 m/s | 15.2 |  | 1.49 | m/s |  | 4.36 | m/s | 22.9742 | 0.009485 | 25.8246 |  | 2 | 1234.5 | 1.2345 | 20.9191 | 6.301 | 4.8962 | 0.01381 | 66.9775 | 1.8432
2025-05-20 09:16 | 2753 | Remove | 2025-05-20 | 9:16 | ST | GS | - | 149 | g | 0 | 112.1 | 11.565 | 1143.3 | 10717 | 22:59 | 29.1 | 1.83 m/s | 21.8 | 31 | 4.27 m/s | 15.3 |  | 1.83 | m/s |  | 4.27 | m/s | 22.9825 | 0.0095275 | 25.8341 |  | -1 | 1234.5 | 1.2345 | 20.9268 | 6.301 | 4.902 | 0.016961 | 66.9945 | 1.8427
2025-05-20 09:16 | 2754 | Remove | 2025-05-20 | 9:16 | ST | GS | - | 146.5 | g | 0 | 112 | 11.625 | 1150.2 | 10727 | 22:59 | 29.1 | 1.79 m/s | 21.9 | 31.1 | 4.21 m/s | 15.3 |  | 1.79 | m/s |  | 4.21 | m/s | 22.9908 | 0.009585 | 25.8437 |  | -2.5 | 1234.5 | 1.2345 | 20.9346 | 6.3299 | 4.9284 | 0.016667 | 67.0111 | 1.8422
2025-05-20 09:17 | 2755 | Remove | 2025-05-20 | 9:17 | ST | GS | - | 146 | g | 0 | 111.9 | 11.716 | 1161.5 | 10736 | 23:00 | 29.1 | 1.71 m/s | 22.5 | 31.1 | 4.26 m/s | 15.7 |  | 1.71 | m/s |  | 4.26 | m/s | 22.9992 | 0.0096792 | 25.8534 |  | -0.5 | 1234.5 | 1.2345 | 20.9424 | 6.5033 | 5.0572 | 0.016358 | 67.0275 | 1.8418
2025-05-20 09:17 | 2756 | Remove | 2025-05-20 | 9:17 | ST | GS | - | 150.5 | g | 0 | 112 | 11.579 | 1144.9 | 10746 | 23:00 | 29.2 | 1.91 m/s | 22.5 | 31.1 | 4.44 m/s | 15.4 |  | 1.91 | m/s |  | 4.44 | m/s | 23.0075 | 0.0095408 | 25.8629 |  | 4.5 | 1239 | 1.239 | 20.874 | 6.5389 | 4.9606 | 0.018371 | 67.0459 | 1.848
2025-05-20 09:18 | 2757 | Remove | 2025-05-20 | 9:18 | US | GS | - | 143.5 | g | 0 | 112 | 11.7 | 1159.3 | 10755 | 23:01 | 29.2 | 2.11 m/s | 22.1 | 31.2 | 4.52 m/s | 15.6 |  | 2.11 | m/s |  | 4.52 | m/s | 23.0158 | 0.0096608 | 25.8726 |  | -7 | 1239 | 1.239 | 20.8818 | 6.4227 | 5.0521 | 0.019934 | 67.0658 | 1.8474
2025-05-20 09:18 | 2758 | Remove | 2025-05-20 | 9:18 | US | GS | - | 148 | g | 0 | 112 | 11.699 | 1159.5 | 10765 | 23:01 | 29.2 | 2.0 m/s | 22.1 | 31.2 | 4.43 m/s | 15.3 |  | 2 | m/s |  | 4.43 | m/s | 23.0242 | 0.0096625 | 25.8822 |  | 4.5 | 1243.5 | 1.2435 | 20.814 | 6.4227 | 4.955 | 0.018895 | 67.0847 | 1.8536
2025-05-20 09:19 | 2759 | Remove | 2025-05-20 | 9:19 | US | GS | - | 150 | g | 0 | 111.9 | 11.723 | 1162.5 | 10775 | 23:02 | 29.2 | 1.87 m/s | 22.3 | 31.2 | 4.41 m/s | 15.4 |  | 1.87 | m/s |  | 4.41 | m/s | 23.0325 | 0.0096875 | 25.8919 |  | 2 | 1245.5 | 1.2455 | 20.7884 | 6.4808 | 4.9873 | 0.017827 | 67.1025 | 1.8561
2025-05-20 09:19 | 2760 | Remove | 2025-05-20 | 9:19 | US | GS | - | 146.5 | g | 0 | 112 | 11.641 | 1152.2 | 10784 | 23:02 | 29.2 | 1.83 m/s | 22 | 31.2 | 4.24 m/s | 15.2 |  | 1.83 | m/s |  | 4.24 | m/s | 23.0408 | 0.0096017 | 25.9015 |  | -3.5 | 1245.5 | 1.2455 | 20.7961 | 6.3936 | 4.9226 | 0.017211 | 67.1197 | 1.8556
2025-05-20 09:20 | 2761 | Keep | 2025-05-20 | 9:20 | US | GS | - | 154 | g | 0 | 111.9 | 11.553 | 1141.5 | 10794 | 23:03 | 29.2 | 1.27 m/s | 21.7 | 31.2 | 4.21 m/s | 15 |  | 1.27 | m/s |  | 4.21 | m/s | 23.0492 | 0.0095125 | 25.9111 |  | 7.5 | 1253 | 1.253 | 20.6792 | 6.3064 | 4.8578 | 0.011781 | 67.1315 | 1.8665
2025-05-20 09:20 | 2762 | Remove | 2025-05-20 | 9:20 | US | GS | - | 147 | g | 0 | 111.8 | 11.643 | 1152 | 10804 | 23:03 | 29.2 | 1.63 m/s | 21.6 | 31.2 | 4.29 m/s | 15.1 |  | 1.63 | m/s |  | 4.29 | m/s | 23.0575 | 0.0096 | 25.9207 |  | -7 | 1253 | 1.253 | 20.6869 | 6.2773 | 4.8902 | 0.015051 | 67.1466 | 1.8661
2025-05-20 09:21 | 2763 | Remove | 2025-05-20 | 9:21 | US | GS | - | 146.5 | g | 0 | 111.9 | 11.603 | 1147.1 | 10813 | 23:04 | 29.2 | 1.56 m/s | 21.7 | 31.2 | 4.33 m/s | 15.2 |  | 1.56 | m/s |  | 4.33 | m/s | 23.0658 | 0.0095592 | 25.9302 |  | -0.5 | 1253 | 1.253 | 20.6945 | 6.3064 | 4.9226 | 0.014471 | 67.161 | 1.8657
2025-05-20 09:21 | 2764 | Remove | 2025-05-20 | 9:21 | US | GS | - | 157 | g | 0 | 111.7 | 11.644 | 1151.8 | 10823 | 23:04 | 29.2 | 1.95 m/s | 22.1 | 31.2 | 4.43 m/s | 15.4 |  | 1.95 | m/s |  | 4.43 | m/s | 23.0744 | 0.0095983 | 25.9398 |  | 10.5 | 1263.5 | 1.2635 | 20.5301 | 6.4227 | 4.9873 | 0.018423 | 67.1794 | 1.8808
2025-05-20 09:22 | 2765 | Remove | 2025-05-20 | 9:22 | US | GS | - | 150 | g | 0 | 111.7 | 11.624 | 1149.1 | 10832 | 23:05 | 29.2 | 1.73 m/s | 21.8 | 31.2 | 4.21 m/s | 15.1 |  | 1.73 | m/s |  | 4.21 | m/s | 23.0828 | 0.0095758 | 25.9494 |  | -7 | 1263.5 | 1.2635 | 20.5377 | 6.3355 | 4.8902 | 0.016122 | 67.1956 | 1.8803
2025-05-20 09:22 | 2766 | Remove | 2025-05-20 | 9:22 | ST | GS | - | 146.5 | g | 0 | 111.7 | 11.719 | 1161.1 | 10842 | 23:05 | 29.2 | 1.9 m/s | 22 | 31.2 | 4.3 m/s | 15.3 |  | 1.9 | m/s |  | 4.3 | m/s | 23.0911 | 0.0096758 | 25.9591 |  | -3.5 | 1263.5 | 1.2635 | 20.5454 | 6.3936 | 4.955 | 0.017869 | 67.2134 | 1.8798
2025-05-20 09:23 | 2767 | Remove | 2025-05-20 | 9:23 | ST | GS | - | 149 | g | 0 | 111.7 | 11.683 | 1156.8 | 10852 | 23:06 | 29.2 | 1.78 m/s | 22.1 | 31.2 | 4.46 m/s | 15.3 |  | 1.78 | m/s |  | 4.46 | m/s | 23.0994 | 0.00964 | 25.9687 |  | 2.5 | 1266 | 1.266 | 20.5124 | 6.4227 | 4.955 | 0.016817 | 67.2303 | 1.8831
2025-05-20 09:23 | 2768 | Remove | 2025-05-20 | 9:23 | ST | GS | - | 143 | g | 0 | 111.7 | 11.699 | 1158.3 | 10862 | 23:06 | 29.2 | 1.89 m/s | 21.8 | 31.3 | 4.23 m/s | 15.2 |  | 1.89 | m/s |  | 4.23 | m/s | 23.1078 | 0.0096525 | 25.9784 |  | -6 | 1266 | 1.266 | 20.52 | 6.3355 | 4.9491 | 0.017613 | 67.2479 | 1.8826
2025-05-20 09:24 | 2769 | Remove | 2025-05-20 | 9:24 | ST | GS | - | 142.5 | g | 0 | 111.7 | 11.687 | 1157.6 | 10871 | 23:07 | 29.2 | 2.0 m/s | 22.2 | 31.3 | 4.94 m/s | 15.3 |  | 2 | m/s |  | 4.94 | m/s | 23.1161 | 0.0096467 | 25.988 |  | -0.5 | 1266 | 1.266 | 20.5276 | 6.4517 | 4.9816 | 0.018981 | 67.2669 | 1.8821
2025-05-20 09:24 | 2770 | Remove | 2025-05-20 | 9:24 | US | GS | - | 140.5 | g | 0 | 111.8 | 11.756 | 1165.8 | 10881 | 23:07 | 29.2 | 2.08 m/s | 22.2 | 31.3 | 4.76 m/s | 15.2 |  | 2.08 | m/s |  | 4.76 | m/s | 23.1244 | 0.009715 | 25.9977 |  | -2 | 1266 | 1.266 | 20.5353 | 6.4517 | 4.9491 | 0.01974 | 67.2866 | 1.8815
2025-05-20 09:25 | 2771 | Remove | 2025-05-20 | 9:25 | US | GS | - | 149.5 | g | 0 | 112 | 11.697 | 1159.1 | 10890 | 23:08 | 29.3 | 2.12 m/s | 22.7 | 31.4 | 4.3 m/s | 15.4 |  | 2.12 | m/s |  | 4.3 | m/s | 23.1328 | 0.0096592 | 26.0074 |  | 9 | 1275 | 1.275 | 20.3979 | 6.6331 | 5.0412 | 0.020685 | 67.3073 | 1.8943
2025-05-20 09:25 | 2772 | Remove | 2025-05-20 | 9:25 | US | GS | - | 145 | g | 0 | 112.2 | 11.585 | 1146.8 | 10900 | 23:08 | 29.3 | 1.93 m/s | 21.8 | 31.4 | 4.4 m/s | 15 |  | 1.93 | m/s |  | 4.4 | m/s | 23.1411 | 0.0095567 | 26.0169 |  | -4.5 | 1275 | 1.275 | 20.4054 | 6.3701 | 4.9102 | 0.018085 | 67.3254 | 1.8938
2025-05-20 09:26 | 2773 | Remove | 2025-05-20 | 9:26 | US | GS | - | 145.5 | g | 0 | 112.2 | 11.568 | 1144 | 10910 | 23:09 | 29.2 | 1.94 m/s | 21.6 | 31.3 | 4.36 m/s | 14.8 |  | 1.94 | m/s |  | 4.36 | m/s | 23.1494 | 0.0095333 | 26.0265 |  | 0.5 | 1275.5 | 1.2755 | 20.4049 | 6.2773 | 4.8188 | 0.017913 | 67.3433 | 1.894
2025-05-20 09:26 | 2774 | Remove | 2025-05-20 | 9:26 | ST | GS | - | 146 | g | 0 | 112.2 | 11.658 | 1155.5 | 10919 | 23:09 | 29.2 | 1.97 m/s | 21.6 | 31.3 | 5.0 m/s | 15 |  | 1.97 | m/s |  | 5 | m/s | 23.1578 | 0.0096292 | 26.0361 |  | 0.5 | 1276 | 1.276 | 20.4045 | 6.2773 | 4.884 | 0.018191 | 67.3615 | 1.8943
2025-05-20 09:27 | 2775 | Remove | 2025-05-20 | 9:27 | ST | GS | - | 149 | g | 0 | 112 | 11.708 | 1160.5 | 10929 | 23:10 | 29.2 | 2.02 m/s | 22.1 | 31.3 | 4.38 m/s | 15 |  | 2.02 | m/s |  | 4.38 | m/s | 23.1661 | 0.0096708 | 26.0458 |  | 3 | 1279 | 1.279 | 20.3642 | 6.4227 | 4.884 | 0.019084 | 67.3805 | 1.8982
2025-05-20 09:27 | 2776 | Remove | 2025-05-20 | 9:27 | ST | GS | - | 147.5 | g | 0 | 112.2 | 11.579 | 1145.3 | 10939 | 23:10 | 29.2 | 1.89 m/s | 21.7 | 31.3 | 4.33 m/s | 14.8 |  | 1.89 | m/s |  | 4.33 | m/s | 23.1744 | 0.0095442 | 26.0553 |  | -1.5 | 1279 | 1.279 | 20.3716 | 6.3064 | 4.8188 | 0.017533 | 67.3981 | 1.8977
2025-05-20 09:28 | 2777 | Remove | 2025-05-20 | 9:28 | US | GS | - | 145.5 | g | 0 | 112.1 | 11.686 | 1157.8 | 10948 | 23:11 | 29.2 | 2.0 m/s | 21.5 | 31.3 | 5.02 m/s | 15 |  | 2 | m/s |  | 5.02 | m/s | 23.1828 | 0.0096483 | 26.065 |  | -2 | 1279 | 1.279 | 20.3792 | 6.2483 | 4.884 | 0.018382 | 67.4165 | 1.8972
2025-05-20 09:28 | 2778 | Remove | 2025-05-20 | 9:28 | ST | GS | - | 146.5 | g | 0 | 112 | 11.617 | 1149.5 | 10958 | 23:11 | 29.2 | 2.15 m/s | 21.8 | 31.3 | 4.44 m/s | 15 |  | 2.15 | m/s |  | 4.44 | m/s | 23.1911 | 0.0095792 | 26.0745 |  | 1 | 1280 | 1.28 | 20.3707 | 6.3355 | 4.884 | 0.020036 | 67.4365 | 1.8981
2025-05-20 09:29 | 2779 | Remove | 2025-05-20 | 9:29 | US | GS | - | 151.5 | g | 0 | 111.7 | 11.753 | 1164.8 | 10968 | 23:12 | 29.2 | 1.75 m/s | 22.3 | 31.3 | 4.56 m/s | 15.1 |  | 1.75 | m/s |  | 4.56 | m/s | 23.1994 | 0.0097067 | 26.0842 |  | 5 | 1285 | 1.285 | 20.299 | 6.4808 | 4.9165 | 0.016683 | 67.4532 | 1.905
2025-05-20 09:29 | 2780 | Remove | 2025-05-20 | 9:29 | ST | GS | - | 153 | g | 0 | 111.9 | 11.583 | 1145.1 | 10977 | 23:12 | 29.2 | 1.66 m/s | 21.5 | 31.3 | 4.27 m/s | 14.8 |  | 1.66 | m/s |  | 4.27 | m/s | 23.2078 | 0.0095425 | 26.0938 |  | 1.5 | 1286.5 | 1.2865 | 20.2828 | 6.2483 | 4.8188 | 0.015257 | 67.4684 | 1.9068
2025-05-20 09:30 | 2781 | Remove | 2025-05-20 | 9:30 | US | GS | - | 150.5 | g | 0 | 111.8 | 11.65 | 1152.3 | 10987 | 23:13 | 29.2 | 1.71 m/s | 21.4 | 31.3 | 4.26 m/s | 15.2 |  | 1.71 | m/s |  | 4.26 | m/s | 23.2164 | 0.0096025 | 26.1034 |  | -2.5 | 1286.5 | 1.2865 | 20.2902 | 6.2192 | 4.9491 | 0.015644 | 67.4841 | 1.9064
2025-05-20 09:30 | 2782 | Remove | 2025-05-20 | 9:30 | ST | GS | - | 153.5 | g | 0 | 111.7 | 11.647 | 1152.1 | 10997 | 23:13 | 29.2 | 1.98 m/s | 21.7 | 31.3 | 4.29 m/s | 15.1 |  | 1.98 | m/s |  | 4.29 | m/s | 23.2247 | 0.0096008 | 26.113 |  | 3 | 1289.5 | 1.2895 | 20.2505 | 6.3064 | 4.9165 | 0.018367 | 67.5024 | 1.9103
2025-05-20 09:31 | 2783 | Remove | 2025-05-20 | 9:31 | ST | GS | - | 152 | g | 0 | 111.7 | 11.7 | 1158.5 | 11006 | 23:14 | 29.2 | 1.62 m/s | 22 | 31.2 | 4.29 m/s | 15.2 |  | 1.62 | m/s |  | 4.29 | m/s | 23.2331 | 0.0096542 | 26.1226 |  | -1.5 | 1289.5 | 1.2895 | 20.258 | 6.3936 | 4.9226 | 0.015236 | 67.5177 | 1.9099
2025-05-20 09:31 | 2784 | Remove | 2025-05-20 | 9:31 | US | GS | - | 154 | g | 0 | 111.9 | 11.634 | 1151.4 | 11016 | 23:14 | 29.2 | 1.6 m/s | 21.7 | 31.3 | 4.29 m/s | 15 |  | 1.6 | m/s |  | 4.29 | m/s | 23.2414 | 0.009595 | 26.1322 |  | 2 | 1291.5 | 1.2915 | 20.234 | 6.3064 | 4.884 | 0.014842 | 67.5325 | 1.9124
2025-05-20 09:32 | 2785 | Remove | 2025-05-20 | 9:32 | ST | GS | - | 156 | g | 0 | 111.8 | 11.659 | 1154 | 11026 | 23:15 | 29.2 | 1.63 m/s | 21.5 | 31.3 | 4.46 m/s | 14.8 |  | 1.63 | m/s |  | 4.46 | m/s | 23.2497 | 0.0096167 | 26.1419 |  | 2 | 1293.5 | 1.2935 | 20.2102 | 6.2483 | 4.8188 | 0.014981 | 67.5475 | 1.9149
2025-05-20 09:32 | 2786 | Remove | 2025-05-20 | 9:32 | ST | GS | - | 150 | g | 0 | 111.8 | 11.662 | 1154.9 | 11035 | 23:15 | 29.2 | 1.93 m/s | 21.4 | 31.3 | 4.26 m/s | 14.8 |  | 1.93 | m/s |  | 4.26 | m/s | 23.2581 | 0.0096242 | 26.1515 |  | -6 | 1293.5 | 1.2935 | 20.2176 | 6.2192 | 4.8188 | 0.017656 | 67.5652 | 1.9144
2025-05-20 09:33 | 2787 | Remove | 2025-05-20 | 9:33 | ST | GS | - | 149.5 | g | 0 | 111.6 | 11.753 | 1165 | 11045 | 23:16 | 29.2 | 1.79 m/s | 21.4 | 31.3 | 4.44 m/s | 15 |  | 1.79 | m/s |  | 4.44 | m/s | 23.2664 | 0.0097083 | 26.1612 |  | -0.5 | 1293.5 | 1.2935 | 20.2251 | 6.2192 | 4.884 | 0.016375 | 67.5815 | 1.914
2025-05-20 09:33 | 2788 | Remove | 2025-05-20 | 9:33 | ST | GS | - | 153 | g | 0 | 111.7 | 11.752 | 1164.7 | 11055 | 23:16 | 29.3 | 1.67 m/s | 21.7 | 31.3 | 4.26 m/s | 15 |  | 1.67 | m/s |  | 4.26 | m/s | 23.2747 | 0.0097058 | 26.1709 |  | 3.5 | 1297 | 1.297 | 20.178 | 6.3409 | 4.884 | 0.015576 | 67.5971 | 1.9187
2025-05-20 09:34 | 2789 | Remove | 2025-05-20 | 9:34 | US | GS | - | 167 | g | 0 | 111.8 | 11.646 | 1152.2 | 11064 | 23:17 | 29.3 | 1.68 m/s | 21.3 | 31.3 | 4.32 m/s | 14.7 |  | 1.68 | m/s |  | 4.32 | m/s | 23.2831 | 0.0096017 | 26.1805 |  | 14 | 1311 | 1.311 | 19.9699 | 6.224 | 4.7863 | 0.015381 | 67.6125 | 1.939
2025-05-20 09:34 | 2790 | Remove | 2025-05-20 | 9:34 | ST | GS | - | 146 | g | 0 | 111.6 | 11.776 | 1167.2 | 11074 | 23:17 | 29.3 | 1.68 m/s | 21.2 | 31.3 | 4.6 m/s | 15 |  | 1.68 | m/s |  | 4.6 | m/s | 23.2914 | 0.0097267 | 26.1902 |  | -21 | 1311 | 1.311 | 19.9773 | 6.1948 | 4.884 | 0.015309 | 67.6278 | 1.9386
2025-05-20 09:35 | 2791 | Keep | 2025-05-20 | 9:35 | ST | GS | - | 146.5 | g | 0 | 111.6 | 11.83 | 1174.6 | 11084 | 23:18 | 29.3 | 1.91 m/s | 21.3 | 31.4 | 4.69 m/s | 15 |  | 1.91 | m/s |  | 4.69 | m/s | 23.2997 | 0.0097883 | 26.2 |  | 0.5 | 1311.5 | 1.3115 | 19.9771 | 6.224 | 4.9102 | 0.017487 | 67.6453 | 1.9388
2025-05-20 09:35 | 2792 | Remove | 2025-05-20 | 9:35 | ST | GS | - | 161 | g | 0 | 111.7 | 11.759 | 1166 | 11094 | 23:18 | 29.3 | 2.11 m/s | 21.5 | 31.4 | 4.4 m/s | 15 |  | 2.11 | m/s |  | 4.4 | m/s | 23.3081 | 0.0097167 | 26.2097 |  | 14.5 | 1326 | 1.326 | 19.766 | 6.2825 | 4.9102 | 0.019499 | 67.6648 | 1.9597
2025-05-20 09:36 | 2793 | Remove | 2025-05-20 | 9:36 | US | GS | - | 154 | g | 0 | 111.7 | 11.761 | 1166.1 | 11103 | 23:19 | 29.4 | 1.97 m/s | 21.2 | 31.4 | 4.44 m/s | 14.7 |  | 1.97 | m/s |  | 4.44 | m/s | 23.3164 | 0.0097175 | 26.2194 |  | -7 | 1326 | 1.326 | 19.7733 | 6.2286 | 4.812 | 0.018049 | 67.6828 | 1.9591
2025-05-20 09:36 | 2794 | Remove | 2025-05-20 | 9:36 | ST | GS | - | 152.5 | g | 0 | 111.6 | 11.829 | 1173.4 | 11113 | 23:19 | 29.4 | 2.0 m/s | 21.4 | 31.4 | 4.58 m/s | 14.8 |  | 2 | m/s |  | 4.58 | m/s | 23.3247 | 0.0097783 | 26.2292 |  | -1.5 | 1326 | 1.326 | 19.7807 | 6.2874 | 4.8448 | 0.018497 | 67.7013 | 1.9586
2025-05-20 09:37 | 2795 | Remove | 2025-05-20 | 9:37 | ST | GS | - | 156 | g | 0 | 111.7 | 11.763 | 1166.2 | 11123 | 23:20 | 29.4 | 1.59 m/s | 21.2 | 31.4 | 4.38 m/s | 14.8 |  | 1.59 | m/s |  | 4.38 | m/s | 23.3331 | 0.0097183 | 26.2389 |  | 3.5 | 1329.5 | 1.3295 | 19.7359 | 6.2286 | 4.8448 | 0.014568 | 67.7159 | 1.9633
2025-05-20 09:37 | 2796 | Remove | 2025-05-20 | 9:37 | US | GS | - | 154.5 | g | 0 | 111.6 | 11.842 | 1175 | 11133 | 23:20 | 29.4 | 1.74 m/s | 21.6 | 31.4 | 4.66 m/s | 15 |  | 1.74 | m/s |  | 4.66 | m/s | 23.3414 | 0.0097917 | 26.2487 |  | -1.5 | 1329.5 | 1.3295 | 19.7433 | 6.3462 | 4.9102 | 0.016243 | 67.7321 | 1.9629
2025-05-20 09:38 | 2797 | Remove | 2025-05-20 | 9:38 | US | GS | - | 156 | g | 0 | 111.6 | 11.708 | 1159.1 | 11142 | 23:21 | 29.4 | 1.6 m/s | 21 | 31.4 | 4.33 m/s | 14.5 |  | 1.6 | m/s |  | 4.33 | m/s | 23.3497 | 0.0096592 | 26.2584 |  | 1.5 | 1331 | 1.331 | 19.7283 | 6.1699 | 4.7466 | 0.014521 | 67.7467 | 1.9647
2025-05-20 09:38 | 2798 | Remove | 2025-05-20 | 9:38 | US | GS | - | 164.5 | g | 0 | 111.9 | 11.624 | 1150.3 | 11152 | 23:21 | 29.4 | 1.68 m/s | 20.9 | 31.4 | 4.58 m/s | 14.5 |  | 1.68 | m/s |  | 4.58 | m/s | 23.3581 | 0.0095858 | 26.268 |  | 8.5 | 1339.5 | 1.3395 | 19.6103 | 6.1405 | 4.7466 | 0.015175 | 67.7618 | 1.9768
2025-05-20 09:39 | 2799 | Remove | 2025-05-20 | 9:39 | ST | GS | - | 163 | g | 0 | 111.8 | 11.639 | 1151.9 | 11162 | 23:22 | 29.4 | 1.53 m/s | 20.9 | 31.4 | 4.52 m/s | 14.6 |  | 1.53 | m/s |  | 4.52 | m/s | 23.3667 | 0.0095992 | 26.2776 |  | -1.5 | 1339.5 | 1.3395 | 19.6175 | 6.1405 | 4.7793 | 0.01382 | 67.7757 | 1.9764
2025-05-20 09:39 | 2800 | Remove | 2025-05-20 | 9:39 | US | GS | - | 163 | g | 0 | 111.6 | 11.673 | 1155.4 | 11171 | 23:22 | 29.3 | 1.6 m/s | 21 | 31.3 | 4.26 m/s | 14.5 |  | 1.6 | m/s |  | 4.26 | m/s | 23.375 | 0.0096283 | 26.2872 |  | 0 | 1339.5 | 1.3395 | 19.6246 | 6.1363 | 4.7212 | 0.014442 | 67.7901 | 1.976
2025-05-20 09:40 | 2801 | Remove | 2025-05-20 | 9:40 | ST | GS | - | 156.5 | g | 0 | 111.8 | 11.723 | 1161.4 | 11181 | 23:23 | 29.3 | 1.77 m/s | 21 | 31.3 | 4.49 m/s | 14.6 |  | 1.77 | m/s |  | 4.49 | m/s | 23.3833 | 0.0096783 | 26.2969 |  | -6.5 | 1339.5 | 1.3395 | 19.6319 | 6.1363 | 4.7537 | 0.015977 | 67.8061 | 1.9755
2025-05-20 09:40 | 2802 | Remove | 2025-05-20 | 9:40 | ST | GS | - | 154.5 | g | 0 | 111.7 | 11.674 | 1156 | 11191 | 23:24 | 29.3 | 1.87 m/s | 21 | 31.3 | 4.69 m/s | 14.8 |  | 1.87 | m/s |  | 4.69 | m/s | 23.3917 | 0.0096333 | 26.3065 |  | -2 | 1339.5 | 1.3395 | 19.6391 | 6.1363 | 4.8188 | 0.016879 | 67.823 | 1.975
2025-05-20 09:41 | 2803 | Remove | 2025-05-20 | 9:41 | US | GS | - | 160 | g | 0 | 111.8 | 11.653 | 1153.3 | 11200 | 23:24 | 29.3 | 1.6 m/s | 21.4 | 31.3 | 4.52 m/s | 14.6 |  | 1.6 | m/s |  | 4.52 | m/s | 23.4 | 0.0096108 | 26.3161 |  | 5.5 | 1345 | 1.345 | 19.5659 | 6.2532 | 4.7537 | 0.014717 | 67.8377 | 1.9827
2025-05-20 09:41 | 2804 | Remove | 2025-05-20 | 9:41 | US | GS | - | 154 | g | 0 | 111.7 | 11.645 | 1152.1 | 11210 | 23:24 | 29.3 | 1.63 m/s | 21 | 31.3 | 4.27 m/s | 14.6 |  | 1.63 | m/s |  | 4.27 | m/s | 23.4083 | 0.0096008 | 26.3257 |  | -6 | 1345 | 1.345 | 19.573 | 6.1363 | 4.7537 | 0.014713 | 67.8524 | 1.9822
2025-05-20 09:42 | 2805 | Remove | 2025-05-20 | 9:42 | US | GS | - | 168 | g | 0 | 111.7 | 11.686 | 1157.3 | 11220 | 23:25 | 29.3 | 1.94 m/s | 21.1 | 31.3 | 4.35 m/s | 14.6 |  | 1.94 | m/s |  | 4.35 | m/s | 23.4167 | 0.0096442 | 26.3354 |  | 14 | 1359 | 1.359 | 19.3785 | 6.1656 | 4.7537 | 0.017595 | 67.87 | 2.0024
2025-05-20 09:42 | 2806 | Remove | 2025-05-20 | 9:42 | ST | GS | - | 151 | g | 0 | 111.7 | 11.759 | 1165.6 | 11229 | 23:26 | 29.3 | 1.78 m/s | 21.1 | 31.3 | 4.64 m/s | 15 |  | 1.78 | m/s |  | 4.64 | m/s | 23.425 | 0.0097133 | 26.3451 |  | -17 | 1359 | 1.359 | 19.3856 | 6.1656 | 4.884 | 0.016143 | 67.8861 | 2.0019
2025-05-20 09:43 | 2807 | Remove | 2025-05-20 | 9:43 | ST | GS | - | 148 | g | 0 | 111.5 | 11.801 | 1170.4 | 11239 | 23:26 | 29.3 | 1.91 m/s | 21.3 | 31.4 | 4.44 m/s | 14.7 |  | 1.91 | m/s |  | 4.44 | m/s | 23.4333 | 0.0097533 | 26.3548 |  | -3 | 1359 | 1.359 | 19.3928 | 6.224 | 4.812 | 0.017487 | 67.9036 | 2.0014
2025-05-20 09:43 | 2808 | Remove | 2025-05-20 | 9:43 | ST | GS | - | 150 | g | 0 | 111.5 | 11.852 | 1176.4 | 11249 | 23:26 | 29.4 | 1.87 m/s | 21.1 | 31.4 | 4.46 m/s | 14.6 |  | 1.87 | m/s |  | 4.46 | m/s | 23.4417 | 0.0098033 | 26.3646 |  | 2 | 1361 | 1.361 | 19.3715 | 6.1993 | 4.7793 | 0.017052 | 67.9207 | 2.0038
2025-05-20 09:44 | 2809 | Remove | 2025-05-20 | 9:44 | ST | GS | - | 150.5 | g | 0 | 111.6 | 11.851 | 1176.4 | 11259 | 23:27 | 29.4 | 1.95 m/s | 21 | 31.4 | 4.52 m/s | 14.7 |  | 1.95 | m/s |  | 4.52 | m/s | 23.45 | 0.0098033 | 26.3744 |  | 0.5 | 1361.5 | 1.3615 | 19.3716 | 6.1699 | 4.812 | 0.017698 | 67.9384 | 2.004
2025-05-20 09:44 | 2810 | Remove | 2025-05-20 | 9:44 | ST | GS | - | 158 | g | 0 | 111.6 | 11.81 | 1171 | 11268 | 23:28 | 29.5 | 1.75 m/s | 21.1 | 31.5 | 4.3 m/s | 14.6 |  | 1.75 | m/s |  | 4.3 | m/s | 23.4583 | 0.0097583 | 26.3842 |  | 7.5 | 1369 | 1.369 | 19.2726 | 6.2331 | 4.805 | 0.016045 | 67.9544 | 2.0146
2025-05-20 09:45 | 2811 | Remove | 2025-05-20 | 9:45 | US | GS | - | 149.5 | g | 0 | 111.7 | 11.713 | 1160.2 | 11278 | 23:28 | 29.5 | 1.77 m/s | 21.1 | 31.5 | 4.32 m/s | 14.6 |  | 1.77 | m/s |  | 4.32 | m/s | 23.4667 | 0.0096683 | 26.3939 |  | -8.5 | 1369 | 1.369 | 19.2797 | 6.2331 | 4.805 | 0.016229 | 67.9706 | 2.0141
2025-05-20 09:45 | 2812 | Remove | 2025-05-20 | 9:45 | ST | GS | - | 154 | g | 0 | 111.7 | 11.735 | 1162.8 | 11288 | 23:28 | 29.5 | 1.59 m/s | 20.8 | 31.5 | 4.27 m/s | 14.6 |  | 1.59 | m/s |  | 4.27 | m/s | 23.475 | 0.00969 | 26.4036 |  | 4.5 | 1373.5 | 1.3735 | 19.2236 | 6.1445 | 4.805 | 0.014371 | 67.985 | 2.0203
2025-05-20 09:46 | 2813 | Remove | 2025-05-20 | 9:46 | US | GS | - | 153.5 | g | 0 | 111.6 | 11.786 | 1168.1 | 11298 | 23:29 | 29.4 | 1.83 m/s | 21 | 31.4 | 4.24 m/s | 14.8 |  | 1.83 | m/s |  | 4.24 | m/s | 23.4833 | 0.0097342 | 26.4133 |  | -0.5 | 1373.5 | 1.3735 | 19.2306 | 6.1699 | 4.8448 | 0.016608 | 68.0016 | 2.0198
2025-05-20 09:46 | 2814 | Remove | 2025-05-20 | 9:46 | ST | GS | - | 157.5 | g | 0 | 111.7 | 11.772 | 1166.8 | 11307 | 23:30 | 29.4 | 1.63 m/s | 21.5 | 31.4 | 4.72 m/s | 14.7 |  | 1.63 | m/s |  | 4.72 | m/s | 23.4917 | 0.0097233 | 26.423 |  | 4 | 1377.5 | 1.3775 | 19.1819 | 6.3168 | 4.812 | 0.015146 | 68.0168 | 2.0252
2025-05-20 09:47 | 2815 | Remove | 2025-05-20 | 9:47 | ST | GS | - | 149.5 | g | 0 | 111.6 | 11.726 | 1161.5 | 11317 | 23:30 | 29.4 | 1.86 m/s | 21 | 31.4 | 4.35 m/s | 14.6 |  | 1.86 | m/s |  | 4.35 | m/s | 23.5 | 0.0096792 | 26.4327 |  | -8 | 1377.5 | 1.3775 | 19.1889 | 6.1699 | 4.7793 | 0.016881 | 68.0336 | 2.0247
2025-05-20 09:47 | 2816 | Remove | 2025-05-20 | 9:47 | US | GS | - | 153 | g | 0 | 111.6 | 11.849 | 1175.9 | 11327 | 23:31 | 29.4 | 1.85 m/s | 21.1 | 31.5 | 4.76 m/s | 14.8 |  | 1.85 | m/s |  | 4.76 | m/s | 23.5086 | 0.0097992 | 26.4425 |  | 3.5 | 1381 | 1.381 | 19.1474 | 6.1993 | 4.8708 | 0.01687 | 68.0505 | 2.0294
2025-05-20 09:48 | 2817 | Remove | 2025-05-20 | 9:48 | US | GS | - | 154.5 | g | 0 | 111.7 | 11.787 | 1168.7 | 11337 | 23:31 | 29.4 | 1.79 m/s | 21.1 | 31.5 | 4.87 m/s | 14.7 |  | 1.79 | m/s |  | 4.87 | m/s | 23.5169 | 0.0097392 | 26.4522 |  | 1.5 | 1382.5 | 1.3825 | 19.1336 | 6.1993 | 4.8379 | 0.016323 | 68.0668 | 2.0311
2025-05-20 09:48 | 2818 | Remove | 2025-05-20 | 9:48 | ST | GS | - | 153.5 | g | 0 | 111.6 | 11.805 | 1170.8 | 11347 | 23:32 | 29.4 | 1.9 m/s | 21 | 31.5 | 4.4 m/s | 14.7 |  | 1.9 | m/s |  | 4.4 | m/s | 23.5253 | 0.0097567 | 26.462 |  | -1 | 1382.5 | 1.3825 | 19.1407 | 6.1699 | 4.8379 | 0.017244 | 68.0841 | 2.0306
2025-05-20 09:49 | 2819 | Remove | 2025-05-20 | 9:49 | ST | GS | - | 156 | g | 0 | 111.6 | 11.773 | 1166.9 | 11356 | 23:32 | 29.5 | 1.85 m/s | 21.4 | 31.5 | 4.27 m/s | 14.6 |  | 1.85 | m/s |  | 4.27 | m/s | 23.5336 | 0.0097242 | 26.4717 |  | 2.5 | 1385 | 1.385 | 19.1132 | 6.3217 | 4.805 | 0.017203 | 68.1013 | 2.0337
2025-05-20 09:49 | 2820 | Remove | 2025-05-20 | 9:49 | ST | GS | - | 149 | g | 0 | 111.8 | 11.722 | 1161.7 | 11366 | 23:33 | 29.5 | 1.78 m/s | 21 | 31.5 | 4.35 m/s | 14.5 |  | 1.78 | m/s |  | 4.35 | m/s | 23.5419 | 0.0096808 | 26.4814 |  | -7 | 1385 | 1.385 | 19.1201 | 6.2036 | 4.7721 | 0.016243 | 68.1175 | 2.0333
2025-05-20 09:50 | 2821 | Keep | 2025-05-20 | 9:50 | ST | GS | - | 149.5 | g | 0 | 111.8 | 11.733 | 1162.5 | 11376 | 23:33 | 29.4 | 1.74 m/s | 21 | 31.5 | 4.49 m/s | 14.6 |  | 1.74 | m/s |  | 4.49 | m/s | 23.5503 | 0.0096875 | 26.4911 |  | 0.5 | 1385.5 | 1.3855 | 19.1202 | 6.1699 | 4.805 | 0.015792 | 68.1333 | 2.0335
2025-05-20 09:50 | 2822 | Remove | 2025-05-20 | 9:50 | ST | GS | - | 151 | g | 0 | 111.7 | 11.786 | 1169.2 | 11385 | 23:34 | 29.4 | 2.05 m/s | 21.4 | 31.5 | 4.29 m/s | 14.6 |  | 2.05 | m/s |  | 4.29 | m/s | 23.5586 | 0.0097433 | 26.5008 |  | 1.5 | 1387 | 1.387 | 19.1066 | 6.2874 | 4.805 | 0.01896 | 68.1523 | 2.0351
2025-05-20 09:51 | 2823 | Remove | 2025-05-20 | 9:51 | ST | GS | - | 152 | g | 0 | 111.6 | 11.834 | 1174.8 | 11395 | 23:34 | 29.4 | 1.85 m/s | 21.3 | 31.5 | 4.47 m/s | 14.8 |  | 1.85 | m/s |  | 4.47 | m/s | 23.5669 | 0.00979 | 26.5106 |  | 1 | 1388 | 1.388 | 19.0999 | 6.258 | 4.8708 | 0.01703 | 68.1693 | 2.0361
2025-05-20 09:51 | 2824 | Remove | 2025-05-20 | 9:51 | ST | GS | - | 150 | g | 0 | 111.5 | 11.826 | 1173.5 | 11405 | 23:35 | 29.5 | 1.95 m/s | 21.5 | 31.5 | 4.29 m/s | 15 |  | 1.95 | m/s |  | 4.29 | m/s | 23.5753 | 0.0097792 | 26.5204 |  | -2 | 1388 | 1.388 | 19.1069 | 6.3513 | 4.9367 | 0.018218 | 68.1875 | 2.0356
2025-05-20 09:52 | 2825 | Remove | 2025-05-20 | 9:52 | ST | GS | - | 152 | g | 0 | 111.7 | 11.81 | 1172.1 | 11415 | 23:35 | 29.4 | 2.0 m/s | 21.1 | 31.6 | 4.44 m/s | 14.4 |  | 2 | m/s |  | 4.44 | m/s | 23.5836 | 0.0097675 | 26.5302 |  | 2 | 1390 | 1.39 | 19.0864 | 6.1993 | 4.7647 | 0.018238 | 68.2058 | 2.038
2025-05-20 09:52 | 2826 | Remove | 2025-05-20 | 9:52 | US | GS | - | 153 | g | 0 | 111.6 | 11.75 | 1164.5 | 11425 | 23:36 | 29.4 | 1.71 m/s | 21.1 | 31.6 | 4.26 m/s | 14.4 |  | 1.71 | m/s |  | 4.26 | m/s | 23.5919 | 0.0097042 | 26.5399 |  | 1 | 1391 | 1.391 | 19.0797 | 6.1993 | 4.7647 | 0.015593 | 68.2214 | 2.039
2025-05-20 09:53 | 2827 | Remove | 2025-05-20 | 9:53 | US | GS | - | 166.5 | g | 0 | 111.7 | 11.648 | 1152.6 | 11434 | 23:36 | 29.4 | 1.33 m/s | 20.6 | 31.5 | 4.29 m/s | 14.3 |  | 1.33 | m/s |  | 4.29 | m/s | 23.6003 | 0.009605 | 26.5495 |  | 13.5 | 1404.5 | 1.4045 | 18.9031 | 6.0524 | 4.7063 | 0.011841 | 68.2332 | 2.0584
2025-05-20 09:53 | 2828 | Remove | 2025-05-20 | 9:53 | US | GS | - | 155.5 | g | 0 | 111.6 | 11.78 | 1167.9 | 11444 | 23:37 | 29.4 | 1.6 m/s | 20.8 | 31.5 | 4.55 m/s | 14.7 |  | 1.6 | m/s |  | 4.55 | m/s | 23.6086 | 0.0097325 | 26.5592 |  | -11 | 1404.5 | 1.4045 | 18.9101 | 6.1111 | 4.8379 | 0.014383 | 68.2476 | 2.0579
2025-05-20 09:54 | 2829 | Remove | 2025-05-20 | 9:54 | ST | GS | - | 154.5 | g | 0 | 111.7 | 11.797 | 1170.2 | 11454 | 23:37 | 29.4 | 1.64 m/s | 21 | 31.5 | 4.41 m/s | 14.6 |  | 1.64 | m/s |  | 4.41 | m/s | 23.6169 | 0.0097517 | 26.569 |  | -1 | 1404.5 | 1.4045 | 18.917 | 6.1699 | 4.805 | 0.014884 | 68.2625 | 2.0575
2025-05-20 09:54 | 2830 | Remove | 2025-05-20 | 9:54 | ST | GS | - | 163 | g | 0 | 111.7 | 11.749 | 1164.2 | 11463 | 23:38 | 29.4 | 2.26 m/s | 21.4 | 31.5 | 4.52 m/s | 14.8 |  | 2.26 | m/s |  | 4.52 | m/s | 23.6253 | 0.0097017 | 26.5787 |  | 8.5 | 1413 | 1.413 | 18.8101 | 6.2874 | 4.8708 | 0.020902 | 68.2834 | 2.0693
Formulas:
Date-Time = [Date]+[Time]